## Score Template (hidden)
|  | Blue highlight denotes input data from PI/SCADA/Markets DB |  |  |  |  | Correlation |  | Delay |  | Precision |  | Composite |  | Slope Check | [40 empty] | A | 1 | 33.33%
[7 empty] | 97.65% |  | 72.93% |  | 56.76% |  | 75.78% |  | 0.05 | [37 empty] | New Method |  |  | B | 1 | 33.33%
[56 empty] | C | 1 | 33.33%
[16 empty] | +0.00m | +0.00m | +0.01m | +0.01m | +0.01m | +0.01m | +0.01m | +0.01m | +0.02m | +0.02m | +0.02m | +0.02m | +0.02m | +0.02m | +0.03m | +0.03m | +0.03m | +0.03m | +0.03m | +0.03m | +0.04m | +0.04m | +0.04m | +0.04m | +0.04m | +0.04m | +0.05m | +0.05m | +0.05m | [6 empty] | Original |  | Hourly | Current Method
[15 empty] | No Time Shift | +10s | +20s | +30s | +40s | +50s | +60s | +70s | +80s | +90s | +100s | +110s | +120s | +130s | +140s | +150s | +160s | +170s | +180s | +190s | +200s | +210s | +220s | +230s | +240s | +250s | +260s | +270s | +280s | +290s | Correlation |  |  |  | Delay |  | Precision |  | Average of Reg Signal | Precision | Precision |  | Combined SCORE
[15 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 97.65% |  |  |  | 72.93% |  | 71.26% |  | 3.122 | 56.76% | 56.76% |  | 75.78%
Interval | TIME | AGC MW | Raw ECOBP | Energy RR at AGC MW (MW/min) | RR MW/10sec | Ramped EcoBP | Unit AREG | Fleet TREG | Fleet Regulation Control Signal | Raw Unit REG | Ramped Reg | Raw EcoBP + Raw Reg | Ramped EcoBP + Ramped Reg | Unit Resp.
1 | 0:00 | 99.5728 | 100 | 3 | 0.5 | 100 | 5 | 20 | 0 | 0 | 0 | 100 | 100 | -0.42716 | [35 empty] | 0.085431 | 0.91457 | 0 | 0.13682 | 0.86318 | 0.86318
2 | 0:00 | 100.1642 | 110 | 3 | 0.5 | 100.5 | 5 | 20 | 0.9256 | 0.2314 | 0.2314 | 110.2314 | 100.7314 | -0.33583 | [35 empty] | 0.11345 | 0.88655 | 0.2314 | 0.18169 | 0.81831 | 0.81831
3 | 0:00 | 99.8928 | 110 | 3 | 0.5 | 101 | 5 | 20 | 1.8492 | 0.4623 | 0.4623 | 110.4623 | 101.4623 | -1.1072 | [35 empty] | 0.31391 | 0.68609 | 0.4623 | 0.50273 | 0.49727 | 0.49727
4 | 0:00 | 99.9248 | 110 | 3 | 0.5 | 101.5 | 5 | 20 | 2.7689 | 0.69221 | 0.69221 | 110.6922 | 102.1922 | -1.5752 | [35 empty] | 0.45348 | 0.54652 | 0.69221 | 0.72625 | 0.27375 | 0.27375
5 | 0:01 | 100.3971 | 110 | 3 | 0.5 | 102 | 5 | 20 | 3.6826 | 0.92064 | 0.92064 | 110.9206 | 102.9206 | -1.6029 | [35 empty] | 0.50471 | 0.49529 | 0.92064 | 0.8083 | 0.1917 | 0.1917
6 | 0:01 | 99.8069 | 110 | 3 | 0.5 | 102.5 | 5 | 20 | 4.5884 | 1.1471 | 1.1471 | 111.1471 | 103.6471 | -2.6931 | [35 empty] | 0.76804 | 0.23196 | 1.1471 | 1.23 | 0 | 0
7 | 0:01 | 99.9757 | 110 | 3 | 0.5 | 103 | 5 | 20 | 5.4844 | 1.3711 | 1.3711 | 111.3711 | 104.3711 | -3.0243 | [35 empty] | 0.87909 | 0.12091 | 1.3711 | 1.4079 | 0 | 0
8 | 0:01 | 99.7059 | 110 | 3 | 0.5 | 103.5 | 5 | 20 | 6.3686 | 1.5922 | 1.5922 | 111.5922 | 105.0922 | -3.7941 | [35 empty] | 1.0772 | 0 | 1.5922 | 1.7252 | 0 | 0
9 | 0:01 | 100.8386 | 110 | 3 | 0.5 | 104 | 5 | 20 | 7.2392 | 1.8098 | 1.8098 | 111.8098 | 105.8098 | -3.1614 | [35 empty] | 0.99424 | 0.0057605 | 1.8098 | 1.5923 | 0 | 0
10 | 0:01 | 101.5879 | 110 | 3 | 0.5 | 104.5 | 5 | 20 | 8.0943 | 2.0236 | 2.0236 | 112.0236 | 106.5236 | -2.9121 | [35 empty] | 0.98714 | 0.012862 | 2.0236 | 1.5809 | 0 | 0
11 | 0:02 | 101.9002 | 110 | 3 | 0.5 | 105 | 5 | 20 | 8.932 | 2.233 | 2.233 | 112.233 | 107.233 | -3.0998 | [35 empty] | 1.0666 | 0 | 2.233 | 1.7081 | 0 | 0
12 | 0:02 | 102.3078 | 110 | 3 | 0.5 | 105.5 | 5 | 20 | 9.7506 | 2.4377 | 2.4377 | 112.4377 | 107.9377 | -3.1922 | [35 empty] | 1.126 | 0 | 2.4377 | 1.8033 | 0 | 0
13 | 0:02 | 103.7491 | 110 | 3 | 0.5 | 106 | 5 | 20 | 10.5483 | 2.6371 | 2.6371 | 112.6371 | 108.6371 | -2.2509 | [35 empty] | 0.97759 | 0.022405 | 2.6371 | 1.5656 | 0 | 0
14 | 0:02 | 104.4906 | 110 | 3 | 0.5 | 106.5 | 5 | 20 | 11.3234 | 2.8308 | 2.8308 | 112.8308 | 109.3308 | -2.0094 | [35 empty] | 0.96805 | 0.031947 | 2.8308 | 1.5504 | 0 | 0
15 | 0:02 | 104.2485 | 110 | 3 | 0.5 | 107 | 5 | 20 | 12.0742 | 3.0186 | 3.0186 | 113.0186 | 110.0186 | -2.7515 | [35 empty] | 1.154 | 0 | 3.0186 | 1.8482 | 0 | 0
16 | 0:02 | 105.3404 | 110 | 3 | 0.5 | 107.5 | 5 | 20 | 12.7992 | 3.1998 | 3.1998 | 113.1998 | 110.6998 | -2.1596 | [35 empty] | 1.0719 | 0 | 3.1998 | 1.7166 | 0 | 0
17 | 0:03 | 105.9536 | 110 | 3 | 0.5 | 108 | 5 | 20 | 13.4967 | 3.3742 | 3.3742 | 113.3742 | 111.3742 | -2.0464 | [35 empty] | 1.0841 | 0 | 3.3742 | 1.7362 | 0 | 0
18 | 0:03 | 106.5056 | 110 | 3 | 0.5 | 108.5 | 5 | 20 | 14.1653 | 3.5413 | 3.5413 | 113.5413 | 112.0413 | -1.9944 | [35 empty] | 1.1071 | 0 | 3.5413 | 1.7731 | 0 | 0
19 | 0:03 | 107.0987 | 110 | 3 | 0.5 | 109 | 5 | 20 | 14.8035 | 3.7009 | 3.7009 | 113.7009 | 112.7009 | -1.9013 | [35 empty] | 1.1204 | 0 | 3.7009 | 1.7944 | 0 | 0
20 | 0:03 | 108.02 | 110 | 3 | 0.5 | 109.5 | 5 | 20 | 15.4101 | 3.8525 | 3.8525 | 113.8525 | 113.3525 | -1.48 | [35 empty] | 1.0665 | 0 | 3.8525 | 1.708 | 0 | 0
21 | 0:03 | 108.3516 | 110 | 3 | 0.5 | 110 | 5 | 20 | 15.9836 | 3.9959 | 3.9959 | 113.9959 | 113.9959 | -1.6484 | [35 empty] | 1.1289 | 0 | 3.9959 | 1.8079 | 0 | 0
22 | 0:04 | 109.6375 | 110 | 3 | 0.5 | 110 | 5 | 20 | 16.5228 | 4.1307 | 4.1307 | 114.1307 | 114.1307 | -0.36248 | [35 empty] | 0.89864 | 0.10136 | 4.1307 | 1.4392 | 0 | 0
23 | 0:04 | 110.0718 | 110 | 3 | 0.5 | 110 | 5 | 20 | 17.0266 | 4.2567 | 4.2567 | 114.2567 | 114.2567 | 0.071848 | [35 empty] | 0.83696 | 0.16304 | 4.2567 | 1.3404 | 0 | 0
24 | 0:04 | 110.4163 | 110 | 3 | 0.5 | 110 | 5 | 20 | 17.494 | 4.3735 | 4.3735 | 114.3735 | 114.3735 | 0.41632 | [35 empty] | 0.79144 | 0.20856 | 4.3735 | 1.2675 | 0 | 0
25 | 0:04 | 111.7591 | 110 | 3 | 0.5 | 110 | 5 | 20 | 17.9238 | 4.481 | 4.481 | 114.481 | 114.481 | 1.7591 | [35 empty] | 0.54437 | 0.45563 | 4.481 | 0.87182 | 0.12818 | 0.12818
26 | 0:04 | 112.1239 | 110 | 3 | 0.5 | 110 | 5 | 20 | 18.3153 | 4.5788 | 4.5788 | 114.5788 | 114.5788 | 2.1239 | [35 empty] | 0.49099 | 0.50901 | 4.5788 | 0.78633 | 0.21367 | 0.21367
27 | 0:04 | 112.739 | 110 | 3 | 0.5 | 110 | 5 | 20 | 18.6675 | 4.6669 | 4.6669 | 114.6669 | 114.6669 | 2.739 | [35 empty] | 0.38557 | 0.61443 | 4.6669 | 0.6175 | 0.3825 | 0.3825
28 | 0:05 | 113.7594 | 110 | 3 | 0.5 | 110 | 5 | 20 | 18.9797 | 4.7449 | 4.7449 | 114.7449 | 114.7449 | 3.7594 | [35 empty] | 0.1971 | 0.8029 | 4.7449 | 0.31566 | 0.68434 | 0.68434
29 | 0:05 | 113.8749 | 110 | 3 | 0.5 | 110 | 5 | 20 | 19.2512 | 4.8128 | 4.8128 | 114.8128 | 114.8128 | 3.8749 | [35 empty] | 0.18758 | 0.81242 | 4.8128 | 0.30041 | 0.69959 | 0.69959
30 | 0:05 | 113.4406 | 110 | 3 | 0.5 | 110 | 5 | 20 | 19.4815 | 4.8704 | 4.8704 | 114.8704 | 114.8704 | 3.4406 | [35 empty] | 0.28595 | 0.71405 | 4.8704 | 0.45796 | 0.54204 | 0.54204
31 | 0:05 | 113.4787 | 110 | 3 | 0.5 | 110 | 5 | 20 | 19.67 | 4.9175 | 4.9175 | 114.9175 | 114.9175 | 3.4787 | 62.83% | 71.13% | 78.85% | 84.3% | 88.45% | 92.18% | 94.11% | 95.42% | 95.9% | 96.56% | 97.15% | 97.43% | 97.51% | 97.6% | 97.71% | 97.15% | 96.23% | 94.93% | 93.04% | 90.37% | 86.18% | 80.8% | 74.71% | 64.03% | 87.23% | 85.31% | 83.29% | 81.42% | 80.04% | 78.41% | 97.71% | 14 | +140s | 130 | 56.67% | 0.28777 | 0.71223 | 4.9175 | 0.46086 | 0.53914 | 0.53914 |  | 69.43%
32 | 0:05 | 114.2947 | 110 | 3 | 0.5 | 110 | 5 | 20 | 19.8164 | 4.9541 | 4.9541 | 114.9541 | 114.9541 | 4.2947 | 70.13% | 77.99% | 83.57% | 87.85% | 91.7% | 93.72% | 95.13% | 95.66% | 96.39% | 97.03% | 97.35% | 97.47% | 97.66% | 97.85% | 97.35% | 96.52% | 95.3% | 93.49% | 90.91% | 86.83% | 81.58% | 75.58% | 65.05% | 87.9% | 85.98% | 83.96% | 82.09% | 80.7% | 79.08% | 0% | 97.85% | 13 | +130s | 120 | 60% | 0.13188 | 0.86812 | 4.9541 | 0.21121 | 0.78879 | 0.78879 |  | 78.91%
33 | 0:05 | 114.6602 | 110 | 3 | 0.5 | 110 | 5 | 20 | 19.9203 | 4.9801 | 4.9801 | 114.9801 | 114.9801 | 4.6602 | 77.04% | 82.76% | 87.18% | 91.16% | 93.28% | 94.79% | 95.37% | 96.18% | 96.88% | 97.24% | 97.4% | 97.7% | 97.97% | 97.54% | 96.8% | 95.67% | 93.96% | 91.48% | 87.52% | 82.4% | 76.51% | 66.14% | 88.6% | 86.68% | 84.66% | 82.8% | 81.41% | 79.78% | 0% | 0% | 97.97% | 12 | +120s | 110 | 63.33% | 0.063965 | 0.93603 | 4.9801 | 0.10244 | 0.89756 | 0.89756 |  | 83.69%
34 | 0:06 | 114.239 | 110 | 3 | 0.5 | 110 | 5 | 20 | 19.9815 | 4.9954 | 4.9954 | 114.9954 | 114.9954 | 4.239 | 81.85% | 86.42% | 90.54% | 92.78% | 94.39% | 95.03% | 95.93% | 96.69% | 97.09% | 97.3% | 97.71% | 98.08% | 97.72% | 97.08% | 96.05% | 94.44% | 92.06% | 88.25% | 83.27% | 77.5% | 67.31% | 89.34% | 87.42% | 85.4% | 83.53% | 82.15% | 80.52% | 0% | 0% | 0% | 98.08% | 11 | +110s | 100 | 66.67% | 0.15127 | 0.84873 | 4.9954 | 0.24226 | 0.75774 | 0.75774 |  | 80.17%
35 | 0:06 | 114.2239 | 110 | 3 | 0.5 | 110 | 5 | 20 | 19.9999 | 5 | 5 | 115 | 115 | 4.2239 | 85.55% | 89.83% | 92.19% | 93.92% | 94.63% | 95.62% | 96.44% | 96.9% | 97.15% | 97.69% | 98.16% | 97.89% | 97.36% | 96.43% | 94.93% | 92.68% | 89.01% | 84.2% | 78.55% | 68.57% | 90.11% | 88.19% | 86.17% | 84.3% | 82.91% | 81.29% | 0% | 0% | 0% | 0% | 98.16% | 10 | +100s | 90 | 70% | 0.15522 | 0.84478 | 5 | 0.24859 | 0.75141 | 0.75141 |  | 81.1%
36 | 0:06 | 114.6915 | 110 | 3 | 0.5 | 110 | 5 | 20 | 19.9754 | 4.9939 | 4.9939 | 114.9939 | 114.9939 | 4.6915 | 89.01% | 91.5% | 93.36% | 94.14% | 95.23% | 96.13% | 96.64% | 96.94% | 97.63% | 98.2% | 98.02% | 97.62% | 96.81% | 95.43% | 93.31% | 89.82% | 85.19% | 79.69% | 69.93% | 90.91% | 88.98% | 86.97% | 85.1% | 83.71% | 82.09% | 0% | 0% | 0% | 0% | 0% | 98.2% | 9 | +90s | 80 | 73.33% | 0.060469 | 0.93953 | 4.9939 | 0.096842 | 0.90316 | 0.90316 |  | 87.28%
37 | 0:06 | 114.6547 | 110 | 3 | 0.5 | 110 | 5 | 20 | 19.9082 | 4.977 | 4.977 | 114.977 | 114.977 | 4.6547 | 90.67% | 92.68% | 93.54% | 94.74% | 95.72% | 96.29% | 96.66% | 97.51% | 98.2% | 98.12% | 97.86% | 97.18% | 95.94% | 93.97% | 90.67% | 86.25% | 80.92% | 71.42% | 91.73% | 89.81% | 87.79% | 85.93% | 84.54% | 82.91% | 0% | 0% | 0% | 0% | 0% | 0% | 98.2% | 8 | +80s | 70 | 76.67% | 0.064472 | 0.93553 | 4.977 | 0.10325 | 0.89675 | 0.89675 |  | 88.18%
38 | 0:06 | 114.5223 | 110 | 3 | 0.5 | 110 | 5 | 20 | 19.7982 | 4.9496 | 4.9496 | 114.9496 | 114.9496 | 4.5223 | 91.84% | 92.79% | 94.12% | 95.2% | 95.83% | 96.27% | 97.3% | 98.13% | 98.17% | 98.06% | 97.54% | 96.46% | 94.66% | 91.58% | 87.39% | 82.26% | 73.05% | 92.59% | 90.66% | 88.65% | 86.78% | 85.39% | 83.77% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 98.17% | 8 | +80s | 70 | 76.67% | 0.085449 | 0.91455 | 4.9496 | 0.13685 | 0.86315 | 0.86315 |  | 87.05%
39 | 0:06 | 114.9759 | 110 | 3 | 0.5 | 110 | 5 | 20 | 19.6459 | 4.9115 | 4.9115 | 114.9115 | 114.9115 | 4.9759 | 91.86% | 93.34% | 94.51% | 95.23% | 95.74% | 96.97% | 97.96% | 98.13% | 98.21% | 97.86% | 96.95% | 95.35% | 92.53% | 88.61% | 83.71% | 74.85% | 93.47% | 91.54% | 89.53% | 87.66% | 86.27% | 84.64% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 98.21% | 8 | +80s | 70 | 76.67% | 0.012877 | 0.98712 | 4.9115 | 0.020623 | 0.97938 | 0.97938 |  | 90.94%
40 | 0:07 | 114.9886 | 110 | 3 | 0.5 | 110 | 5 | 20 | 19.4514 | 4.8629 | 4.8629 | 114.8629 | 114.8629 | 4.9886 | 92.31% | 93.61% | 94.41% | 95.02% | 96.48% | 97.65% | 97.98% | 98.25% | 98.11% | 97.41% | 96.04% | 93.51% | 89.92% | 85.28% | 76.84% | 94.37% | 92.44% | 90.43% | 88.56% | 87.17% | 85.55% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 98.25% | 7 | +70s | 60 | 80% | 0.025142 | 0.97486 | 4.8629 | 0.040265 | 0.95973 | 0.95973 |  | 91.41%
41 | 0:07 | 115.7892 | 110 | 3 | 0.5 | 110 | 5 | 20 | 19.2153 | 4.8038 | 4.8038 | 114.8038 | 114.8038 | 5.7892 | 92.4% | 93.3% | 94.01% | 95.75% | 97.13% | 97.63% | 98.15% | 98.24% | 97.79% | 96.69% | 94.52% | 91.31% | 86.99% | 79.05% | 95.29% | 93.37% | 91.35% | 89.48% | 88.1% | 86.47% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 98.24% | 7 | +70s | 60 | 80% | 0.19708 | 0.80292 | 4.8038 | 0.31562 | 0.68438 | 0.68438 |  | 82.23%
42 | 0:07 | 116.0377 | 110 | 3 | 0.5 | 110 | 5 | 20 | 18.9379 | 4.7345 | 4.7345 | 114.7345 | 114.7345 | 6.0377 | 91.77% | 92.61% | 94.66% | 96.29% | 97% | 97.81% | 98.17% | 98.02% | 97.25% | 95.49% | 92.74% | 88.81% | 81.49% | 96.23% | 94.31% | 92.29% | 90.42% | 89.04% | 87.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 98.17% | 6 | +60s | 50 | 83.33% | 0.26064 | 0.73936 | 4.7345 | 0.41741 | 0.58259 | 0.58259 |  | 79.92%
43 | 0:07 | 115.915 | 110 | 3 | 0.5 | 110 | 5 | 20 | 18.62 | 4.655 | 4.655 | 114.655 | 114.655 | 5.915 | 90.6% | 93.03% | 94.95% | 95.91% | 97.07% | 97.77% | 97.97% | 97.59% | 96.36% | 94.17% | 90.73% | 84.16% | 97.19% | 95.27% | 93.25% | 91.38% | 89.99% | 88.37% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 97.97% | 6 | +60s | 50 | 83.33% | 0.252 | 0.748 | 4.655 | 0.40358 | 0.59642 | 0.59642 |  | 80.32%
44 | 0:07 | 115.0137 | 110 | 3 | 0.5 | 110 | 5 | 20 | 18.2622 | 4.5656 | 4.5656 | 114.5656 | 114.5656 | 5.0137 | 90.58% | 92.85% | 94.11% | 95.68% | 96.79% | 97.43% | 97.54% | 96.94% | 95.46% | 92.62% | 87.03% | 98.16% | 96.24% | 94.22% | 92.35% | 90.97% | 89.34% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 98.16% | 11 | +110s | 100 | 66.67% | 0.089622 | 0.91038 | 4.5656 | 0.14353 | 0.85647 | 0.85647 |  | 83.49%
45 | 0:07 | 115.6538 | 110 | 3 | 0.5 | 110 | 5 | 20 | 17.8653 | 4.4663 | 4.4663 | 114.4663 | 114.4663 | 5.6538 | 74.35% | 76.01% | 77.81% | 79.87% | 82.33% | 85.21% | 88.36% | 92.01% | 94.76% | 97.83% | 99.15% | 97.22% | 95.21% | 93.34% | 91.95% | 90.33% | 88.58% | 87.11% | 85.75% | 84.91% | 83.84% | 82.79% | 81.97% | 80.98% | 79.75% | 78.76% | 77.77% | 77.48% | 77.9% | 78.35% | 99.15% | 10 | +100s | 90 | 70% | 0.2375 | 0.7625 | 4.4663 | 0.38036 | 0.61964 | 0.61964 |  | 77.04%
46 | 0:08 | 115.3287 | 110 | 3 | 0.5 | 110 | 5 | 20 | 17.4301 | 4.3575 | 4.3575 | 114.3575 | 114.3575 | 5.3287 | 75.01% | 76.81% | 78.87% | 81.33% | 84.21% | 87.36% | 91.01% | 93.76% | 96.83% | 99.86% | 98.22% | 96.2% | 94.34% | 92.95% | 91.32% | 89.58% | 88.11% | 86.75% | 85.9% | 84.83% | 83.79% | 82.97% | 81.97% | 80.75% | 79.75% | 78.77% | 78.47% | 78.89% | 79.35% | 78.99% | 99.86% | 9 | +90s | 80 | 73.33% | 0.19424 | 0.80576 | 4.3575 | 0.31107 | 0.68893 | 0.68893 |  | 80.69%
47 | 0:08 | 114.9999 | 110 | 3 | 0.5 | 110 | 5 | 20 | 16.9575 | 4.2394 | 4.2394 | 114.2394 | 114.2394 | 4.9999 | 75.81% | 77.87% | 80.33% | 83.2% | 86.36% | 90.01% | 92.76% | 95.82% | 98.85% | 99.22% | 97.21% | 95.34% | 93.95% | 92.33% | 90.59% | 89.11% | 87.75% | 86.91% | 85.84% | 84.79% | 83.97% | 82.98% | 81.75% | 80.76% | 79.77% | 79.48% | 79.9% | 80.35% | 79.99% | 79.96% | 99.22% | 9 | +90s | 80 | 73.33% | 0.1521 | 0.8479 | 4.2394 | 0.24359 | 0.75641 | 0.75641 |  | 82.73%
48 | 0:08 | 114.928 | 110 | 3 | 0.5 | 110 | 5 | 20 | 16.4486 | 4.1121 | 4.1121 | 114.1121 | 114.1121 | 4.928 | 76.86% | 79.32% | 82.19% | 85.35% | 89% | 91.75% | 94.81% | 97.84% | 99.76% | 98.22% | 96.35% | 94.96% | 93.34% | 91.6% | 90.12% | 88.76% | 87.92% | 86.85% | 85.8% | 84.98% | 83.99% | 82.77% | 81.77% | 80.78% | 80.49% | 80.91% | 81.36% | 81% | 80.97% | 81.25% | 99.76% | 8 | +80s | 70 | 76.67% | 0.16317 | 0.83683 | 4.1121 | 0.26132 | 0.73868 | 0.73868 |  | 83.43%
49 | 0:08 | 114.6683 | 110 | 3 | 0.5 | 110 | 5 | 20 | 15.9044 | 3.9761 | 3.9761 | 113.9761 | 113.9761 | 4.6683 | 78.3% | 81.18% | 84.33% | 87.98% | 90.73% | 93.8% | 96.83% | 98.75% | 99.23% | 97.37% | 95.98% | 94.35% | 92.61% | 91.14% | 89.78% | 88.93% | 87.86% | 86.82% | 86% | 85.01% | 83.78% | 82.78% | 81.8% | 81.51% | 81.92% | 82.38% | 82.02% | 81.98% | 82.27% | 82.62% | 99.23% | 8 | +80s | 70 | 76.67% | 0.13844 | 0.86156 | 3.9761 | 0.22172 | 0.77828 | 0.77828 |  | 84.58%
50 | 0:08 | 114.3322 | 110 | 3 | 0.5 | 110 | 5 | 20 | 15.3262 | 3.8315 | 3.8315 | 113.8315 | 113.8315 | 4.3322 | 80.16% | 83.31% | 86.97% | 89.71% | 92.78% | 95.81% | 97.73% | 99.75% | 98.38% | 97% | 95.37% | 93.63% | 92.16% | 90.8% | 89.95% | 88.88% | 87.84% | 87.02% | 86.02% | 84.8% | 83.8% | 82.81% | 82.52% | 82.94% | 83.39% | 83.04% | 83% | 83.29% | 83.64% | 83.96% | 99.75% | 7 | +70s | 60 | 80% | 0.10014 | 0.89986 | 3.8315 | 0.16038 | 0.83962 | 0.83962 |  | 87.9%
51 | 0:08 | 113.8378 | 110 | 3 | 0.5 | 110 | 5 | 20 | 14.7151 | 3.6788 | 3.6788 | 113.6788 | 113.6788 | 3.8378 | 82.3% | 85.95% | 88.7% | 91.76% | 94.79% | 96.71% | 98.73% | 99.4% | 98.01% | 96.39% | 94.65% | 93.17% | 91.81% | 90.97% | 89.9% | 88.85% | 88.03% | 87.04% | 85.82% | 84.82% | 83.83% | 83.54% | 83.96% | 84.41% | 84.05% | 84.02% | 84.3% | 84.65% | 84.98% | 84.94% | 99.4% | 7 | +70s | 60 | 80% | 0.031816 | 0.96818 | 3.6788 | 0.050953 | 0.94905 | 0.94905 |  | 91.44%
52 | 0:09 | 113.5492 | 110 | 3 | 0.5 | 110 | 5 | 20 | 14.0724 | 3.5181 | 3.5181 | 113.5181 | 113.5181 | 3.5492 | 84.93% | 87.68% | 90.75% | 93.78% | 95.7% | 97.72% | 99.58% | 99.03% | 97.4% | 95.66% | 94.19% | 92.83% | 91.98% | 90.91% | 89.87% | 89.05% | 88.05% | 86.83% | 85.83% | 84.85% | 84.55% | 84.97% | 85.43% | 85.07% | 85.03% | 85.32% | 85.67% | 86% | 85.95% | 86.06% | 99.58% | 6 | +60s | 50 | 83.33% | 0.0062148 | 0.99379 | 3.5181 | 0.0099531 | 0.99005 | 0.99005 |  | 93.97%
53 | 0:09 | 114.0164 | 110 | 3 | 0.5 | 110 | 5 | 20 | 13.3997 | 3.3499 | 3.3499 | 113.3499 | 113.3499 | 4.0164 | 86.67% | 89.74% | 92.77% | 94.69% | 96.71% | 98.57% | 99.96% | 98.41% | 96.67% | 95.2% | 93.84% | 92.99% | 91.92% | 90.88% | 90.06% | 89.07% | 87.84% | 86.84% | 85.86% | 85.57% | 85.98% | 86.44% | 86.08% | 86.04% | 86.33% | 86.68% | 87.01% | 86.96% | 87.07% | 86.88% | 99.96% | 6 | +60s | 50 | 83.33% | 0.1333 | 0.8667 | 3.3499 | 0.21348 | 0.78652 | 0.78652 |  | 87.31%
54 | 0:09 | 113.3187 | 110 | 3 | 0.5 | 110 | 5 | 20 | 12.6982 | 3.1745 | 3.1745 | 113.1745 | 113.1745 | 3.3187 | 88.73% | 91.76% | 93.69% | 95.7% | 97.57% | 98.96% | 99.42% | 97.68% | 96.2% | 94.84% | 94% | 92.93% | 91.88% | 91.06% | 90.07% | 88.84% | 87.85% | 86.86% | 86.57% | 86.99% | 87.44% | 87.08% | 87.05% | 87.33% | 87.68% | 88.01% | 87.97% | 88.07% | 87.89% | 87.34% | 99.42% | 6 | +60s | 50 | 83.33% | 0.028825 | 0.97118 | 3.1745 | 0.046163 | 0.95384 | 0.95384 |  | 92.71%
55 | 0:09 | 113.2303 | 110 | 3 | 0.5 | 110 | 5 | 20 | 11.9694 | 2.9924 | 2.9924 | 112.9924 | 112.9924 | 3.2303 | 90.77% | 92.69% | 94.71% | 96.57% | 97.96% | 99.59% | 89.46% | 90.78% | 91.67% | 90.71% | 88.55% | 85.54% | 82.94% | 80.85% | 78.97% | 77.84% | 76.72% | 76.87% | 76.16% | 75.92% | 75.38% | 77.74% | 78.01% | 77.24% | 77.45% | 79.01% | 78.93% | 78.21% | 78.07% | 78.54% | 99.59% | 5 | +50s | 40 | 86.67% | 0.047596 | 0.9524 | 2.9924 | 0.076226 | 0.92377 | 0.92377 |  | 92.88%
56 | 0:09 | 113.8155 | 110 | 3 | 0.5 | 110 | 5 | 20 | 11.2151 | 2.8038 | 2.8038 | 112.8038 | 112.8038 | 3.8155 | 91.71% | 93.72% | 95.59% | 96.98% | 98.61% | 87.47% | 90.28% | 91.96% | 91.66% | 90.45% | 88.41% | 86.46% | 84.93% | 83.59% | 82.71% | 81.82% | 81.95% | 81.3% | 81.08% | 80.62% | 82.7% | 82.94% | 82.24% | 82.43% | 83.81% | 83.74% | 83.11% | 83% | 83.42% | 81.74% | 98.61% | 4 | +40s | 30 | 90% | 0.20234 | 0.79766 | 2.8038 | 0.32405 | 0.67595 | 0.67595 |  | 85.4%
57 | 0:09 | 113.4074 | 110 | 3 | 0.5 | 110 | 5 | 20 | 10.4367 | 2.6092 | 2.6092 | 112.6092 | 112.6092 | 3.4074 | 92.75% | 94.62% | 96.01% | 97.63% | 85.37% | 89.36% | 91.68% | 91.89% | 91.45% | 90.22% | 88.8% | 87.73% | 86.82% | 86.15% | 85.45% | 85.57% | 84.98% | 84.77% | 84.37% | 86.21% | 86.43% | 85.8% | 85.97% | 87.19% | 87.13% | 86.59% | 86.5% | 86.87% | 85.39% | 84.73% | 97.63% | 3 | +30s | 20 | 93.33% | 0.15964 | 0.84036 | 2.6092 | 0.25566 | 0.74434 | 0.74434 |  | 88.47%
58 | 0:10 | 113.083 | 110 | 3 | 0.5 | 110 | 5 | 20 | 9.6359 | 2.409 | 2.409 | 112.409 | 112.409 | 3.083 | 93.66% | 95.05% | 96.68% | 83.32% | 88.27% | 91.09% | 91.73% | 91.93% | 91.36% | 90.38% | 89.69% | 89.13% | 88.64% | 88.1% | 88.2% | 87.66% | 87.47% | 87.12% | 88.76% | 88.96% | 88.38% | 88.53% | 89.62% | 89.57% | 89.1% | 89.03% | 89.36% | 88.05% | 87.47% | 88.71% | 96.68% | 2 | +20s | 10 | 96.67% | 0.13479 | 0.86521 | 2.409 | 0.21588 | 0.78412 | 0.78412 |  | 90.59%
59 | 0:10 | 112.8125 | 110 | 3 | 0.5 | 110 | 5 | 20 | 8.8145 | 2.2036 | 2.2036 | 112.2036 | 112.2036 | 2.8125 | 94.11% | 95.74% | 81.41% | 87.14% | 90.37% | 91.36% | 92.09% | 92.06% | 91.45% | 91.08% | 90.82% | 90.48% | 90.06% | 90.16% | 89.66% | 89.48% | 89.18% | 90.65% | 90.83% | 90.29% | 90.44% | 91.41% | 91.37% | 90.95% | 90.9% | 91.2% | 90.03% | 89.52% | 90.64% | 90.45% | 95.74% | 1 | +10s | 0 | 100% | 0.12176 | 0.87824 | 2.2036 | 0.19501 | 0.80499 | 0.80499 |  | 92.08%
60 | 0:10 | 112.2278 | 110 | 3 | 0.5 | 110 | 5 | 20 | 7.9742 | 1.9936 | 1.9936 | 111.9936 | 111.9936 | 2.2278 | 94.82% | 79.65% | 86.02% | 89.6% | 90.88% | 92.05% | 92.49% | 92.19% | 92.09% | 92.08% | 91.86% | 91.56% | 91.64% | 91.18% | 91.01% | 90.75% | 92.07% | 92.24% | 91.74% | 91.87% | 92.75% | 92.72% | 92.35% | 92.31% | 92.59% | 91.53% | 91.08% | 92.1% | 91.92% | 92.4% | 94.82% | 0 | No Time Shift | 0 | 100% | 0.046858 | 0.95314 | 1.9936 | 0.075044 | 0.92496 | 0.92496 |  | 95.77%
61 | 0:10 | 112.3947 | 110 | 3 | 0.5 | 110 | 5 | 20 | 7.1168 | 1.7792 | 1.7792 | 111.7792 | 111.7792 | 2.3947 | 78.03% | 84.95% | 88.82% | 90.35% | 91.9% | 92.73% | 92.7% | 92.83% | 93.03% | 92.92% | 92.72% | 92.79% | 92.36% | 92.2% | 91.97% | 93.17% | 93.32% | 92.86% | 92.98% | 93.78% | 93.75% | 93.42% | 93.39% | 93.65% | 92.7% | 92.3% | 93.23% | 93.06% | 93.49% | 93.83% | 93.83% | 29 | +290s | 280 | 6.667% | 0.12311 | 0.87689 | 1.7792 | 0.19716 | 0.80284 | 0.80284 |  | 60.26%
62 | 0:10 | 112.7249 | 110 | 3 | 0.5 | 110 | 5 | 20 | 6.2442 | 1.5611 | 1.5611 | 111.5611 | 111.5611 | 2.7249 | 83.94% | 88.05% | 89.8% | 91.67% | 92.85% | 93.05% | 93.38% | 93.77% | 93.75% | 93.63% | 93.7% | 93.29% | 93.14% | 92.94% | 94.02% | 94.16% | 93.74% | 93.85% | 94.57% | 94.54% | 94.26% | 94.24% | 94.47% | 93.62% | 93.26% | 94.11% | 93.96% | 94.34% | 94.65% | 94.37% | 94.65% | 28 | +280s | 270 | 10% | 0.23277 | 0.76723 | 1.5611 | 0.37278 | 0.62722 | 0.62722 |  | 55.79%
63 | 0:10 | 111.9936 | 110 | 3 | 0.5 | 110 | 5 | 20 | 5.3582 | 1.3395 | 1.3395 | 111.3395 | 111.3395 | 1.9936 | 87.31% | 89.25% | 91.41% | 92.88% | 93.29% | 93.79% | 94.34% | 94.4% | 94.36% | 94.42% | 94.04% | 93.9% | 93.72% | 94.7% | 94.83% | 94.44% | 94.54% | 95.2% | 95.17% | 94.92% | 94.91% | 95.13% | 94.35% | 94.04% | 94.82% | 94.67% | 95.02% | 95.29% | 95.06% | 94.71% | 95.29% | 27 | +270s | 260 | 13.33% | 0.13082 | 0.86918 | 1.3395 | 0.20951 | 0.79049 | 0.79049 |  | 62.56%
64 | 0:11 | 112.2998 | 110 | 3 | 0.5 | 110 | 5 | 20 | 4.4607 | 1.1152 | 1.1152 | 111.1152 | 111.1152 | 2.2998 | 88.71% | 91.12% | 92.86% | 93.44% | 94.1% | 94.8% | 94.93% | 94.95% | 95% | 94.65% | 94.51% | 94.36% | 95.25% | 95.37% | 95% | 95.09% | 95.69% | 95.67% | 95.45% | 95.45% | 95.65% | 94.95% | 94.67% | 95.38% | 95.25% | 95.56% | 95.8% | 95.61% | 95.3% | 94.87% | 95.8% | 26 | +260s | 250 | 16.67% | 0.23692 | 0.76308 | 1.1152 | 0.37943 | 0.62057 | 0.62057 |  | 58.18%
65 | 0:11 | 112.2236 | 110 | 3 | 0.5 | 110 | 5 | 20 | 3.5536 | 0.88841 | 0.88841 | 110.8884 | 110.8884 | 2.2236 | 90.81% | 92.79% | 93.53% | 94.33% | 95.16% | 95.35% | 95.43% | 95.48% | 95.14% | 95.01% | 94.88% | 95.69% | 95.81% | 95.46% | 95.54% | 96.09% | 96.08% | 95.88% | 95.89% | 96.07% | 95.44% | 95.19% | 95.85% | 95.72% | 96% | 96.22% | 96.06% | 95.78% | 95.38% | 94.79% | 96.22% | 25 | +250s | 240 | 20% | 0.26704 | 0.73296 | 0.88841 | 0.42766 | 0.57234 | 0.57234 |  | 57.82%
66 | 0:11 | 112.141 | 110 | 3 | 0.5 | 110 | 5 | 20 | 2.6389 | 0.65974 | 0.65974 | 110.6597 | 110.6597 | 2.141 | 92.7% | 93.58% | 94.5% | 95.44% | 95.7% | 95.83% | 95.87% | 95.56% | 95.43% | 95.32% | 96.06% | 96.17% | 95.84% | 95.92% | 96.42% | 96.41% | 96.24% | 96.24% | 96.42% | 95.84% | 95.62% | 96.23% | 96.11% | 96.36% | 96.56% | 96.43% | 96.18% | 95.8% | 95.26% | 95.37% | 96.56% | 24 | +240s | 230 | 23.33% | 0.29626 | 0.70374 | 0.65974 | 0.47446 | 0.52554 | 0.52554 |  | 57.48%
67 | 0:11 | 111.8821 | 110 | 3 | 0.5 | 110 | 5 | 20 | 1.7186 | 0.42965 | 0.42965 | 110.4297 | 110.4297 | 1.8821 | 93.6% | 94.63% | 95.68% | 95.99% | 96.17% | 96.2% | 95.9% | 95.78% | 95.69% | 96.36% | 96.46% | 96.15% | 96.23% | 96.68% | 96.67% | 96.53% | 96.54% | 96.7% | 96.18% | 95.99% | 96.55% | 96.44% | 96.66% | 96.84% | 96.74% | 96.51% | 96.15% | 95.65% | 95.76% | 96.13% | 96.84% | 23 | +230s | 220 | 26.67% | 0.29049 | 0.70951 | 0.42965 | 0.46523 | 0.53477 | 0.53477 |  | 58.99%
68 | 0:11 | 111.4422 | 110 | 3 | 0.5 | 110 | 5 | 20 | 0.79461 | 0.19865 | 0.19865 | 110.1987 | 110.1987 | 1.4422 | 94.72% | 95.87% | 96.22% | 96.45% | 96.48% | 96.2% | 96.08% | 96% | 96.61% | 96.71% | 96.42% | 96.48% | 96.9% | 96.89% | 96.77% | 96.79% | 96.93% | 96.47% | 96.3% | 96.81% | 96.71% | 96.91% | 97.07% | 96.99% | 96.79% | 96.45% | 95.99% | 96.08% | 96.43% | 96.99% | 97.07% | 22 | +220s | 210 | 30% | 0.2487 | 0.7513 | 0.19865 | 0.3983 | 0.6017 | 0.6017 |  | 62.41%
69 | 0:11 | 110.9888 | 110 | 3 | 0.5 | 110 | 5 | 20 | -0.13111 | -0.032777 | -0.032777 | 109.9672 | 109.9672 | 0.98881 | 96.02% | 96.42% | 96.68% | 96.72% | 96.44% | 96.33% | 96.27% | 96.82% | 96.91% | 96.64% | 96.7% | 97.08% | 97.07% | 96.97% | 96.99% | 97.13% | 96.71% | 96.56% | 97.04% | 96.94% | 97.12% | 97.26% | 97.2% | 97.02% | 96.7% | 96.28% | 96.37% | 96.68% | 97.21% | 97.78% | 97.78% | 29 | +290s | 280 | 6.667% | 0.20432 | 0.79568 | 0.032777 | 0.32722 | 0.67278 | 0.67278 |  | 57.24%
70 | 0:12 | 110.6425 | 110 | 3 | 0.5 | 110 | 5 | 20 | -1.0565 | -0.26414 | -0.26414 | 109.7359 | 109.7359 | 0.64247 | 96.59% | 96.89% | 96.91% | 96.66% | 96.55% | 96.5% | 97% | 97.08% | 96.82% | 96.88% | 97.23% | 97.22% | 97.13% | 97.16% | 97.29% | 96.92% | 96.79% | 97.22% | 97.13% | 97.3% | 97.41% | 97.38% | 97.22% | 96.92% | 96.53% | 96.61% | 96.9% | 97.39% | 97.91% | 98.18% | 98.18% | 29 | +290s | 280 | 6.667% | 0.18132 | 0.81868 | 0.26414 | 0.29039 | 0.70961 | 0.70961 |  | 58.6%
71 | 0:12 | 110.3627 | 110 | 3 | 0.5 | 110 | 5 | 20 | -1.9797 | -0.49493 | -0.49493 | 109.5051 | 109.5051 | 0.36266 | 97.06% | 97.08% | 96.84% | 96.74% | 96.7% | 97.15% | 97.23% | 96.98% | 97.04% | 97.35% | 97.35% | 97.28% | 97.31% | 97.43% | 97.09% | 96.98% | 97.39% | 97.3% | 97.44% | 97.54% | 97.54% | 97.39% | 97.1% | 96.75% | 96.82% | 97.09% | 97.54% | 98.02% | 98.26% | 98.23% | 98.26% | 28 | +280s | 270 | 10% | 0.17152 | 0.82848 | 0.49493 | 0.27469 | 0.72531 | 0.72531 |  | 60.26%
72 | 0:12 | 110.3464 | 110 | 3 | 0.5 | 110 | 5 | 20 | -2.8986 | -0.72466 | -0.72466 | 109.2753 | 109.2753 | 0.34644 | 97.23% | 97% | 96.9% | 96.87% | 97.28% | 97.35% | 97.12% | 97.17% | 97.45% | 97.45% | 97.39% | 97.43% | 97.54% | 97.24% | 97.15% | 97.52% | 97.44% | 97.57% | 97.65% | 97.66% | 97.54% | 97.26% | 96.95% | 97.01% | 97.25% | 97.67% | 98.11% | 98.33% | 98.31% | 97.77% | 98.33% | 27 | +270s | 260 | 13.33% | 0.21422 | 0.78578 | 0.72466 | 0.34308 | 0.65692 | 0.65692 |  | 59.12%
73 | 0:12 | 110.8928 | 110 | 3 | 0.5 | 110 | 5 | 20 | -3.8114 | -0.95284 | -0.95284 | 109.0472 | 109.0472 | 0.89278 | 97.13% | 97.04% | 97.02% | 97.38% | 97.45% | 97.23% | 97.28% | 97.53% | 97.53% | 97.49% | 97.53% | 97.63% | 97.37% | 97.3% | 97.64% | 97.56% | 97.67% | 97.74% | 97.77% | 97.67% | 97.4% | 97.12% | 97.17% | 97.39% | 97.78% | 98.18% | 98.38% | 98.37% | 97.88% | 97.88% | 98.38% | 26 | +260s | 250 | 16.67% | 0.36912 | 0.63088 | 0.95284 | 0.59116 | 0.40884 | 0.40884 |  | 51.98%
74 | 0:12 | 110.7382 | 110 | 3 | 0.5 | 110 | 5 | 20 | -4.7159 | -1.179 | -1.179 | 108.821 | 108.821 | 0.73816 | 97.16% | 97.15% | 97.47% | 97.53% | 97.33% | 97.37% | 97.6% | 97.6% | 97.57% | 97.62% | 97.71% | 97.49% | 97.43% | 97.74% | 97.67% | 97.76% | 97.82% | 97.86% | 97.77% | 97.52% | 97.26% | 97.31% | 97.51% | 97.88% | 98.23% | 98.41% | 98.41% | 97.97% | 97.99% | 97.98% | 98.41% | 25 | +250s | 240 | 20% | 0.38343 | 0.61657 | 1.179 | 0.61407 | 0.38593 | 0.38593 |  | 52.34%
75 | 0:12 | 110.0135 | 110 | 3 | 0.5 | 110 | 5 | 20 | -5.6104 | -1.4026 | -1.4026 | 108.5974 | 108.5974 | 0.013465 | 97.27% | 97.55% | 97.6% | 97.41% | 97.45% | 97.65% | 97.66% | 97.64% | 97.69% | 97.77% | 97.58% | 97.54% | 97.82% | 97.75% | 97.83% | 97.88% | 97.94% | 97.87% | 97.63% | 97.4% | 97.43% | 97.62% | 97.95% | 98.28% | 98.43% | 98.44% | 98.04% | 98.07% | 98.08% | 97.82% | 98.44% | 25 | +250s | 240 | 20% | 0.28321 | 0.71679 | 1.4026 | 0.45357 | 0.54643 | 0.54643 |  | 57.7%
76 | 0:13 | 109.5278 | 110 | 3 | 0.5 | 110 | 5 | 20 | -6.4928 | -1.6232 | -1.6232 | 108.3768 | 108.3768 | -0.47221 | 97.61% | 97.66% | 97.48% | 97.51% | 97.69% | 97.7% | 97.69% | 97.75% | 97.83% | 97.66% | 97.64% | 97.89% | 97.83% | 97.89% | 97.92% | 98% | 97.94% | 97.72% | 97.51% | 97.55% | 97.71% | 98.02% | 98.31% | 98.45% | 98.46% | 98.1% | 98.15% | 98.16% | 97.91% | 97.84% | 98.46% | 24 | +240s | 230 | 23.33% | 0.2302 | 0.7698 | 1.6232 | 0.36866 | 0.63134 | 0.63134 |  | 61.64%
77 | 0:13 | 110.0036 | 110 | 3 | 0.5 | 110 | 5 | 20 | -7.3613 | -1.8403 | -1.8403 | 108.1597 | 108.1597 | 0.0035948 | 97.71% | 97.54% | 97.57% | 97.72% | 97.73% | 97.74% | 97.79% | 97.86% | 97.74% | 97.72% | 97.95% | 97.89% | 97.94% | 97.96% | 98.06% | 98.01% | 97.8% | 97.62% | 97.64% | 97.79% | 98.07% | 98.32% | 98.45% | 98.47% | 98.15% | 98.21% | 98.22% | 97.99% | 97.93% | 97.89% | 98.47% | 23 | +230s | 220 | 26.67% | 0.36878 | 0.63122 | 1.8403 | 0.59061 | 0.40939 | 0.40939 |  | 55.36%
78 | 0:13 | 110.0988 | 110 | 3 | 0.5 | 110 | 5 | 20 | -8.214 | -2.0535 | -2.0535 | 107.9465 | 107.9465 | 0.098846 | 97.58% | 97.61% | 97.74% | 97.75% | 97.77% | 97.83% | 97.89% | 97.79% | 97.8% | 98% | 97.94% | 97.98% | 97.98% | 98.1% | 98.07% | 97.86% | 97.71% | 97.73% | 97.86% | 98.11% | 98.33% | 98.44% | 98.47% | 98.19% | 98.26% | 98.28% | 98.06% | 98% | 97.97% | 98.01% | 98.47% | 22 | +220s | 210 | 30% | 0.43047 | 0.56953 | 2.0535 | 0.6894 | 0.3106 | 0.3106 |  | 53.18%
79 | 0:13 | 109.8147 | 110 | 3 | 0.5 | 110 | 5 | 20 | -9.0491 | -2.2623 | -2.2623 | 107.7377 | 107.7377 | -0.18534 | 97.65% | 97.75% | 97.76% | 97.8% | 97.86% | 97.91% | 97.84% | 97.86% | 98.03% | 97.99% | 98.01% | 98% | 98.13% | 98.11% | 97.92% | 97.79% | 97.8% | 97.92% | 98.15% | 98.33% | 98.42% | 98.46% | 98.22% | 98.3% | 98.33% | 98.12% | 98.06% | 98.04% | 98.09% | 97.99% | 98.46% | 21 | +210s | 200 | 33.33% | 0.41539 | 0.58461 | 2.2623 | 0.66525 | 0.33475 | 0.33475 |  | 55.09%
80 | 0:13 | 109.1362 | 110 | 3 | 0.5 | 110 | 5 | 20 | -9.8649 | -2.4662 | -2.4662 | 107.5338 | 107.5338 | -0.86376 | 97.75% | 97.76% | 97.81% | 97.87% | 97.93% | 97.89% | 97.92% | 98.06% | 98.02% | 98.03% | 98.01% | 98.15% | 98.15% | 97.97% | 97.86% | 97.87% | 97.97% | 98.17% | 98.33% | 98.4% | 98.44% | 98.24% | 98.34% | 98.37% | 98.17% | 98.11% | 98.09% | 98.15% | 98.06% | 97.65% | 98.44% | 20 | +200s | 190 | 36.67% | 0.32049 | 0.67951 | 2.4662 | 0.51327 | 0.48673 | 0.48673 |  | 61.26%
81 | 0:13 | 109.3725 | 110 | 3 | 0.5 | 110 | 5 | 20 | -10.6595 | -2.6649 | -2.6649 | 107.3351 | 107.3351 | -0.62754 | 97.76% | 97.82% | 97.88% | 97.93% | 97.92% | 97.96% | 98.08% | 98.04% | 98.04% | 98.01% | 98.17% | 98.18% | 98.01% | 97.92% | 97.93% | 98.01% | 98.19% | 98.31% | 98.37% | 98.42% | 98.25% | 98.36% | 98.4% | 98.21% | 98.16% | 98.14% | 98.21% | 98.12% | 97.73% | 97.01% | 98.42% | 19 | +190s | 180 | 40% | 0.40747 | 0.59253 | 2.6649 | 0.65256 | 0.34744 | 0.34744 |  | 57.72%
82 | 0:14 | 109.0898 | 110 | 3 | 0.5 | 110 | 5 | 20 | -11.4312 | -2.8578 | -2.8578 | 107.1422 | 107.1422 | -0.91024 | 97.82% | 97.89% | 97.93% | 97.94% | 98% | 98.1% | 98.06% | 98.04% | 98% | 98.17% | 98.2% | 98.04% | 97.98% | 97.97% | 98.04% | 98.2% | 98.29% | 98.33% | 98.39% | 98.25% | 98.38% | 98.42% | 98.24% | 98.19% | 98.18% | 98.25% | 98.18% | 97.8% | 97.11% | 94.91% | 98.42% | 21 | +210s | 200 | 33.33% | 0.38951 | 0.61049 | 2.8578 | 0.62381 | 0.37619 | 0.37619 |  | 56.46%
83 | 0:14 | 108.4839 | 110 | 3 | 0.5 | 110 | 5 | 20 | -12.1785 | -3.0446 | -3.0446 | 106.9554 | 106.9554 | -1.5161 | 97.88% | 97.91% | 97.96% | 98.03% | 98.1% | 98.07% | 98.04% | 97.99% | 98.17% | 98.21% | 98.06% | 98.02% | 98.01% | 98.06% | 98.2% | 98.26% | 98.28% | 98.35% | 98.25% | 98.38% | 98.43% | 98.27% | 98.22% | 98.21% | 98.29% | 98.22% | 97.86% | 97.2% | 95.07% | 88.7% | 98.43% | 20 | +200s | 190 | 36.67% | 0.3057 | 0.6943 | 3.0446 | 0.48959 | 0.51041 | 0.51041 |  | 62.05%
84 | 0:14 | 108.6706 | 110 | 3 | 0.5 | 110 | 5 | 20 | -12.8996 | -3.2249 | -3.2249 | 106.7751 | 106.7751 | -1.3294 | 97.9% | 97.97% | 98.05% | 98.1% | 98.07% | 98.03% | 97.97% | 98.17% | 98.22% | 98.08% | 98.06% | 98.05% | 98.08% | 98.19% | 98.22% | 98.23% | 98.3% | 98.24% | 98.39% | 98.44% | 98.28% | 98.24% | 98.24% | 98.33% | 98.26% | 97.92% | 97.28% | 95.22% | 88.95% | 80.94% | 98.44% | 19 | +190s | 180 | 40% | 0.3791 | 0.6209 | 3.2249 | 0.60713 | 0.39287 | 0.39287 |  | 59.24%
85 | 0:14 | 108.8107 | 110 | 3 | 0.5 | 110 | 5 | 20 | -13.5932 | -3.3983 | -3.3983 | 106.6017 | 106.6017 | -1.1893 | 97.97% | 98.07% | 98.09% | 98.07% | 98.01% | 97.94% | 98.15% | 98.21% | 98.09% | 98.09% | 98.07% | 98.09% | 98.18% | 98.18% | 98.17% | 98.25% | 98.22% | 98.38% | 98.44% | 98.29% | 98.25% | 98.25% | 98.35% | 98.29% | 97.97% | 97.35% | 95.36% | 89.19% | 81.29% | 66.29% | 98.44% | 18 | +180s | 170 | 43.33% | 0.4418 | 0.5582 | 3.3983 | 0.70755 | 0.29245 | 0.29245 |  | 57%
86 | 0:14 | 108.3194 | 110 | 3 | 0.5 | 110 | 5 | 20 | -14.2575 | -3.5644 | -3.5644 | 106.4356 | 106.4356 | -1.6806 | 98.07% | 98.08% | 98.05% | 97.98% | 97.9% | 98.13% | 98.2% | 98.09% | 98.12% | 98.09% | 98.09% | 98.16% | 98.12% | 98.1% | 98.19% | 98.2% | 98.37% | 98.43% | 98.3% | 98.26% | 98.26% | 98.37% | 98.32% | 98.01% | 97.42% | 95.5% | 89.43% | 81.63% | 66.79% | 46.99% | 98.43% | 17 | +170s | 160 | 46.67% | 0.37676 | 0.62324 | 3.5644 | 0.60338 | 0.39662 | 0.39662 |  | 61.59%
87 | 0:14 | 107.9472 | 110 | 3 | 0.5 | 110 | 5 | 20 | -14.8914 | -3.7228 | -3.7228 | 106.2772 | 106.2772 | -2.0528 | 98.05% | 98.03% | 97.95% | 97.86% | 98.1% | 98.19% | 98.08% | 98.13% | 98.1% | 98.09% | 98.13% | 98.06% | 98.03% | 98.12% | 98.16% | 98.34% | 98.41% | 98.29% | 98.26% | 98.27% | 98.38% | 98.33% | 98.04% | 97.47% | 95.63% | 89.66% | 81.97% | 67.29% | 47.61% | 81.74% | 98.41% | 16 | +160s | 150 | 50% | 0.334 | 0.666 | 3.7228 | 0.53491 | 0.46509 | 0.46509 |  | 64.97%
88 | 0:15 | 108.2945 | 110 | 3 | 0.5 | 110 | 5 | 20 | -15.4933 | -3.8733 | -3.8733 | 106.1267 | 106.1267 | -1.7055 | 98% | 97.91% | 97.8% | 98.06% | 98.16% | 98.07% | 98.14% | 98.1% | 98.07% | 98.09% | 97.99% | 97.94% | 98.04% | 98.12% | 98.31% | 98.39% | 98.28% | 98.25% | 98.26% | 98.38% | 98.34% | 98.06% | 97.53% | 95.76% | 89.89% | 82.31% | 67.78% | 48.24% | 81.91% | 79.32% | 98.39% | 15 | +150s | 140 | 53.33% | 0.43356 | 0.56644 | 3.8733 | 0.69435 | 0.30565 | 0.30565 |  | 60.76%
89 | 0:15 | 107.581 | 110 | 3 | 0.5 | 110 | 5 | 20 | -16.062 | -4.0155 | -4.0155 | 105.9845 | 105.9845 | -2.419 | 97.86% | 97.74% | 98.01% | 98.13% | 98.05% | 98.14% | 98.1% | 98.05% | 98.04% | 97.92% | 97.85% | 97.95% | 98.07% | 98.28% | 98.35% | 98.26% | 98.23% | 98.25% | 98.37% | 98.34% | 98.08% | 97.57% | 95.87% | 90.12% | 82.65% | 68.28% | 48.88% | 82.13% | 79.54% | 77.33% | 98.37% | 18 | +180s | 170 | 43.33% | 0.3193 | 0.6807 | 4.0155 | 0.51137 | 0.48863 | 0.48863 |  | 63.52%
90 | 0:15 | 107.2768 | 110 | 3 | 0.5 | 110 | 5 | 20 | -16.5963 | -4.1491 | -4.1491 | 105.8509 | 105.8509 | -2.7232 | 97.67% | 97.95% | 98.09% | 98.01% | 98.14% | 98.09% | 98.02% | 97.99% | 97.83% | 97.74% | 97.85% | 98.01% | 98.23% | 98.31% | 98.23% | 98.2% | 98.22% | 98.36% | 98.33% | 98.09% | 97.61% | 95.99% | 90.34% | 82.99% | 68.79% | 49.52% | 82.39% | 79.8% | 77.59% | 75.13% | 98.36% | 17 | +170s | 160 | 46.67% | 0.28518 | 0.71482 | 4.1491 | 0.45673 | 0.54327 | 0.54327 |  | 66.45%
91 | 0:15 | 107.2024 | 110 | 3 | 0.5 | 110 | 5 | 20 | -17.0951 | -4.2738 | -4.2738 | 105.7262 | 105.7262 | -2.7976 | 97.89% | 98.03% | 97.97% | 98.12% | 98.06% | 97.98% | 97.92% | 97.73% | 97.63% | 97.75% | 97.94% | 98.17% | 98.26% | 98.19% | 98.17% | 98.19% | 98.33% | 98.32% | 98.09% | 97.64% | 96.1% | 90.57% | 83.33% | 69.3% | 50.18% | 82.7% | 80.11% | 77.9% | 75.44% | 0% | 98.33% | 16 | +160s | 150 | 50% | 0.29523 | 0.70477 | 4.2738 | 0.47282 | 0.52718 | 0.52718 |  | 67.02%
92 | 0:15 | 107.2717 | 110 | 3 | 0.5 | 110 | 5 | 20 | -17.5572 | -4.3893 | -4.3893 | 105.6107 | 105.6107 | -2.7283 | 97.97% | 97.92% | 98.09% | 98.03% | 97.93% | 97.84% | 97.62% | 97.5% | 97.62% | 97.86% | 98.1% | 98.2% | 98.14% | 98.12% | 98.15% | 98.3% | 98.29% | 98.09% | 97.66% | 96.2% | 90.79% | 83.68% | 69.82% | 50.86% | 83.05% | 80.46% | 78.25% | 75.79% | 0% | 0% | 98.3% | 15 | +150s | 140 | 53.33% | 0.3322 | 0.6678 | 4.3893 | 0.53202 | 0.46798 | 0.46798 |  | 66.14%
93 | 0:15 | 107.5806 | 110 | 3 | 0.5 | 110 | 5 | 20 | -17.9816 | -4.4954 | -4.4954 | 105.5046 | 105.5046 | -2.4194 | 97.86% | 98.06% | 97.99% | 97.87% | 97.75% | 97.49% | 97.35% | 97.49% | 97.77% | 98.02% | 98.12% | 98.08% | 98.06% | 98.1% | 98.26% | 98.26% | 98.07% | 97.67% | 96.29% | 91.01% | 84.03% | 70.35% | 51.55% | 83.45% | 80.86% | 78.65% | 76.18% | 0% | 0% | 0% | 98.26% | 14 | +140s | 130 | 56.67% | 0.4152 | 0.5848 | 4.4954 | 0.66495 | 0.33505 | 0.33505 |  | 62.81%
94 | 0:16 | 107.2267 | 110 | 3 | 0.5 | 110 | 5 | 20 | -18.3676 | -4.5919 | -4.5919 | 105.4081 | 105.4081 | -2.7733 | 98.01% | 97.93% | 97.79% | 97.65% | 97.35% | 97.19% | 97.33% | 97.66% | 97.93% | 98.03% | 98% | 97.99% | 98.03% | 98.2% | 98.21% | 98.04% | 97.67% | 96.38% | 91.22% | 84.38% | 70.9% | 52.27% | 83.89% | 81.3% | 79.09% | 76.62% | 0% | 0% | 0% | 0% | 98.21% | 14 | +140s | 130 | 56.67% | 0.36372 | 0.63628 | 4.5919 | 0.58251 | 0.41749 | 0.41749 |  | 65.54%
95 | 0:16 | 106.8314 | 110 | 3 | 0.5 | 110 | 5 | 20 | -18.7141 | -4.6785 | -4.6785 | 105.3215 | 105.3215 | -3.1686 | 97.86% | 97.7% | 97.53% | 97.19% | 97.01% | 97.16% | 97.53% | 97.82% | 97.93% | 97.91% | 97.9% | 97.95% | 98.13% | 98.14% | 98% | 97.66% | 96.47% | 91.44% | 84.74% | 71.47% | 53.01% | 84.37% | 81.78% | 79.57% | 77.1% | 0% | 0% | 0% | 0% | 0% | 98.14% | 13 | +130s | 120 | 60% | 0.30199 | 0.69801 | 4.6785 | 0.48364 | 0.51636 | 0.51636 |  | 69.93%
96 | 0:16 | 106.5426 | 110 | 3 | 0.5 | 110 | 5 | 20 | -19.0206 | -4.7552 | -4.7552 | 105.2448 | 105.2448 | -3.4574 | 97.59% | 97.39% | 97.01% | 96.81% | 96.97% | 97.39% | 97.69% | 97.8% | 97.81% | 97.8% | 97.85% | 98.04% | 98.06% | 97.94% | 97.64% | 96.54% | 91.65% | 85.1% | 72.05% | 53.78% | 84.89% | 82.3% | 80.09% | 77.63% | 0% | 0% | 0% | 0% | 0% | 0% | 98.06% | 12 | +120s | 110 | 63.33% | 0.25956 | 0.74044 | 4.7552 | 0.41569 | 0.58431 | 0.58431 |  | 73.28%
97 | 0:16 | 106.3332 | 110 | 3 | 0.5 | 110 | 5 | 20 | -19.2863 | -4.8216 | -4.8216 | 105.1784 | 105.1784 | -3.6668 | 97.23% | 96.8% | 96.58% | 96.75% | 97.22% | 97.53% | 97.66% | 97.68% | 97.67% | 97.73% | 97.93% | 97.96% | 97.86% | 97.6% | 96.6% | 91.87% | 85.48% | 72.65% | 54.59% | 85.45% | 82.86% | 80.65% | 78.19% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 97.96% | 11 | +110s | 100 | 66.67% | 0.23095 | 0.76905 | 4.8216 | 0.36988 | 0.63012 | 0.63012 |  | 75.88%
98 | 0:16 | 105.9277 | 110 | 3 | 0.5 | 110 | 5 | 20 | -19.5107 | -4.8777 | -4.8777 | 105.1223 | 105.1223 | -4.0723 | 96.57% | 96.32% | 96.5% | 97.02% | 97.36% | 97.49% | 97.52% | 97.53% | 97.59% | 97.8% | 97.84% | 97.77% | 97.54% | 96.65% | 92.08% | 85.86% | 73.29% | 55.45% | 86.05% | 83.46% | 81.25% | 78.79% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 97.84% | 10 | +100s | 90 | 70% | 0.16109 | 0.83891 | 4.8777 | 0.25798 | 0.74202 | 0.74202 |  | 80.68%
99 | 0:16 | 105.8424 | 110 | 3 | 0.5 | 110 | 5 | 20 | -19.6933 | -4.9233 | -4.9233 | 105.0767 | 105.0767 | -4.1576 | 96.03% | 96.22% | 96.8% | 97.15% | 97.29% | 97.34% | 97.35% | 97.42% | 97.64% | 97.69% | 97.65% | 97.46% | 96.69% | 92.29% | 86.26% | 73.95% | 56.35% | 86.69% | 84.1% | 81.89% | 79.43% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 97.69% | 9 | +90s | 80 | 73.33% | 0.15314 | 0.84686 | 4.9233 | 0.24525 | 0.75475 | 0.75475 |  | 82.17%
100 | 0:17 | 105.9072 | 110 | 3 | 0.5 | 110 | 5 | 20 | -19.8337 | -4.9584 | -4.9584 | 105.0416 | 105.0416 | -4.0928 | 95.89% | 96.53% | 96.9% | 97.05% | 97.13% | 97.14% | 97.21% | 97.44% | 97.51% | 97.49% | 97.36% | 96.71% | 92.5% | 86.66% | 74.64% | 57.3% | 87.36% | 84.77% | 82.56% | 80.1% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 97.51% | 8 | +80s | 70 | 76.67% | 0.17311 | 0.82689 | 4.9584 | 0.27725 | 0.72275 | 0.72275 |  | 82.15%
101 | 0:17 | 106.2931 | 110 | 3 | 0.5 | 110 | 5 | 20 | -19.9315 | -4.9829 | -4.9829 | 105.0171 | 105.0171 | -3.7069 | 96.22% | 96.61% | 96.77% | 96.87% | 96.88% | 96.96% | 97.21% | 97.29% | 97.3% | 97.21% | 96.7% | 92.7% | 87.08% | 75.38% | 58.33% | 88.07% | 85.48% | 83.27% | 80.81% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 97.3% | 8 | +80s | 70 | 76.67% | 0.25521 | 0.74479 | 4.9829 | 0.40872 | 0.59128 | 0.59128 |  | 77.7%
102 | 0:17 | 105.3524 | 110 | 3 | 0.5 | 110 | 5 | 20 | -19.9867 | -4.9967 | -4.9967 | 105.0033 | 105.0033 | -4.6476 | 96.26% | 96.43% | 96.55% | 96.57% | 96.66% | 96.93% | 97.02% | 97.07% | 97.03% | 96.67% | 92.89% | 87.51% | 76.16% | 59.43% | 88.81% | 86.22% | 84.02% | 81.55% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 97.07% | 7 | +70s | 60 | 80% | 0.069818 | 0.93018 | 4.9967 | 0.11181 | 0.88819 | 0.88819 |  | 88.63%
103 | 0:17 | 105.0384 | 110 | 3 | 0.5 | 110 | 5 | 20 | -19.999 | -4.9998 | -4.9998 | 105.0002 | 105.0002 | -4.9616 | 96.03% | 96.17% | 96.2% | 96.3% | 96.58% | 96.69% | 96.77% | 96.79% | 96.59% | 93.06% | 87.95% | 76.99% | 60.61% | 89.59% | 87% | 84.79% | 82.33% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 96.79% | 7 | +70s | 60 | 80% | 0.0076318 | 0.99237 | 4.9998 | 0.012222 | 0.98778 | 0.98778 |  | 91.86%
104 | 0:17 | 105.7528 | 110 | 3 | 0.5 | 110 | 5 | 20 | -19.9685 | -4.9921 | -4.9921 | 105.0079 | 105.0079 | -4.2472 | 95.71% | 95.74% | 95.85% | 96.15% | 96.27% | 96.4% | 96.48% | 96.47% | 93.21% | 88.39% | 77.88% | 61.9% | 90.39% | 87.8% | 85.59% | 83.13% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 96.48% | 6 | +60s | 50 | 83.33% | 0.14899 | 0.85101 | 4.9921 | 0.2386 | 0.7614 | 0.7614 |  | 85.32%
105 | 0:17 | 105.5183 | 110 | 3 | 0.5 | 110 | 5 | 20 | -19.8952 | -4.9738 | -4.9738 | 105.0262 | 105.0262 | -4.4817 | 95.17% | 95.29% | 95.61% | 95.75% | 95.93% | 96.08% | 96.27% | 93.33% | 88.85% | 78.83% | 63.31% | 91.22% | 88.63% | 86.42% | 83.96% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 96.27% | 6 | +60s | 50 | 83.33% | 0.098426 | 0.90157 | 4.9738 | 0.15763 | 0.84237 | 0.84237 |  | 87.95%
106 | 0:18 | 104.8956 | 110 | 3 | 0.5 | 110 | 5 | 20 | -19.7792 | -4.9448 | -4.9448 | 105.0552 | 105.0552 | -5.1044 | 94.59% | 94.93% | 95.1% | 95.32% | 95.56% | 95.98% | 93.39% | 89.29% | 79.84% | 64.86% | 92.08% | 89.49% | 87.28% | 84.82% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 95.98% | 5 | +50s | 40 | 86.67% | 0.031925 | 0.96807 | 4.9448 | 0.051129 | 0.94887 | 0.94887 |  | 92.51%
107 | 0:18 | 104.4177 | 110 | 3 | 0.5 | 110 | 5 | 20 | -19.6209 | -4.9052 | -4.9052 | 105.0948 | 105.0948 | -5.5823 | 94.07% | 94.26% | 94.54% | 94.88% | 95.56% | 93.38% | 89.72% | 80.93% | 66.58% | 92.96% | 90.37% | 88.16% | 85.7% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 95.56% | 4 | +40s | 30 | 90% | 0.13541 | 0.86459 | 4.9052 | 0.21686 | 0.78314 | 0.78314 |  | 87.96%
108 | 0:18 | 104.8001 | 110 | 3 | 0.5 | 110 | 5 | 20 | -19.4205 | -4.8551 | -4.8551 | 105.1449 | 105.1449 | -5.1999 | 93.17% | 93.52% | 93.97% | 94.95% | 93.25% | 90.11% | 82.09% | 68.48% | 93.87% | 91.27% | 89.07% | 86.6% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 94.95% | 3 | +30s | 20 | 93.33% | 0.06896 | 0.93104 | 4.8551 | 0.11044 | 0.88956 | 0.88956 |  | 92.41%
109 | 0:18 | 104.7381 | 90 | 3 | 0.5 | 109.5 | 5 | 20 | -19.1785 | -4.7946 | -4.7946 | 85.2054 | 104.7054 | -4.7619 | 92.17% | 92.74% | 94.08% | 92.94% | 90.4% | 83.31% | 70.59% | 94.79% | 92.2% | 89.99% | 87.53% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 94.79% | 7 | +70s | 60 | 80% | 0.006551 | 0.99345 | 4.7946 | 0.010491 | 0.98951 | 0.98951 |  | 91.25%
110 | 0:18 | 104.3652 | 90 | 3 | 0.5 | 109 | 5 | 20 | -18.8954 | -4.7238 | -4.7238 | 85.2762 | 104.2762 | -4.6348 | 91.05% | 92.81% | 92.34% | 90.54% | 84.57% | 72.94% | 95.73% | 93.14% | 90.93% | 88.47% | 2.708% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 95.73% | 6 | +60s | 50 | 83.33% | 0.0178 | 0.9822 | 4.7238 | 0.028507 | 0.97149 | 0.97149 |  | 92.07%
111 | 0:18 | 104.4322 | 90 | 3 | 0.5 | 108.5 | 5 | 20 | -18.5718 | -4.6429 | -4.6429 | 85.3571 | 103.8571 | -4.0678 | 90.96% | 91.3% | 90.39% | 85.79% | 75.52% | 96.69% | 94.1% | 91.89% | 89.43% | 8.31% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 96.69% | 5 | +50s | 40 | 86.67% | 0.11503 | 0.88497 | 4.6429 | 0.18423 | 0.81577 | 0.81577 |  | 88.31%
112 | 0:19 | 104.9969 | 90 | 3 | 0.5 | 108 | 5 | 20 | -18.2084 | -4.5521 | -4.5521 | 85.4479 | 103.4479 | -3.0031 | 89.55% | 89.74% | 86.85% | 78.3% | 97.67% | 95.08% | 92.87% | 90.41% | 15.15% | 3.893% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 97.67% | 4 | +40s | 30 | 90% | 0.30981 | 0.69019 | 4.5521 | 0.49616 | 0.50384 | 0.50384 |  | 79.35%
113 | 0:19 | 104.6507 | 90 | 3 | 0.5 | 107.5 | 5 | 20 | -17.806 | -4.4515 | -4.4515 | 85.5485 | 103.0485 | -2.8493 | 93.82% | 96.01% | 98.71% | 98.66% | 96.06% | 93.86% | 91.39% | 89.16% | 86.87% | 84.77% | 82.56% | 80.23% | 77.98% | 76.46% | 75.2% | 73.78% | 72.56% | 71.94% | 71.32% | 70.32% | 70.03% | 70.22% | 69.98% | 70.16% | 70.87% | 71.95% | 72.91% | 74.17% | 75.35% | 76.26% | 98.71% | 2 | +20s | 10 | 96.67% | 0.32043 | 0.67957 | 4.4515 | 0.51318 | 0.48682 | 0.48682 |  | 81.35%
114 | 0:19 | 105.2228 | 90 | 3 | 0.5 | 107 | 5 | 20 | -17.3654 | -4.3413 | -4.3413 | 85.6587 | 102.6587 | -1.7772 | 95.01% | 97.71% | 99.65% | 97.06% | 94.85% | 92.39% | 90.16% | 87.87% | 85.77% | 83.56% | 81.23% | 78.98% | 77.46% | 76.2% | 74.78% | 73.56% | 72.93% | 72.32% | 71.32% | 71.02% | 71.22% | 70.98% | 71.16% | 71.87% | 72.94% | 73.91% | 75.16% | 76.35% | 77.26% | 77.8% | 99.65% | 2 | +20s | 10 | 96.67% | 0.51284 | 0.48716 | 4.3413 | 0.82131 | 0.17869 | 0.17869 |  | 71.4%
115 | 0:19 | 105.3444 | 90 | 3 | 0.5 | 106.5 | 5 | 20 | -16.8876 | -4.2219 | -4.2219 | 85.7781 | 102.2781 | -1.1556 | 96.7% | 99.34% | 98.07% | 95.86% | 93.4% | 91.17% | 88.87% | 86.78% | 84.57% | 82.23% | 79.99% | 78.47% | 77.21% | 75.79% | 74.56% | 73.94% | 73.33% | 72.33% | 72.03% | 72.22% | 71.98% | 72.16% | 72.87% | 73.95% | 74.91% | 76.17% | 77.36% | 78.27% | 78.8% | 79.67% | 99.34% | 1 | +10s | 0 | 100% | 0.61326 | 0.38674 | 4.2219 | 0.98214 | 0.017859 | 0.017859 |  | 67.04%
116 | 0:19 | 104.6102 | 90 | 3 | 0.5 | 106 | 5 | 20 | -16.3736 | -4.0934 | -4.0934 | 85.9066 | 101.9066 | -1.3898 | 98.33% | 99.08% | 96.87% | 94.41% | 92.18% | 89.88% | 87.79% | 85.58% | 83.25% | 81% | 79.48% | 78.22% | 76.8% | 75.58% | 74.95% | 74.34% | 73.34% | 73.04% | 73.24% | 72.99% | 73.18% | 73.88% | 74.96% | 75.93% | 77.18% | 78.37% | 79.28% | 79.81% | 80.69% | 80.83% | 99.08% | 1 | +10s | 0 | 100% | 0.54073 | 0.45927 | 4.0934 | 0.86599 | 0.13401 | 0.13401 |  | 70.83%
117 | 0:19 | 104.5439 | 90 | 3 | 0.5 | 105.5 | 5 | 20 | -15.8246 | -3.9561 | -3.9561 | 86.0439 | 101.5439 | -0.95613 | 99.9% | 97.89% | 95.42% | 93.19% | 90.9% | 88.8% | 86.59% | 84.26% | 82.01% | 80.49% | 79.23% | 77.81% | 76.59% | 75.97% | 75.35% | 74.35% | 74.06% | 74.25% | 74.01% | 74.19% | 74.9% | 75.98% | 76.94% | 78.2% | 79.39% | 80.3% | 80.83% | 81.7% | 81.85% | 82% | 99.9% | 0 | No Time Shift | 0 | 100% | 0.6 | 0.4 | 3.9561 | 0.96091 | 0.039087 | 0.039087 |  | 67.94%
118 | 0:20 | 103.8577 | 90 | 3 | 0.5 | 105 | 5 | 20 | -15.2416 | -3.8104 | -3.8104 | 86.1896 | 101.1896 | -1.1423 | 98.9% | 96.44% | 94.21% | 91.92% | 89.82% | 87.61% | 85.28% | 83.03% | 81.51% | 80.25% | 78.83% | 77.61% | 76.99% | 76.37% | 75.37% | 75.07% | 75.27% | 75.03% | 75.21% | 75.92% | 77% | 77.96% | 79.21% | 80.4% | 81.31% | 81.85% | 82.72% | 82.87% | 83.02% | 83.41% | 98.9% | 0 | No Time Shift | 0 | 100% | 0.53362 | 0.46638 | 3.8104 | 0.8546 | 0.1454 | 0.1454 |  | 71.15%
119 | 0:20 | 103.4678 | 90 | 3 | 0.5 | 104.5 | 5 | 20 | -14.6259 | -3.6565 | -3.6565 | 86.3435 | 100.8435 | -1.0322 | 97.46% | 95.23% | 92.93% | 90.84% | 88.63% | 86.3% | 84.05% | 82.53% | 81.27% | 79.85% | 78.63% | 78% | 77.39% | 76.39% | 76.09% | 76.29% | 76.04% | 76.23% | 76.93% | 78.01% | 78.98% | 80.23% | 81.42% | 82.33% | 82.86% | 83.74% | 83.88% | 84.03% | 84.43% | 84.14% | 97.46% | 0 | No Time Shift | 0 | 100% | 0.52485 | 0.47515 | 3.6565 | 0.84056 | 0.15944 | 0.15944 |  | 71.13%
120 | 0:20 | 103.389 | 90 | 3 | 0.5 | 104 | 5 | 20 | -13.979 | -3.4947 | -3.4947 | 86.5053 | 100.5053 | -0.61104 | 96.24% | 93.95% | 91.85% | 89.64% | 87.31% | 85.06% | 83.54% | 82.28% | 80.86% | 79.64% | 79.02% | 78.4% | 77.4% | 77.11% | 77.3% | 77.06% | 77.24% | 77.95% | 79.03% | 79.99% | 81.24% | 82.43% | 83.34% | 83.88% | 84.75% | 84.9% | 85.05% | 85.44% | 85.15% | 85.39% | 96.24% | 0 | No Time Shift | 0 | 100% | 0.57674 | 0.42326 | 3.4947 | 0.92366 | 0.07634 | 0.07634 |  | 67.96%
121 | 0:20 | 103.4399 | 90 | 3 | 0.5 | 103.5 | 5 | 20 | -13.302 | -3.3255 | -3.3255 | 86.6745 | 100.1745 | -0.060144 | 94.96% | 92.86% | 90.65% | 88.32% | 86.07% | 84.55% | 83.29% | 81.87% | 80.65% | 80.03% | 79.41% | 78.41% | 78.12% | 78.31% | 78.07% | 78.25% | 78.96% | 80.04% | 81% | 82.25% | 83.44% | 84.35% | 84.89% | 85.76% | 85.91% | 86.06% | 86.45% | 86.16% | 86.4% | 87.42% | 94.96% | 0 | No Time Shift | 0 | 100% | 0.65307 | 0.34693 | 3.3255 | 1.0459 | 0 | 0 |  | 64.99%
122 | 0:20 | 102.8678 | 90 | 3 | 0.5 | 103 | 5 | 20 | -12.5966 | -3.1491 | -3.1491 | 86.8509 | 99.8509 | -0.13221 | 93.87% | 91.66% | 89.32% | 87.07% | 85.55% | 84.3% | 82.87% | 81.65% | 81.03% | 80.42% | 79.41% | 79.12% | 79.31% | 79.07% | 79.25% | 79.96% | 81.04% | 82% | 83.26% | 84.45% | 85.36% | 85.89% | 86.76% | 86.91% | 87.06% | 87.45% | 87.16% | 87.41% | 88.43% | 89.58% | 93.87% | 0 | No Time Shift | 0 | 100% | 0.60339 | 0.39661 | 3.1491 | 0.96634 | 0.033664 | 0.033664 |  | 65.74%
123 | 0:20 | 102.6602 | 90 | 3 | 0.5 | 102.5 | 5 | 20 | -11.8641 | -2.966 | -2.966 | 87.034 | 99.534 | 0.16024 | 92.91% | 93.56% | 93.12% | 90.44% | 87.17% | 84.75% | 82.73% | 79.1% | 75.48% | 72.24% | 69.93% | 67.71% | 65.27% | 62.8% | 61.84% | 63.23% | 65.53% | 66.75% | 70.37% | 74.89% | 77.06% | 78.87% | 79.13% | 76.85% | 75.78% | 76.44% | 76.77% | 73.39% | 67.28% | 57.53% | 93.56% | 1 | +10s | 0 | 100% | 0.62526 | 0.37474 | 2.966 | 1.0014 | 0 | 0 |  | 64.52%
124 | 0:21 | 102.2272 | 90 | 3 | 0.5 | 102 | 5 | 20 | -11.1063 | -2.7766 | -2.7766 | 87.2234 | 99.2234 | 0.2272 | 93.28% | 93.81% | 92.05% | 89.6% | 87.84% | 86.29% | 83.22% | 80.15% | 77.46% | 75.44% | 73.45% | 71.3% | 69.07% | 68.17% | 69.42% | 71.49% | 72.6% | 75.93% | 80.07% | 82.03% | 83.7% | 83.94% | 81.9% | 80.94% | 81.5% | 81.8% | 78.66% | 72.95% | 63.78% | 54.32% | 93.81% | 1 | +10s | 0 | 100% | 0.60075 | 0.39925 | 2.7766 | 0.96212 | 0.037881 | 0.037881 |  | 65.87%
125 | 0:21 | 102.1415 | 90 | 3 | 0.5 | 101.5 | 5 | 20 | -10.3246 | -2.5812 | -2.5812 | 87.4188 | 98.9188 | 0.64154 | 93.86% | 92.85% | 91.08% | 89.85% | 88.69% | 86.1% | 83.48% | 81.25% | 79.48% | 77.68% | 75.78% | 73.76% | 72.91% | 74.03% | 75.91% | 76.92% | 80% | 83.81% | 85.6% | 87.14% | 87.36% | 85.53% | 84.66% | 85.15% | 85.41% | 82.49% | 77.13% | 68.47% | 59.45% | 50.38% | 93.86% | 0 | No Time Shift | 0 | 100% | 0.64454 | 0.35546 | 2.5812 | 1.0322 | 0 | 0 |  | 64.62%
126 | 0:21 | 101.0882 | 90 | 3 | 0.5 | 101 | 5 | 20 | -9.5208 | -2.3802 | -2.3802 | 87.6198 | 98.6198 | 0.088158 | 93.17% | 91.97% | 91.18% | 90.34% | 88.14% | 85.91% | 84.07% | 82.5% | 80.86% | 79.17% | 77.34% | 76.52% | 77.54% | 79.25% | 80.18% | 83.05% | 86.58% | 88.22% | 89.65% | 89.85% | 88.2% | 87.4% | 87.83% | 88.06% | 85.33% | 80.27% | 72.08% | 63.44% | 54.73% | 40.1% | 93.17% | 0 | No Time Shift | 0 | 100% | 0.49367 | 0.50633 | 2.3802 | 0.79063 | 0.20937 | 0.20937 |  | 71.37%
127 | 0:21 | 100.679 | 90 | 3 | 0.5 | 100.5 | 5 | 20 | -8.6966 | -2.1742 | -2.1742 | 87.8258 | 98.3258 | 0.17905 | 92.48% | 92.06% | 91.49% | 89.63% | 87.72% | 86.2% | 84.82% | 83.32% | 81.8% | 80.12% | 79.35% | 80.28% | 81.85% | 82.71% | 85.38% | 88.67% | 90.18% | 91.52% | 91.7% | 90.21% | 89.47% | 89.84% | 90.05% | 87.48% | 82.69% | 74.89% | 66.6% | 58.21% | 43.95% | 33.99% | 92.48% | 0 | No Time Shift | 0 | 100% | 0.47064 | 0.52936 | 2.1742 | 0.75374 | 0.24626 | 0.24626 |  | 72.37%
128 | 0:21 | 100.9147 | 90 | 3 | 0.5 | 100 | 5 | 20 | -7.8538 | -1.9635 | -1.9635 | 88.0365 | 98.0365 | 0.91466 | 92.64% | 92.3% | 90.73% | 89.1% | 87.86% | 86.62% | 85.25% | 83.88% | 82.33% | 81.6% | 82.45% | 83.9% | 84.69% | 87.2% | 90.28% | 91.68% | 92.94% | 93.1% | 91.75% | 91.07% | 91.38% | 91.58% | 89.15% | 84.6% | 77.15% | 69.15% | 61.05% | 47.13% | 37.41% | 27.66% | 93.1% | 17 | +170s | 160 | 46.67% | 0.57562 | 0.42438 | 1.9635 | 0.92187 | 0.07813 | 0.07813 |  | 49.19%
129 | 0:21 | 100.8241 | 90 | 3 | 0.5 | 99.5 | 5 | 20 | -6.9942 | -1.7485 | -1.7485 | 88.2515 | 97.7515 | 1.3241 | 92.88% | 91.56% | 90.17% | 89.17% | 88.06% | 86.79% | 85.56% | 84.13% | 83.42% | 84.2% | 85.54% | 86.29% | 88.65% | 91.55% | 92.84% | 94.04% | 94.19% | 92.95% | 92.32% | 92.59% | 92.77% | 90.47% | 86.12% | 78.98% | 71.26% | 63.41% | 49.79% | 40.29% | 30.62% | 93.8% | 94.19% | 16 | +160s | 150 | 50% | 0.61452 | 0.38548 | 1.7485 | 0.98417 | 0.015835 | 0.015835 |  | 48.59%
130 | 0:22 | 99.7835 | 90 | 3 | 0.5 | 99 | 5 | 20 | -6.1195 | -1.5299 | -1.5299 | 88.4701 | 97.4701 | 0.78351 | 92.19% | 91.01% | 90.22% | 89.23% | 88.05% | 86.94% | 85.6% | 84.93% | 85.64% | 86.89% | 87.59% | 89.83% | 92.56% | 93.77% | 94.9% | 95.04% | 93.9% | 93.31% | 93.55% | 93.71% | 91.52% | 87.36% | 80.49% | 73.01% | 65.4% | 52.06% | 42.75% | 33.17% | 92.93% | 92.1% | 95.04% | 15 | +150s | 140 | 53.33% | 0.46268 | 0.53732 | 1.5299 | 0.74099 | 0.25901 | 0.25901 |  | 58.09%
131 | 0:22 | 99.5284 | 90 | 3 | 0.5 | 98.5 | 5 | 20 | -5.2318 | -1.3079 | -1.3079 | 88.6921 | 97.1921 | 1.0284 | 91.68% | 91.07% | 90.18% | 89.09% | 88.08% | 86.84% | 86.18% | 86.85% | 88.02% | 88.67% | 90.8% | 93.38% | 94.51% | 95.59% | 95.72% | 94.67% | 94.12% | 94.33% | 94.48% | 92.38% | 88.38% | 81.77% | 74.5% | 67.1% | 54.01% | 44.88% | 35.37% | 92.09% | 91.25% | 90.45% | 95.72% | 14 | +140s | 130 | 56.67% | 0.46728 | 0.53272 | 1.3079 | 0.74835 | 0.25165 | 0.25165 |  | 59.18%
132 | 0:22 | 99.5974 | 90 | 3 | 0.5 | 98 | 5 | 20 | -4.3328 | -1.0832 | -1.0832 | 88.9168 | 96.9168 | 1.5974 | 91.78% | 90.98% | 89.96% | 89.05% | 87.88% | 87.25% | 87.87% | 88.96% | 89.57% | 91.6% | 94.06% | 95.12% | 96.15% | 96.27% | 95.3% | 94.78% | 94.96% | 95.1% | 93.1% | 89.24% | 82.85% | 75.78% | 68.56% | 55.71% | 46.75% | 37.31% | 91.27% | 90.43% | 89.63% | 88.31% | 96.27% | 13 | +130s | 120 | 60% | 0.53613 | 0.46387 | 1.0832 | 0.85861 | 0.14139 | 0.14139 |  | 56.8%
133 | 0:22 | 99.2916 | 90 | 3 | 0.5 | 97.5 | 5 | 20 | -3.4245 | -0.85613 | -0.85613 | 89.1439 | 96.6439 | 1.7916 | 91.66% | 90.7% | 89.87% | 88.78% | 88.17% | 88.74% | 89.77% | 90.35% | 92.28% | 94.62% | 95.62% | 96.6% | 96.72% | 95.82% | 95.33% | 95.49% | 95.61% | 93.69% | 89.97% | 83.78% | 76.9% | 69.85% | 57.21% | 48.4% | 39.04% | 90.48% | 89.64% | 88.84% | 87.52% | 86.33% | 96.72% | 12 | +120s | 110 | 63.33% | 0.52954 | 0.47046 | 0.85613 | 0.84807 | 0.15193 | 0.15193 |  | 58.41%
134 | 0:22 | 98.7429 | 90 | 3 | 0.5 | 97 | 5 | 20 | -2.5089 | -0.62723 | -0.62723 | 89.3728 | 96.3728 | 1.7429 | 91.34% | 90.58% | 89.56% | 88.97% | 89.5% | 90.47% | 91.01% | 92.87% | 95.09% | 96.04% | 96.98% | 97.08% | 96.25% | 95.8% | 95.92% | 96.04% | 94.19% | 90.6% | 84.59% | 77.88% | 70.99% | 58.55% | 49.88% | 40.58% | 89.72% | 88.88% | 88.08% | 86.76% | 85.57% | 85.31% | 97.08% | 11 | +110s | 100 | 66.67% | 0.47403 | 0.52597 | 0.62723 | 0.75917 | 0.24083 | 0.24083 |  | 62.61%
135 | 0:22 | 98.6505 | 90 | 3 | 0.5 | 96.5 | 5 | 20 | -1.588 | -0.39699 | -0.39699 | 89.603 | 96.103 | 2.1505 | 91.2% | 90.24% | 89.67% | 90.17% | 91.07% | 91.59% | 93.37% | 95.5% | 96.39% | 97.29% | 97.39% | 96.62% | 96.19% | 96.3% | 96.4% | 94.62% | 91.14% | 85.31% | 78.74% | 72% | 59.75% | 51.21% | 41.97% | 88.99% | 88.16% | 87.35% | 86.03% | 84.85% | 84.58% | 84.42% | 97.39% | 10 | +100s | 90 | 70% | 0.5095 | 0.4905 | 0.39699 | 0.81597 | 0.18403 | 0.18403 |  | 61.93%
136 | 0:23 | 98.1237 | 90 | 3 | 0.5 | 96 | 5 | 20 | -0.66358 | -0.1659 | -0.1659 | 89.8341 | 95.8341 | 2.1237 | 90.85% | 90.29% | 90.75% | 91.61% | 92.1% | 93.8% | 95.84% | 96.69% | 97.55% | 97.65% | 96.93% | 96.52% | 96.61% | 96.71% | 94.99% | 91.61% | 85.94% | 79.52% | 72.91% | 60.84% | 52.42% | 43.24% | 88.29% | 87.46% | 86.66% | 85.33% | 84.15% | 83.89% | 83.73% | 83.32% | 97.65% | 9 | +90s | 80 | 73.33% | 0.45791 | 0.54209 | 0.1659 | 0.73335 | 0.26665 | 0.26665 |  | 65.88%
137 | 0:23 | 97.8604 | 90 | 3 | 0.5 | 95.5 | 5 | 20 | 0.26221 | 0.065553 | 0.065553 | 90.0656 | 95.5656 | 2.3604 | 90.84% | 91.27% | 92.08% | 92.55% | 94.19% | 96.14% | 96.94% | 97.77% | 97.86% | 97.2% | 96.81% | 96.88% | 96.97% | 95.32% | 92.03% | 86.51% | 80.22% | 73.74% | 61.83% | 53.53% | 44.41% | 87.64% | 86.8% | 86% | 84.68% | 83.49% | 83.23% | 83.07% | 82.66% | 82.83% | 97.86% | 8 | +80s | 70 | 76.67% | 0.45897 | 0.54103 | 0.065553 | 0.73505 | 0.26495 | 0.26495 |  | 67.01%
138 | 0:23 | 97.7562 | 90 | 3 | 0.5 | 95 | 5 | 20 | 1.1874 | 0.29686 | 0.29686 | 90.2969 | 95.2969 | 2.7562 | 91.74% | 92.51% | 92.95% | 94.53% | 96.4% | 97.16% | 97.96% | 98.04% | 97.43% | 97.06% | 97.12% | 97.2% | 95.6% | 92.41% | 87.02% | 80.86% | 74.5% | 62.74% | 54.55% | 45.49% | 87.01% | 86.18% | 85.37% | 84.05% | 82.87% | 82.61% | 82.45% | 82.04% | 82.21% | 82.42% | 98.04% | 7 | +70s | 60 | 80% | 0.49187 | 0.50813 | 0.29686 | 0.78775 | 0.21225 | 0.21225 |  | 66.42%
139 | 0:23 | 97.5942 | 90 | 3 | 0.5 | 94.5 | 5 | 20 | 2.1101 | 0.52753 | 0.52753 | 90.5275 | 95.0275 | 3.0942 | 92.89% | 93.31% | 94.83% | 96.62% | 97.35% | 98.12% | 98.2% | 97.63% | 97.28% | 97.32% | 97.4% | 95.84% | 92.74% | 87.49% | 81.45% | 75.2% | 63.59% | 55.5% | 46.49% | 86.43% | 85.6% | 84.79% | 83.47% | 82.29% | 82.02% | 81.86% | 81.46% | 81.63% | 81.84% | 82.14% | 98.2% | 6 | +60s | 50 | 83.33% | 0.51334 | 0.48666 | 0.52753 | 0.82212 | 0.17788 | 0.17788 |  | 66.44%
140 | 0:23 | 96.6967 | 90 | 3 | 0.5 | 94 | 5 | 20 | 3.0283 | 0.75708 | 0.75708 | 90.7571 | 94.7571 | 2.6967 | 93.63% | 95.1% | 96.82% | 97.51% | 98.25% | 98.33% | 97.8% | 97.48% | 97.5% | 97.57% | 96.06% | 93.04% | 87.92% | 81.99% | 75.85% | 64.38% | 56.39% | 47.43% | 85.88% | 85.05% | 84.25% | 82.92% | 81.74% | 81.48% | 81.32% | 80.91% | 81.08% | 81.29% | 81.6% | 82.1% | 98.33% | 5 | +50s | 40 | 86.67% | 0.38792 | 0.61208 | 0.75708 | 0.62126 | 0.37874 | 0.37874 |  | 74.29%
141 | 0:23 | 96.6667 | 90 | 3 | 0.5 | 93.5 | 5 | 20 | 3.94 | 0.985 | 0.985 | 90.985 | 94.485 | 3.1667 | 95.34% | 97% | 97.65% | 98.37% | 98.44% | 97.95% | 97.64% | 97.65% | 97.72% | 96.26% | 93.32% | 88.31% | 82.49% | 76.45% | 65.11% | 57.22% | 48.31% | 85.38% | 84.54% | 83.74% | 82.42% | 81.23% | 80.97% | 80.81% | 80.41% | 80.58% | 80.79% | 81.09% | 81.6% | 82.26% | 98.44% | 4 | +40s | 30 | 90% | 0.43634 | 0.56366 | 0.985 | 0.6988 | 0.3012 | 0.3012 |  | 72.85%
142 | 0:24 | 96.5458 | 90 | 3 | 0.5 | 93 | 5 | 20 | 4.8432 | 1.2108 | 1.2108 | 91.2108 | 94.2108 | 3.5458 | 97.16% | 97.77% | 98.46% | 98.53% | 98.08% | 97.79% | 97.79% | 97.85% | 96.43% | 93.57% | 88.67% | 82.95% | 77.02% | 65.81% | 58.01% | 49.15% | 84.92% | 84.08% | 83.28% | 81.95% | 80.77% | 80.51% | 80.35% | 79.94% | 80.11% | 80.33% | 80.63% | 81.13% | 81.8% | 82.46% | 98.53% | 3 | +30s | 20 | 93.33% | 0.467 | 0.533 | 1.2108 | 0.74791 | 0.25209 | 0.25209 |  | 72.36%
143 | 0:24 | 96.0388 | 90 | 3 | 0.5 | 92.5 | 5 | 20 | 5.7361 | 1.434 | 1.434 | 91.434 | 93.934 | 3.5388 | 97.88% | 98.55% | 98.61% | 98.2% | 97.93% | 97.9% | 97.96% | 96.59% | 93.79% | 89.01% | 83.39% | 77.55% | 66.47% | 58.75% | 49.95% | 84.49% | 83.66% | 82.86% | 81.53% | 80.35% | 80.09% | 79.93% | 79.52% | 79.69% | 79.9% | 80.21% | 80.71% | 81.38% | 82.04% | 82.63% | 98.61% | 2 | +20s | 10 | 96.67% | 0.42095 | 0.57905 | 1.434 | 0.67416 | 0.32584 | 0.32584 |  | 75.95%
144 | 0:24 | 95.2501 | 90 | 3 | 0.5 | 92 | 5 | 20 | 6.6166 | 1.6542 | 1.6542 | 91.6542 | 93.6542 | 3.2501 | 98.62% | 98.67% | 98.3% | 98.04% | 98.01% | 98.06% | 96.73% | 94% | 89.33% | 83.8% | 78.06% | 67.1% | 59.47% | 50.71% | 84.12% | 83.28% | 82.48% | 81.16% | 79.97% | 79.71% | 79.55% | 79.14% | 79.32% | 79.53% | 79.83% | 80.33% | 81% | 81.66% | 82.25% | 83.44% | 98.67% | 1 | +10s | 0 | 100% | 0.31919 | 0.68081 | 1.6542 | 0.5112 | 0.4888 | 0.4888 |  | 82.52%
145 | 0:24 | 95.2131 | 90 | 3 | 0.5 | 91.5 | 5 | 20 | 7.483 | 1.8708 | 1.8708 | 91.8708 | 93.3708 | 3.7131 | 98.73% | 98.39% | 98.15% | 98.1% | 98.15% | 96.86% | 94.2% | 89.63% | 84.2% | 78.54% | 67.7% | 60.15% | 51.44% | 83.78% | 82.95% | 82.14% | 80.82% | 79.64% | 79.38% | 79.22% | 78.81% | 78.98% | 79.19% | 79.5% | 80% | 80.67% | 81.33% | 81.92% | 83.11% | 53.32% | 98.73% | 0 | No Time Shift | 0 | 100% | 0.36848 | 0.63152 | 1.8708 | 0.59012 | 0.40988 | 0.40988 |  | 79.91%
146 | 0:24 | 94.411 | 90 | 3 | 0.5 | 91 | 5 | 20 | 8.3334 | 2.0833 | 2.0833 | 92.0833 | 93.0833 | 3.411 | 98.47% | 98.24% | 98.18% | 98.22% | 96.97% | 94.38% | 89.91% | 84.57% | 79% | 68.28% | 60.81% | 52.15% | 83.49% | 82.66% | 81.86% | 80.53% | 79.35% | 79.09% | 78.93% | 78.52% | 78.69% | 78.9% | 79.21% | 79.71% | 80.38% | 81.04% | 81.63% | 82.82% | 52.69% | 58.53% | 98.47% | 0 | No Time Shift | 0 | 100% | 0.26553 | 0.73447 | 2.0833 | 0.42525 | 0.57475 | 0.57475 |  | 85.31%
147 | 0:24 | 94.0621 | 90 | 3 | 0.5 | 90.5 | 5 | 20 | 9.1659 | 2.2915 | 2.2915 | 92.2915 | 92.7915 | 3.5621 | 98.32% | 98.25% | 98.29% | 97.08% | 94.55% | 90.17% | 84.93% | 79.45% | 68.84% | 61.45% | 52.83% | 83.25% | 82.42% | 81.61% | 80.29% | 79.11% | 78.84% | 78.69% | 78.28% | 78.45% | 78.66% | 78.96% | 79.47% | 80.13% | 80.8% | 81.39% | 82.57% | 52.07% | 57.93% | 65.57% | 98.32% | 0 | No Time Shift | 0 | 100% | 0.25412 | 0.74588 | 2.2915 | 0.40698 | 0.59302 | 0.59302 |  | 85.87%
148 | 0:24 | 94.5601 | 90 | 3 | 0.5 | 90 | 5 | 20 | 9.9787 | 2.4947 | 2.4947 | 92.4947 | 92.4947 | 4.5601 | 98.31% | 98.34% | 97.17% | 94.7% | 90.43% | 85.27% | 79.87% | 69.38% | 62.07% | 53.5% | 83.05% | 82.22% | 81.41% | 80.09% | 78.91% | 78.65% | 78.49% | 78.08% | 78.25% | 78.46% | 78.77% | 79.27% | 79.94% | 80.6% | 81.19% | 82.38% | 51.45% | 57.35% | 65.05% | 70.59% | 98.34% | 1 | +10s | 0 | 100% | 0.41309 | 0.58691 | 2.4947 | 0.66157 | 0.33843 | 0.33843 |  | 77.4%
149 | 0:25 | 94.2437 | 90 | 3 | 0.5 | 90 | 5 | 20 | 10.7702 | 2.6925 | 2.6925 | 92.6925 | 92.6925 | 4.2437 | 98.39% | 97.25% | 94.85% | 90.67% | 85.6% | 80.29% | 69.91% | 62.68% | 54.15% | 82.9% | 82.07% | 81.26% | 79.94% | 78.76% | 78.5% | 78.34% | 77.93% | 78.1% | 78.31% | 78.62% | 79.12% | 79.78% | 80.45% | 81.04% | 82.23% | 50.84% | 56.76% | 64.54% | 70.13% | 75.92% | 98.39% | 0 | No Time Shift | 0 | 100% | 0.31024 | 0.68976 | 2.6925 | 0.49685 | 0.50315 | 0.50315 |  | 82.9%
150 | 0:25 | 93.2047 | 90 | 3 | 0.5 | 90 | 5 | 20 | 11.5386 | 2.8846 | 2.8846 | 92.8846 | 92.8846 | 3.2047 | 97.33% | 94.99% | 90.91% | 85.92% | 80.69% | 70.42% | 63.28% | 54.79% | 82.8% | 81.96% | 81.16% | 79.84% | 78.65% | 78.39% | 78.23% | 77.82% | 78% | 78.21% | 78.51% | 79.02% | 79.68% | 80.34% | 80.94% | 82.12% | 50.24% | 56.19% | 64.02% | 69.67% | 75.53% | 85.86% | 97.33% | 0 | No Time Shift | 0 | 100% | 0.064005 | 0.936 | 2.8846 | 0.1025 | 0.8975 | 0.8975 |  | 95.69%
151 | 0:25 | 92.8137 | 90 | 3 | 0.5 | 90 | 5 | 20 | 12.2822 | 3.0706 | 3.0706 | 93.0706 | 93.0706 | 2.8137 | 95.12% | 91.13% | 86.23% | 81.09% | 70.93% | 63.86% | 55.42% | 82.74% | 81.91% | 81.1% | 79.78% | 78.6% | 78.33% | 78.18% | 77.77% | 77.94% | 78.15% | 78.45% | 78.96% | 79.62% | 80.29% | 80.88% | 82.06% | 49.63% | 55.61% | 63.51% | 69.21% | 75.13% | 85.6% | 93.41% | 95.12% | 0 | No Time Shift | 0 | 100% | 0.051364 | 0.94864 | 3.0706 | 0.082261 | 0.91774 | 0.91774 |  | 95.63%
152 | 0:25 | 92.3944 | 90 | 3 | 0.5 | 90 | 5 | 20 | 12.9996 | 3.2499 | 3.2499 | 93.2499 | 93.2499 | 2.3944 | 91.35% | 86.54% | 81.48% | 71.43% | 64.44% | 56.05% | 82.73% | 81.9% | 81.09% | 79.77% | 78.59% | 78.32% | 78.17% | 77.76% | 77.93% | 78.14% | 78.44% | 78.95% | 79.61% | 80.28% | 80.87% | 82.05% | 49.03% | 55.02% | 62.99% | 68.74% | 74.73% | 85.34% | 93.28% | 94.92% | 94.92% | 29 | +290s | 280 | 6.667% | 0.17111 | 0.82889 | 3.2499 | 0.27403 | 0.72597 | 0.72597 |  | 58.06%
153 | 0:25 | 92.3191 | 90 | 3 | 0.5 | 90 | 5 | 20 | 13.689 | 3.4223 | 3.4223 | 93.4223 | 93.4223 | 2.3191 | 86.84% | 81.86% | 71.93% | 65.02% | 56.67% | 82.77% | 81.93% | 81.13% | 79.81% | 78.62% | 78.36% | 78.2% | 77.79% | 77.97% | 78.18% | 78.48% | 78.99% | 79.65% | 80.31% | 80.9% | 82.09% | 48.42% | 54.44% | 62.46% | 68.27% | 74.33% | 85.06% | 93.14% | 94.9% | 94.44% | 94.9% | 28 | +280s | 270 | 10% | 0.22063 | 0.77937 | 3.4223 | 0.35334 | 0.64666 | 0.64666 |  | 56.52%
154 | 0:25 | 92.3992 | 90 | 3 | 0.5 | 90 | 5 | 20 | 14.3492 | 3.5873 | 3.5873 | 93.5873 | 93.5873 | 2.3992 | 82.24% | 72.42% | 65.59% | 57.3% | 82.85% | 82.02% | 81.21% | 79.89% | 78.71% | 78.44% | 78.29% | 77.88% | 78.05% | 78.26% | 78.56% | 79.07% | 79.73% | 80.4% | 80.99% | 82.17% | 47.8% | 53.84% | 61.93% | 67.79% | 73.91% | 84.79% | 92.99% | 94.87% | 94.53% | 93.03% | 94.87% | 27 | +270s | 260 | 13.33% | 0.23761 | 0.76239 | 3.5873 | 0.38054 | 0.61946 | 0.61946 |  | 56.72%
155 | 0:26 | 91.5842 | 90 | 3 | 0.5 | 90 | 5 | 20 | 14.9786 | 3.7446 | 3.7446 | 93.7446 | 93.7446 | 1.5842 | 72.91% | 66.17% | 57.92% | 82.98% | 82.15% | 81.34% | 80.02% | 78.84% | 78.57% | 78.42% | 78.01% | 78.18% | 78.39% | 78.7% | 79.2% | 79.86% | 80.53% | 81.12% | 82.3% | 47.17% | 53.24% | 61.39% | 67.3% | 73.49% | 84.5% | 92.83% | 94.84% | 94.6% | 93.2% | 91.62% | 94.84% | 26 | +260s | 250 | 16.67% | 0.43209 | 0.56791 | 3.7446 | 0.692 | 0.308 | 0.308 |  | 47.43%
156 | 0:26 | 92.2254 | 90 | 3 | 0.5 | 90 | 5 | 20 | 15.5759 | 3.894 | 3.894 | 93.894 | 93.894 | 2.2254 | 66.74% | 58.55% | 83.16% | 82.33% | 81.52% | 80.2% | 79.02% | 78.75% | 78.59% | 78.19% | 78.36% | 78.57% | 78.87% | 79.38% | 80.04% | 80.71% | 81.3% | 82.48% | 46.53% | 52.62% | 60.83% | 66.8% | 73.06% | 84.2% | 92.66% | 94.79% | 94.68% | 93.37% | 91.87% | 90.41% | 94.79% | 25 | +250s | 240 | 20% | 0.33371 | 0.66629 | 3.894 | 0.53444 | 0.46556 | 0.46556 |  | 53.78%
157 | 0:26 | 92.322 | 90 | 3 | 0.5 | 90 | 5 | 20 | 16.1398 | 4.0349 | 4.0349 | 94.0349 | 94.0349 | 2.322 | 59.18% | 83.38% | 82.55% | 81.74% | 80.42% | 79.24% | 78.98% | 78.82% | 78.41% | 78.58% | 78.79% | 79.1% | 79.6% | 80.27% | 80.93% | 81.52% | 82.71% | 45.87% | 51.99% | 60.26% | 66.28% | 72.61% | 83.89% | 92.48% | 94.74% | 94.74% | 93.53% | 92.1% | 90.71% | 88.2% | 94.74% | 25 | +250s | 240 | 20% | 0.34258 | 0.65742 | 4.0349 | 0.54865 | 0.45135 | 0.45135 |  | 53.29%
158 | 0:26 | 92.2101 | 90 | 3 | 0.5 | 90 | 5 | 20 | 16.6691 | 4.1673 | 4.1673 | 94.1673 | 94.1673 | 2.2101 | 83.65% | 82.82% | 82.01% | 80.69% | 79.51% | 79.24% | 79.09% | 78.68% | 78.85% | 79.06% | 79.37% | 79.87% | 80.53% | 81.2% | 81.79% | 82.97% | 45.2% | 51.34% | 59.67% | 65.75% | 72.14% | 83.56% | 92.29% | 94.67% | 94.8% | 93.68% | 92.34% | 91.02% | 88.55% | 85.14% | 94.8% | 24 | +240s | 230 | 23.33% | 0.39143 | 0.60857 | 4.1673 | 0.62688 | 0.37312 | 0.37312 |  | 51.82%
159 | 0:26 | 92.9013 | 90 | 3 | 0.5 | 90 | 5 | 20 | 17.1627 | 4.2907 | 4.2907 | 94.2907 | 94.2907 | 2.9013 | 83.13% | 82.33% | 81.01% | 79.82% | 79.56% | 79.4% | 78.99% | 79.17% | 79.38% | 79.68% | 80.18% | 80.85% | 81.51% | 82.1% | 83.29% | 44.5% | 50.66% | 59.06% | 65.2% | 71.66% | 83.22% | 92.09% | 94.6% | 94.85% | 93.83% | 92.57% | 91.33% | 88.91% | 85.56% | 80.35% | 94.85% | 23 | +230s | 220 | 26.67% | 0.27788 | 0.72212 | 4.2907 | 0.44504 | 0.55496 | 0.55496 |  | 59.01%
160 | 0:26 | 92.6449 | 90 | 3 | 0.5 | 90 | 5 | 20 | 17.6196 | 4.4049 | 4.4049 | 94.4049 | 94.4049 | 2.6449 | 82.69% | 81.36% | 80.18% | 79.92% | 79.76% | 79.35% | 79.52% | 79.74% | 80.04% | 80.54% | 81.21% | 81.87% | 82.46% | 83.65% | 43.78% | 49.96% | 58.43% | 64.62% | 71.15% | 82.86% | 91.87% | 94.52% | 94.9% | 93.98% | 92.8% | 91.63% | 89.26% | 85.98% | 80.86% | 72.66% | 94.9% | 22 | +220s | 210 | 30% | 0.352 | 0.648 | 4.4049 | 0.56374 | 0.43626 | 0.43626 |  | 56.17%
161 | 0:27 | 92.4544 | 90 | 3 | 0.5 | 90 | 5 | 20 | 18.0386 | 4.5097 | 4.5097 | 94.5097 | 94.5097 | 2.4544 | 81.77% | 80.58% | 80.32% | 80.16% | 79.75% | 79.93% | 80.14% | 80.44% | 80.95% | 81.61% | 82.27% | 82.87% | 84.05% | 43.03% | 49.23% | 57.77% | 64.01% | 70.62% | 82.48% | 91.64% | 94.42% | 94.93% | 94.12% | 93.04% | 91.94% | 89.62% | 86.42% | 81.38% | 73.28% | 61.72% | 94.93% | 21 | +210s | 200 | 33.33% | 0.41106 | 0.58894 | 4.5097 | 0.65832 | 0.34168 | 0.34168 |  | 54.15%
162 | 0:27 | 92.5338 | 90 | 3 | 0.5 | 90 | 5 | 20 | 18.4191 | 4.6048 | 4.6048 | 94.6048 | 94.6048 | 2.5338 | 81.03% | 80.77% | 80.61% | 80.2% | 80.37% | 80.58% | 80.89% | 81.39% | 82.06% | 82.72% | 83.31% | 84.5% | 42.23% | 48.47% | 57.07% | 63.37% | 70.06% | 82.07% | 91.38% | 94.31% | 94.96% | 94.26% | 93.27% | 92.25% | 89.98% | 86.85% | 81.91% | 73.92% | 62.49% | 83.68% | 94.96% | 20 | +200s | 190 | 36.67% | 0.4142 | 0.5858 | 4.6048 | 0.66334 | 0.33666 | 0.33666 |  | 55.1%
163 | 0:27 | 93.5483 | 90 | 3 | 0.5 | 90 | 5 | 20 | 18.76 | 4.69 | 4.69 | 94.69 | 94.69 | 3.5483 | 81.25% | 81.1% | 80.69% | 80.86% | 81.07% | 81.37% | 81.88% | 82.54% | 83.21% | 83.8% | 84.98% | 41.4% | 47.66% | 56.33% | 62.7% | 69.46% | 81.63% | 91.1% | 94.18% | 94.98% | 94.39% | 93.49% | 92.57% | 90.35% | 87.3% | 82.46% | 74.57% | 63.3% | 84.16% | 82.24% | 94.98% | 19 | +190s | 180 | 40% | 0.22834 | 0.77166 | 4.69 | 0.36569 | 0.63431 | 0.63431 |  | 66.14%
164 | 0:27 | 93.646 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.0607 | 4.7652 | 4.7652 | 94.7652 | 94.7652 | 3.646 | 81.62% | 81.21% | 81.39% | 81.6% | 81.9% | 82.41% | 83.07% | 83.73% | 84.33% | 85.51% | 40.52% | 46.8% | 55.55% | 61.98% | 68.82% | 81.16% | 90.8% | 94.03% | 94.98% | 94.52% | 93.72% | 92.89% | 90.73% | 87.77% | 83.03% | 75.26% | 64.13% | 84.69% | 82.77% | 80.65% | 94.98% | 18 | +180s | 170 | 43.33% | 0.22385 | 0.77615 | 4.7652 | 0.35849 | 0.64151 | 0.64151 |  | 67.49%
165 | 0:27 | 93.4061 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.3206 | 4.8302 | 4.8302 | 94.8302 | 94.8302 | 3.4061 | 81.78% | 81.95% | 82.17% | 82.47% | 82.97% | 83.64% | 84.3% | 84.89% | 86.08% | 39.58% | 45.89% | 54.71% | 61.21% | 68.14% | 80.65% | 90.46% | 93.86% | 94.98% | 94.64% | 93.95% | 93.21% | 91.11% | 88.24% | 83.62% | 75.97% | 65.01% | 85.26% | 83.34% | 81.22% | 79.82% | 94.98% | 17 | +170s | 160 | 46.67% | 0.28482 | 0.71518 | 4.8302 | 0.45614 | 0.54386 | 0.54386 |  | 65.34%
166 | 0:27 | 94.0432 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.5391 | 4.8848 | 4.8848 | 94.8848 | 94.8848 | 4.0432 | 82.56% | 82.77% | 83.07% | 83.58% | 84.24% | 84.91% | 85.5% | 86.68% | 38.58% | 44.91% | 53.81% | 60.38% | 67.4% | 80.1% | 90.08% | 93.66% | 94.95% | 94.75% | 94.18% | 93.54% | 91.5% | 88.73% | 84.23% | 76.72% | 65.93% | 85.87% | 83.94% | 81.82% | 80.43% | 79.08% | 94.95% | 16 | +160s | 150 | 50% | 0.16832 | 0.83168 | 4.8848 | 0.26957 | 0.73043 | 0.73043 |  | 72.66%
167 | 0:28 | 94.263 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.7158 | 4.9289 | 4.9289 | 94.9289 | 94.9289 | 4.263 | 83.42% | 83.72% | 84.22% | 84.89% | 85.55% | 86.14% | 87.33% | 37.49% | 43.85% | 52.84% | 59.48% | 66.59% | 79.48% | 89.67% | 93.43% | 94.91% | 94.85% | 94.4% | 93.88% | 91.91% | 89.24% | 84.86% | 77.5% | 66.9% | 86.51% | 84.59% | 82.47% | 81.07% | 79.72% | 0% | 94.91% | 15 | +150s | 140 | 53.33% | 0.13318 | 0.86682 | 4.9289 | 0.2133 | 0.7867 | 0.7867 |  | 75.64%
168 | 0:28 | 94.3039 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.8501 | 4.9625 | 4.9625 | 94.9625 | 94.9625 | 4.3039 | 84.4% | 84.9% | 85.57% | 86.23% | 86.82% | 88.01% | 36.32% | 42.71% | 51.78% | 58.5% | 65.71% | 78.81% | 89.2% | 93.16% | 94.84% | 94.94% | 94.62% | 94.21% | 92.32% | 89.77% | 85.53% | 78.33% | 67.94% | 87.19% | 85.27% | 83.15% | 81.75% | 80.4% | 0% | 0% | 94.94% | 15 | +150s | 140 | 53.33% | 0.13173 | 0.86827 | 4.9625 | 0.21096 | 0.78904 | 0.78904 |  | 75.73%
169 | 0:28 | 94.3443 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.942 | 4.9855 | 4.9855 | 94.9855 | 94.9855 | 4.3443 | 85.62% | 86.28% | 86.94% | 87.53% | 88.72% | 35.03% | 41.45% | 50.62% | 57.42% | 64.74% | 78.05% | 88.66% | 92.85% | 94.73% | 95.01% | 94.84% | 94.56% | 92.75% | 90.32% | 86.23% | 79.2% | 69.04% | 87.9% | 85.98% | 83.86% | 82.47% | 81.11% | 0% | 0% | 0% | 95.01% | 14 | +140s | 130 | 56.67% | 0.12824 | 0.87176 | 4.9855 | 0.20537 | 0.79463 | 0.79463 |  | 77.05%
170 | 0:28 | 94.3553 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.9911 | 4.9978 | 4.9978 | 94.9978 | 94.9978 | 4.3553 | 87.03% | 87.69% | 88.28% | 89.47% | 33.62% | 40.06% | 49.33% | 56.22% | 63.65% | 77.21% | 88.05% | 92.47% | 94.59% | 95.06% | 95.04% | 94.9% | 93.18% | 90.89% | 86.97% | 80.13% | 70.23% | 88.65% | 86.73% | 84.61% | 83.21% | 81.86% | 0% | 0% | 0% | 0% | 95.06% | 13 | +130s | 120 | 60% | 0.1285 | 0.8715 | 4.9978 | 0.20579 | 0.79421 | 0.79421 |  | 78.16%
171 | 0:28 | 94.8601 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.9973 | 4.9993 | 4.9993 | 94.9993 | 94.9993 | 4.8601 | 88.47% | 89.06% | 90.24% | 32.05% | 38.52% | 47.89% | 54.88% | 62.43% | 76.24% | 87.34% | 92.02% | 94.4% | 95.07% | 95.23% | 95.25% | 93.62% | 91.48% | 87.75% | 81.13% | 71.5% | 89.42% | 87.5% | 85.38% | 83.99% | 82.64% | 0% | 0% | 0% | 0% | 0% | 95.25% | 14 | +140s | 130 | 56.67% | 0.027853 | 0.97215 | 4.9993 | 0.044608 | 0.95539 | 0.95539 |  | 82.48%
172 | 0:28 | 94.3852 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.9607 | 4.9902 | 4.9902 | 94.9902 | 94.9902 | 4.3852 | 89.87% | 91.05% | 30.29% | 36.79% | 46.27% | 53.36% | 61.05% | 75.14% | 86.52% | 91.48% | 94.15% | 95.05% | 95.4% | 95.58% | 94.07% | 92.1% | 88.58% | 82.2% | 72.89% | 90.23% | 88.31% | 86.19% | 84.8% | 83.44% | 0% | 0% | 0% | 0% | 0% | 0% | 95.58% | 13 | +130s | 120 | 60% | 0.121 | 0.879 | 4.9902 | 0.19378 | 0.80622 | 0.80622 |  | 78.74%
173 | 0:29 | 95.0435 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.8813 | 4.9703 | 4.9703 | 94.9703 | 94.9703 | 5.0435 | 91.89% | 28.29% | 34.82% | 44.43% | 51.63% | 59.46% | 73.85% | 85.54% | 90.83% | 93.81% | 94.96% | 95.53% | 95.91% | 94.52% | 92.74% | 89.45% | 83.35% | 74.4% | 91.07% | 89.15% | 87.03% | 85.63% | 84.28% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 95.91% | 12 | +120s | 110 | 63.33% | 0.014634 | 0.98537 | 4.9703 | 0.023437 | 0.97656 | 0.97656 |  | 85.63%
174 | 0:29 | 95.1698 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.7594 | 4.9398 | 4.9398 | 94.9398 | 94.9398 | 5.1698 | 26.01% | 32.57% | 42.31% | 49.62% | 57.61% | 72.34% | 84.37% | 90.01% | 93.35% | 94.79% | 95.61% | 96.2% | 94.96% | 93.4% | 90.38% | 84.59% | 76.06% | 91.93% | 90.01% | 87.89% | 86.49% | 85.14% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 96.2% | 11 | +110s | 100 | 66.67% | 0.045997 | 0.954 | 4.9398 | 0.073666 | 0.92633 | 0.92633 |  | 85.17%
175 | 0:29 | 95.0092 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.5951 | 4.8988 | 4.8988 | 94.8988 | 94.8988 | 5.0092 | 29.96% | 39.84% | 47.28% | 55.45% | 70.54% | 82.95% | 88.99% | 92.74% | 94.51% | 95.6% | 96.45% | 95.38% | 94.06% | 91.36% | 85.93% | 77.89% | 92.81% | 90.89% | 88.77% | 87.38% | 86.03% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 96.45% | 10 | +100s | 90 | 70% | 0.022089 | 0.97791 | 4.8988 | 0.035376 | 0.96462 | 0.96462 |  | 87.64%
176 | 0:29 | 95.1487 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.3887 | 4.8472 | 4.8472 | 94.8472 | 94.8472 | 5.1487 | 36.92% | 44.5% | 52.86% | 68.36% | 81.19% | 87.69% | 91.91% | 94.06% | 95.48% | 96.61% | 95.73% | 94.71% | 92.37% | 87.38% | 79.91% | 93.72% | 91.8% | 89.68% | 88.28% | 86.93% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 96.61% | 9 | +90s | 80 | 73.33% | 0.0603 | 0.9397 | 4.8472 | 0.096571 | 0.90343 | 0.90343 |  | 86.76%
177 | 0:29 | 95.2844 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.1409 | 4.7852 | 4.7852 | 94.7852 | 94.7852 | 5.2844 | 41.16% | 49.72% | 65.68% | 78.98% | 86.01% | 90.77% | 93.36% | 95.15% | 96.62% | 95.97% | 95.29% | 93.39% | 88.92% | 82.14% | 94.65% | 92.73% | 90.61% | 89.21% | 87.86% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 96.62% | 8 | +80s | 70 | 76.67% | 0.099841 | 0.90016 | 4.7852 | 0.1599 | 0.8401 | 0.8401 |  | 85.77%
178 | 0:29 | 95.4893 | 90 | 3 | 0.5 | 90 | 5 | 20 | 18.852 | 4.713 | 4.713 | 94.713 | 94.713 | 5.4893 | 45.86% | 62.31% | 76.14% | 83.78% | 89.17% | 92.29% | 94.53% | 96.39% | 96.02% | 95.76% | 94.38% | 90.54% | 84.59% | 95.59% | 93.67% | 91.55% | 90.16% | 88.81% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 96.39% | 7 | +70s | 60 | 80% | 0.15526 | 0.84474 | 4.713 | 0.24865 | 0.75135 | 0.75135 |  | 83.84%
179 | 0:30 | 95.4217 | 90 | 3 | 0.5 | 90 | 5 | 20 | 18.5227 | 4.6307 | 4.6307 | 94.6307 | 94.6307 | 5.4217 | 57.99% | 72.42% | 80.78% | 86.92% | 90.65% | 93.42% | 95.76% | 95.73% | 95.96% | 95.22% | 92.16% | 87.25% | 96.56% | 94.64% | 92.52% | 91.12% | 89.77% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 96.56% | 12 | +120s | 110 | 63.33% | 0.15821 | 0.84179 | 4.6307 | 0.25337 | 0.74663 | 0.74663 |  | 78.18%
180 | 0:30 | 95.5632 | 90 | 3 | 0.5 | 90 | 5 | 20 | 18.1538 | 4.5384 | 4.5384 | 94.5384 | 94.5384 | 5.5632 | 67.44% | 76.63% | 83.65% | 88.13% | 91.54% | 94.45% | 94.84% | 95.69% | 95.74% | 93.65% | 90.04% | 97.53% | 95.61% | 93.49% | 92.1% | 90.75% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 97.53% | 11 | +110s | 100 | 66.67% | 0.20495 | 0.79505 | 4.5384 | 0.32823 | 0.67177 | 0.67177 |  | 77.13%
181 | 0:30 | 94.8447 | 90 | 3 | 0.5 | 90 | 5 | 20 | 17.7459 | 4.4365 | 4.4365 | 94.4365 | 94.4365 | 4.8447 | 91.81% | 91.95% | 92.4% | 92.9% | 93.37% | 94.57% | 95.55% | 96.72% | 98.26% | 99.64% | 98.52% | 96.6% | 94.48% | 93.09% | 91.73% | 90.13% | 89% | 87.65% | 86.47% | 85.37% | 84.24% | 83.36% | 81.96% | 80.91% | 80.52% | 80.03% | 79.62% | 79.1% | 78.86% | 78.78% | 99.64% | 9 | +90s | 80 | 73.33% | 0.081656 | 0.91834 | 4.4365 | 0.13077 | 0.86923 | 0.86923 |  | 86.63%
182 | 0:30 | 94.5702 | 90 | 3 | 0.5 | 90 | 5 | 20 | 17.3 | 4.325 | 4.325 | 94.325 | 94.325 | 4.5702 | 90.95% | 91.4% | 91.9% | 92.37% | 93.57% | 94.55% | 95.73% | 97.26% | 98.64% | 99.52% | 97.6% | 95.48% | 94.08% | 92.73% | 91.13% | 90% | 88.65% | 87.47% | 86.36% | 85.24% | 84.36% | 82.96% | 81.91% | 81.52% | 81.03% | 80.62% | 80.1% | 79.86% | 79.78% | 79.76% | 99.52% | 9 | +90s | 80 | 73.33% | 0.049044 | 0.95096 | 4.325 | 0.078544 | 0.92146 | 0.92146 |  | 88.33%
183 | 0:30 | 94.6182 | 90 | 3 | 0.5 | 90 | 5 | 20 | 16.817 | 4.2043 | 4.2043 | 94.2043 | 94.2043 | 4.6182 | 90.39% | 90.9% | 91.36% | 92.56% | 93.54% | 94.72% | 96.25% | 97.63% | 99.47% | 98.61% | 96.49% | 95.09% | 93.74% | 92.14% | 91.01% | 89.66% | 88.48% | 87.37% | 86.25% | 85.37% | 83.96% | 82.91% | 82.52% | 82.04% | 81.62% | 81.11% | 80.86% | 80.78% | 80.77% | 80.26% | 99.47% | 8 | +80s | 70 | 76.67% | 0.082785 | 0.91722 | 4.2043 | 0.13258 | 0.86742 | 0.86742 |  | 87.63%
184 | 0:30 | 94.7534 | 90 | 3 | 0.5 | 90 | 5 | 20 | 16.298 | 4.0745 | 4.0745 | 94.0745 | 94.0745 | 4.7534 | 89.88% | 90.35% | 91.55% | 92.53% | 93.71% | 95.24% | 96.62% | 98.46% | 99.62% | 97.5% | 96.1% | 94.75% | 93.15% | 92.02% | 90.67% | 89.49% | 88.38% | 87.26% | 86.38% | 84.98% | 83.93% | 83.53% | 83.05% | 82.64% | 82.12% | 81.88% | 81.8% | 81.78% | 81.28% | 80.68% | 99.62% | 8 | +80s | 70 | 76.67% | 0.13577 | 0.86423 | 4.0745 | 0.21744 | 0.78256 | 0.78256 |  | 84.85%
185 | 0:31 | 94.8961 | 90 | 3 | 0.5 | 90 | 5 | 20 | 15.744 | 3.936 | 3.936 | 93.936 | 93.936 | 4.8961 | 89.33% | 90.53% | 91.51% | 92.69% | 94.22% | 95.6% | 97.44% | 99.36% | 98.51% | 97.12% | 95.77% | 94.17% | 93.04% | 91.68% | 90.51% | 89.4% | 88.27% | 87.4% | 85.99% | 84.94% | 84.55% | 84.07% | 83.65% | 83.13% | 82.89% | 82.81% | 82.8% | 82.29% | 81.7% | 81.75% | 99.36% | 7 | +70s | 60 | 80% | 0.19202 | 0.80798 | 3.936 | 0.30752 | 0.69248 | 0.69248 |  | 82.87%
186 | 0:31 | 94.7147 | 90 | 3 | 0.5 | 90 | 5 | 20 | 15.1564 | 3.7891 | 3.7891 | 93.7891 | 93.7891 | 4.7147 | 89.52% | 90.5% | 91.67% | 93.2% | 94.59% | 96.43% | 98.35% | 99.53% | 98.14% | 96.79% | 95.18% | 94.05% | 92.7% | 91.52% | 90.42% | 89.29% | 88.41% | 87.01% | 85.96% | 85.57% | 85.09% | 84.67% | 84.15% | 83.91% | 83.83% | 83.82% | 83.31% | 82.72% | 82.77% | 82.79% | 99.53% | 7 | +70s | 60 | 80% | 0.18511 | 0.81489 | 3.7891 | 0.29646 | 0.70354 | 0.70354 |  | 83.3%
187 | 0:31 | 94.6044 | 90 | 3 | 0.5 | 90 | 5 | 20 | 14.5362 | 3.6341 | 3.6341 | 93.6341 | 93.6341 | 4.6044 | 89.48% | 90.66% | 92.19% | 93.57% | 95.41% | 97.33% | 99.45% | 99.15% | 97.8% | 96.2% | 95.07% | 93.72% | 92.54% | 91.43% | 90.31% | 89.43% | 88.03% | 86.98% | 86.58% | 86.1% | 85.69% | 85.17% | 84.93% | 84.85% | 84.83% | 84.33% | 83.74% | 83.78% | 83.81% | 84.04% | 99.45% | 6 | +60s | 50 | 83.33% | 0.19406 | 0.80594 | 3.6341 | 0.3108 | 0.6892 | 0.6892 |  | 83.9%
188 | 0:31 | 94.3331 | 90 | 3 | 0.5 | 90 | 5 | 20 | 13.8849 | 3.4712 | 3.4712 | 93.4712 | 93.4712 | 4.3331 | 89.64% | 91.17% | 92.55% | 94.4% | 96.32% | 98.44% | 99.83% | 98.82% | 97.21% | 96.08% | 94.73% | 93.55% | 92.45% | 91.32% | 90.44% | 89.04% | 87.99% | 87.6% | 87.12% | 86.7% | 86.18% | 85.94% | 85.86% | 85.85% | 85.34% | 84.75% | 84.8% | 84.82% | 85.06% | 85.42% | 99.83% | 6 | +60s | 50 | 83.33% | 0.17238 | 0.82762 | 3.4712 | 0.27607 | 0.72393 | 0.72393 |  | 85.19%
189 | 0:31 | 94.0028 | 90 | 3 | 0.5 | 90 | 5 | 20 | 13.2038 | 3.301 | 3.301 | 93.301 | 93.301 | 4.0028 | 90.16% | 91.55% | 93.39% | 95.31% | 97.43% | 98.82% | 99.83% | 98.22% | 97.09% | 95.74% | 94.56% | 93.46% | 92.33% | 91.45% | 90.05% | 89% | 88.61% | 88.13% | 87.71% | 87.19% | 86.95% | 86.87% | 86.85% | 86.35% | 85.76% | 85.81% | 85.83% | 86.07% | 86.43% | 86.91% | 99.83% | 6 | +60s | 50 | 83.33% | 0.14037 | 0.85963 | 3.301 | 0.22481 | 0.77519 | 0.77519 |  | 86.89%
190 | 0:31 | 93.6315 | 90 | 3 | 0.5 | 90 | 5 | 20 | 12.4945 | 3.1236 | 3.1236 | 93.1236 | 93.1236 | 3.6315 | 90.54% | 92.39% | 94.31% | 96.43% | 97.82% | 99.17% | 99.22% | 98.09% | 96.74% | 95.56% | 94.46% | 93.33% | 92.45% | 91.05% | 90% | 89.61% | 89.13% | 88.71% | 88.19% | 87.95% | 87.87% | 87.86% | 87.35% | 86.76% | 86.81% | 86.83% | 87.07% | 87.43% | 87.92% | 88.29% | 99.22% | 6 | +60s | 50 | 83.33% | 0.10158 | 0.89842 | 3.1236 | 0.16268 | 0.83732 | 0.83732 |  | 88.76%
191 | 0:32 | 93.1923 | 90 | 3 | 0.5 | 90 | 5 | 20 | 11.7583 | 2.9396 | 2.9396 | 92.9396 | 92.9396 | 3.1923 | 91.39% | 93.31% | 95.44% | 96.83% | 98.18% | 91.73% | 93.8% | 95.43% | 95.36% | 94.16% | 92.33% | 90.97% | 89.37% | 88.62% | 86.06% | 83.41% | 81.48% | 81.05% | 81.07% | 80.8% | 81.93% | 81.9% | 81.32% | 78.83% | 78.03% | 78.1% | 77.77% | 77.54% | 77.62% | 77.35% | 98.18% | 4 | +40s | 30 | 90% | 0.050548 | 0.94945 | 2.9396 | 0.080953 | 0.91905 | 0.91905 |  | 93.36%
192 | 0:32 | 93.3028 | 90 | 3 | 0.5 | 90 | 5 | 20 | 10.997 | 2.7493 | 2.7493 | 92.7493 | 92.7493 | 3.3028 | 92.33% | 94.45% | 95.85% | 97.2% | 89.39% | 92.53% | 94.97% | 95.73% | 95.36% | 94.34% | 93.42% | 92.4% | 91.84% | 89.68% | 87.44% | 85.8% | 85.43% | 85.45% | 85.22% | 86.23% | 86.2% | 85.71% | 83.5% | 82.8% | 82.85% | 82.56% | 82.35% | 82.42% | 82.18% | 81.93% | 97.2% | 3 | +30s | 20 | 93.33% | 0.1107 | 0.8893 | 2.7493 | 0.17729 | 0.82271 | 0.82271 |  | 90.94%
193 | 0:32 | 92.9439 | 90 | 3 | 0.5 | 90 | 5 | 20 | 10.2121 | 2.553 | 2.553 | 92.553 | 92.553 | 2.9439 | 93.49% | 94.88% | 96.23% | 87.04% | 91.03% | 94.11% | 95.54% | 95.85% | 95.49% | 94.91% | 94.37% | 93.97% | 92.14% | 90.26% | 88.85% | 88.54% | 88.56% | 88.36% | 89.26% | 89.24% | 88.82% | 86.85% | 86.22% | 86.27% | 86.01% | 85.81% | 85.88% | 85.66% | 85.43% | 85.82% | 96.23% | 2 | +20s | 10 | 96.67% | 0.078174 | 0.92183 | 2.553 | 0.1252 | 0.8748 | 0.8748 |  | 93.46%
194 | 0:32 | 93.088 | 90 | 3 | 0.5 | 90 | 5 | 20 | 9.4053 | 2.3513 | 2.3513 | 92.3513 | 92.3513 | 3.088 | 93.93% | 95.28% | 84.81% | 89.49% | 93.08% | 95.06% | 95.92% | 96.1% | 95.82% | 95.68% | 95.41% | 93.85% | 92.26% | 91.06% | 90.8% | 90.82% | 90.64% | 91.44% | 91.43% | 91.07% | 89.31% | 88.75% | 88.79% | 88.55% | 88.37% | 88.43% | 88.23% | 88.02% | 88.35% | 87.72% | 96.1% | 7 | +70s | 60 | 80% | 0.14733 | 0.85267 | 2.3513 | 0.23594 | 0.76406 | 0.76406 |  | 84.17%
195 | 0:32 | 93.0262 | 90 | 3 | 0.5 | 90 | 5 | 20 | 8.5784 | 2.1446 | 2.1446 | 92.1446 | 92.1446 | 3.0262 | 94.35% | 82.75% | 88% | 92.01% | 94.44% | 95.76% | 96.39% | 96.36% | 96.54% | 96.38% | 95.06% | 93.72% | 92.68% | 92.46% | 92.49% | 92.33% | 93.05% | 93.04% | 92.74% | 91.15% | 90.64% | 90.68% | 90.46% | 90.3% | 90.35% | 90.17% | 89.98% | 90.26% | 89.68% | 89.34% | 96.54% | 8 | +80s | 70 | 76.67% | 0.17632 | 0.82368 | 2.1446 | 0.28238 | 0.71762 | 0.71762 |  | 81.66%
196 | 0:32 | 92.8244 | 90 | 3 | 0.5 | 90 | 5 | 20 | 7.7331 | 1.9333 | 1.9333 | 91.9333 | 91.9333 | 2.8244 | 80.87% | 86.58% | 90.95% | 93.76% | 95.46% | 96.48% | 96.65% | 97.11% | 97.04% | 95.93% | 94.79% | 93.91% | 93.72% | 93.74% | 93.6% | 94.26% | 94.25% | 93.99% | 92.56% | 92.1% | 92.13% | 91.93% | 91.78% | 91.83% | 91.66% | 91.48% | 91.72% | 91.19% | 90.88% | 91.41% | 97.11% | 7 | +70s | 60 | 80% | 0.17823 | 0.82177 | 1.9333 | 0.28545 | 0.71455 | 0.71455 |  | 82.85%
197 | 0:33 | 92.8876 | 90 | 3 | 0.5 | 90 | 5 | 20 | 6.8712 | 1.7178 | 1.7178 | 91.7178 | 91.7178 | 2.8876 | 85.27% | 89.92% | 93.05% | 95.09% | 96.43% | 96.78% | 97.48% | 97.49% | 96.55% | 95.6% | 94.85% | 94.69% | 94.71% | 94.59% | 95.19% | 95.18% | 94.96% | 93.65% | 93.23% | 93.27% | 93.08% | 92.94% | 92.98% | 92.83% | 92.66% | 92.86% | 92.38% | 92.1% | 92.57% | 92.23% | 97.49% | 7 | +70s | 60 | 80% | 0.23397 | 0.76603 | 1.7178 | 0.3747 | 0.6253 | 0.6253 |  | 80.01%
198 | 0:33 | 92.2109 | 90 | 3 | 0.5 | 90 | 5 | 20 | 5.9946 | 1.4986 | 1.4986 | 91.4986 | 91.4986 | 2.2109 | 88.95% | 92.36% | 94.67% | 96.3% | 96.81% | 97.71% | 97.79% | 97.01% | 96.22% | 95.57% | 95.44% | 95.46% | 95.35% | 95.9% | 95.89% | 95.71% | 94.52% | 94.14% | 94.17% | 93.99% | 93.86% | 93.9% | 93.76% | 93.61% | 93.77% | 93.32% | 93.07% | 93.48% | 93.17% | 92.94% | 97.79% | 6 | +60s | 50 | 83.33% | 0.14246 | 0.85754 | 1.4986 | 0.22815 | 0.77185 | 0.77185 |  | 86.1%
199 | 0:33 | 92.3153 | 90 | 3 | 0.5 | 90 | 5 | 20 | 5.1051 | 1.2763 | 1.2763 | 91.2763 | 91.2763 | 2.3153 | 91.68% | 94.25% | 96.12% | 96.76% | 97.84% | 97.99% | 97.34% | 96.69% | 96.15% | 96.04% | 96.06% | 95.96% | 96.46% | 96.46% | 96.3% | 95.22% | 94.87% | 94.89% | 94.73% | 94.61% | 94.65% | 94.51% | 94.37% | 94.5% | 94.09% | 93.86% | 94.22% | 93.94% | 93.72% | 93.9% | 97.99% | 5 | +50s | 40 | 86.67% | 0.20781 | 0.79219 | 1.2763 | 0.33281 | 0.66719 | 0.66719 |  | 83.79%
200 | 0:33 | 92.2592 | 90 | 3 | 0.5 | 90 | 5 | 20 | 4.2047 | 1.0512 | 1.0512 | 91.0512 | 91.0512 | 2.2592 | 93.81% | 95.91% | 96.67% | 97.91% | 98.11% | 97.58% | 97.06% | 96.6% | 96.51% | 96.53% | 96.45% | 96.91% | 96.91% | 96.78% | 95.78% | 95.46% | 95.49% | 95.33% | 95.22% | 95.26% | 95.13% | 95% | 95.1% | 94.72% | 94.51% | 94.83% | 94.56% | 94.35% | 94.53% | 94.69% | 98.11% | 4 | +40s | 30 | 90% | 0.2416 | 0.7584 | 1.0512 | 0.38693 | 0.61307 | 0.61307 |  | 83.14%
201 | 0:33 | 92.0773 | 90 | 3 | 0.5 | 90 | 5 | 20 | 3.2953 | 0.82382 | 0.82382 | 90.8238 | 90.8238 | 2.0773 | 95.67% | 96.54% | 97.93% | 98.17% | 97.76% | 97.35% | 96.97% | 96.9% | 96.92% | 96.84% | 97.27% | 97.26% | 97.16% | 96.25% | 95.95% | 95.97% | 95.83% | 95.72% | 95.76% | 95.64% | 95.52% | 95.6% | 95.24% | 95.06% | 95.33% | 95.08% | 94.89% | 95.04% | 95.19% | 95.28% | 98.17% | 3 | +30s | 20 | 93.33% | 0.25071 | 0.74929 | 0.82382 | 0.40151 | 0.59849 | 0.59849 |  | 83.79%
202 | 0:33 | 91.7954 | 90 | 3 | 0.5 | 90 | 5 | 20 | 2.3788 | 0.5947 | 0.5947 | 90.5947 | 90.5947 | 1.7954 | 96.39% | 97.91% | 98.2% | 97.88% | 97.57% | 97.26% | 97.21% | 97.23% | 97.16% | 97.55% | 97.55% | 97.47% | 96.63% | 96.36% | 96.38% | 96.25% | 96.15% | 96.18% | 96.07% | 95.95% | 96.01% | 95.68% | 95.51% | 95.75% | 95.52% | 95.33% | 95.48% | 95.6% | 95.69% | 96.2% | 98.2% | 2 | +20s | 10 | 96.67% | 0.24013 | 0.75987 | 0.5947 | 0.38458 | 0.61542 | 0.61542 |  | 85.47%
203 | 0:34 | 91.2285 | 90 | 3 | 0.5 | 90 | 5 | 20 | 1.4572 | 0.36431 | 0.36431 | 90.3643 | 90.3643 | 1.2285 | 97.86% | 98.19% | 97.96% | 97.75% | 97.5% | 97.47% | 97.49% | 97.43% | 97.79% | 97.79% | 97.73% | 96.96% | 96.71% | 96.73% | 96.6% | 96.51% | 96.54% | 96.43% | 96.32% | 96.36% | 96.05% | 95.9% | 96.11% | 95.88% | 95.71% | 95.85% | 95.95% | 96.03% | 96.49% | 96.67% | 98.19% | 1 | +10s | 0 | 100% | 0.17284 | 0.82716 | 0.36431 | 0.27681 | 0.72319 | 0.72319 |  | 90.17%
204 | 0:34 | 90.9026 | 90 | 3 | 0.5 | 90 | 5 | 20 | 0.53253 | 0.13313 | 0.13313 | 90.1331 | 90.1331 | 0.90263 | 98.16% | 98.01% | 97.89% | 97.7% | 97.68% | 97.7% | 97.65% | 97.98% | 97.98% | 97.94% | 97.23% | 97% | 97.02% | 96.9% | 96.81% | 96.84% | 96.74% | 96.64% | 96.66% | 96.37% | 96.23% | 96.41% | 96.2% | 96.03% | 96.16% | 96.25% | 96.32% | 96.74% | 96.91% | 97.28% | 98.16% | 0 | No Time Shift | 0 | 100% | 0.1539 | 0.8461 | 0.13313 | 0.24647 | 0.75353 | 0.75353 |  | 91.17%
205 | 0:34 | 91.577 | 90 | 3 | 0.5 | 90 | 5 | 20 | -0.3933 | -0.098326 | -0.098326 | 89.9017 | 89.9017 | 1.577 | 98.03% | 97.99% | 97.86% | 97.85% | 97.87% | 97.83% | 98.13% | 98.14% | 98.11% | 97.46% | 97.25% | 97.27% | 97.16% | 97.07% | 97.1% | 97% | 96.91% | 96.91% | 96.65% | 96.52% | 96.67% | 96.47% | 96.31% | 96.43% | 96.51% | 96.57% | 96.95% | 97.11% | 97.42% | 97.17% | 98.14% | 7 | +70s | 60 | 80% | 0.33506 | 0.66494 | 0.098326 | 0.5366 | 0.4634 | 0.4634 |  | 74.83%
206 | 0:34 | 91.3607 | 90 | 3 | 0.5 | 90 | 5 | 20 | -1.3183 | -0.32957 | -0.32957 | 89.6704 | 89.6704 | 1.3607 | 98.07% | 98% | 97.99% | 98.01% | 97.98% | 98.26% | 98.26% | 98.25% | 97.66% | 97.47% | 97.48% | 97.38% | 97.3% | 97.32% | 97.23% | 97.14% | 97.13% | 96.88% | 96.77% | 96.9% | 96.7% | 96.56% | 96.67% | 96.73% | 96.78% | 97.13% | 97.27% | 97.54% | 97.31% | 97.35% | 98.26% | 6 | +60s | 50 | 83.33% | 0.33806 | 0.66194 | 0.32957 | 0.54141 | 0.45859 | 0.45859 |  | 75.82%
207 | 0:34 | 91.0792 | 90 | 3 | 0.5 | 90 | 5 | 20 | -2.2405 | -0.56012 | -0.56012 | 89.4399 | 89.4399 | 1.0792 | 98.1% | 98.11% | 98.13% | 98.11% | 98.36% | 98.37% | 98.37% | 97.83% | 97.65% | 97.67% | 97.57% | 97.49% | 97.52% | 97.43% | 97.35% | 97.32% | 97.09% | 96.99% | 97.09% | 96.91% | 96.77% | 96.87% | 96.92% | 96.96% | 97.28% | 97.41% | 97.63% | 97.43% | 97.48% | 97.87% | 98.37% | 6 | +60s | 50 | 83.33% | 0.32786 | 0.67214 | 0.56012 | 0.52507 | 0.47493 | 0.47493 |  | 76.4%
208 | 0:34 | 90.4923 | 90 | 3 | 0.5 | 90 | 5 | 20 | -3.1578 | -0.78946 | -0.78946 | 89.2105 | 89.2105 | 0.49227 | 98.21% | 98.23% | 98.21% | 98.44% | 98.45% | 98.47% | 97.98% | 97.82% | 97.83% | 97.73% | 97.66% | 97.68% | 97.6% | 97.52% | 97.48% | 97.27% | 97.18% | 97.26% | 97.09% | 96.95% | 97.05% | 97.08% | 97.12% | 97.41% | 97.53% | 97.7% | 97.53% | 97.58% | 97.93% | 98.26% | 98.47% | 5 | +50s | 40 | 86.67% | 0.25635 | 0.74365 | 0.78946 | 0.41054 | 0.58946 | 0.58946 |  | 81.36%
209 | 0:35 | 90.413 | 90 | 3 | 0.5 | 90 | 5 | 20 | -4.0684 | -1.0171 | -1.0171 | 88.9829 | 88.9829 | 0.41297 | 98.31% | 98.29% | 98.51% | 98.51% | 98.55% | 98.1% | 97.96% | 97.97% | 97.88% | 97.81% | 97.83% | 97.75% | 97.68% | 97.63% | 97.43% | 97.35% | 97.4% | 97.24% | 97.12% | 97.21% | 97.23% | 97.26% | 97.52% | 97.63% | 97.76% | 97.61% | 97.67% | 97.98% | 98.28% | 98.24% | 98.55% | 4 | +40s | 30 | 90% | 0.28602 | 0.71398 | 1.0171 | 0.45806 | 0.54194 | 0.54194 |  | 80.91%
210 | 0:35 | 90.4105 | 90 | 3 | 0.5 | 90 | 5 | 20 | -4.9703 | -1.2426 | -1.2426 | 88.7574 | 88.7574 | 0.4105 | 98.36% | 98.56% | 98.56% | 98.61% | 98.21% | 98.08% | 98.09% | 98% | 97.94% | 97.96% | 97.89% | 97.82% | 97.75% | 97.57% | 97.5% | 97.53% | 97.38% | 97.26% | 97.34% | 97.35% | 97.38% | 97.61% | 97.72% | 97.8% | 97.68% | 97.74% | 98.01% | 98.28% | 98.26% | 98.32% | 98.61% | 3 | +30s | 20 | 93.33% | 0.33062 | 0.66938 | 1.2426 | 0.52949 | 0.47051 | 0.47051 |  | 79.66%
211 | 0:35 | 90.0383 | 90 | 3 | 0.5 | 90 | 5 | 20 | -5.8616 | -1.4654 | -1.4654 | 88.5346 | 88.5346 | 0.038334 | 98.59% | 98.6% | 98.66% | 98.3% | 98.18% | 98.19% | 98.11% | 98.05% | 98.07% | 98% | 97.94% | 97.86% | 97.69% | 97.63% | 97.65% | 97.5% | 97.39% | 97.46% | 97.46% | 97.49% | 97.69% | 97.79% | 97.83% | 97.73% | 97.8% | 98.03% | 98.28% | 98.26% | 98.32% | 98.22% | 98.66% | 2 | +20s | 10 | 96.67% | 0.30074 | 0.69926 | 1.4654 | 0.48165 | 0.51835 | 0.51835 |  | 82.39%
212 | 0:35 | 89.6219 | 90 | 3 | 0.5 | 90 | 5 | 20 | -6.7402 | -1.6851 | -1.6851 | 88.3149 | 88.3149 | -0.37811 | 98.63% | 98.7% | 98.38% | 98.28% | 98.28% | 98.21% | 98.15% | 98.17% | 98.11% | 98.04% | 97.95% | 97.8% | 97.75% | 97.74% | 97.61% | 97.5% | 97.57% | 97.56% | 97.58% | 97.75% | 97.85% | 97.85% | 97.77% | 97.84% | 98.04% | 98.27% | 98.25% | 98.31% | 98.23% | 98.31% | 98.7% | 1 | +10s | 0 | 100% | 0.26139 | 0.73861 | 1.6851 | 0.41862 | 0.58138 | 0.58138 |  | 85.61%
213 | 0:35 | 89.4266 | 90 | 3 | 0.5 | 90 | 5 | 20 | -7.6045 | -1.9011 | -1.9011 | 88.0989 | 88.0989 | -0.57338 | 98.72% | 98.45% | 98.36% | 98.36% | 98.29% | 98.24% | 98.26% | 98.2% | 98.14% | 98.04% | 97.89% | 97.85% | 97.83% | 97.7% | 97.6% | 97.66% | 97.64% | 97.66% | 97.8% | 97.89% | 97.85% | 97.8% | 97.87% | 98.04% | 98.24% | 98.23% | 98.29% | 98.23% | 98.3% | 98.34% | 98.72% | 0 | No Time Shift | 0 | 100% | 0.26555 | 0.73445 | 1.9011 | 0.42528 | 0.57472 | 0.57472 |  | 85.4%
214 | 0:35 | 90.0895 | 90 | 3 | 0.5 | 90 | 5 | 20 | -8.4524 | -2.1131 | -2.1131 | 87.8869 | 87.8869 | 0.089478 | 98.51% | 98.43% | 98.43% | 98.37% | 98.32% | 98.33% | 98.27% | 98.22% | 98.11% | 97.98% | 97.94% | 97.91% | 97.79% | 97.69% | 97.75% | 97.71% | 97.73% | 97.85% | 97.93% | 97.85% | 97.82% | 97.9% | 98.03% | 98.21% | 98.2% | 98.27% | 98.22% | 98.28% | 98.32% | 98.23% | 98.51% | 0 | No Time Shift | 0 | 100% | 0.44051 | 0.55949 | 2.1131 | 0.70549 | 0.29451 | 0.29451 |  | 75.99%
215 | 0:36 | 89.598 | 90 | 3 | 0.5 | 90 | 5 | 20 | -9.2822 | -2.3205 | -2.3205 | 87.6795 | 87.6795 | -0.40198 | 98.48% | 98.49% | 98.43% | 98.38% | 98.4% | 98.34% | 98.29% | 98.17% | 98.05% | 98.03% | 97.97% | 97.86% | 97.77% | 97.82% | 97.78% | 97.79% | 97.88% | 97.96% | 97.84% | 97.83% | 97.91% | 98.01% | 98.17% | 98.17% | 98.23% | 98.21% | 98.26% | 98.29% | 98.25% | 98.43% | 98.49% | 1 | +10s | 0 | 100% | 0.38371 | 0.61629 | 2.3205 | 0.61452 | 0.38548 | 0.38548 |  | 79.01%
216 | 0:36 | 89.4602 | 90 | 3 | 0.5 | 90 | 5 | 20 | -10.0921 | -2.523 | -2.523 | 87.477 | 87.477 | -0.53976 | 98.54% | 98.48% | 98.44% | 98.45% | 98.4% | 98.36% | 98.22% | 98.12% | 98.1% | 98.03% | 97.92% | 97.84% | 97.88% | 97.83% | 97.84% | 97.91% | 97.97% | 97.83% | 97.83% | 97.92% | 97.99% | 98.13% | 98.13% | 98.19% | 98.18% | 98.23% | 98.26% | 98.26% | 98.46% | 98.47% | 98.54% | 0 | No Time Shift | 0 | 100% | 0.39665 | 0.60335 | 2.523 | 0.63525 | 0.36475 | 0.36475 |  | 78.34%
217 | 0:36 | 89.4954 | 90 | 3 | 0.5 | 90 | 5 | 20 | -10.8804 | -2.7201 | -2.7201 | 87.2799 | 87.2799 | -0.50458 | 98.53% | 98.49% | 98.5% | 98.45% | 98.41% | 98.27% | 98.17% | 98.16% | 98.07% | 97.98% | 97.9% | 97.94% | 97.88% | 97.88% | 97.92% | 97.98% | 97.8% | 97.83% | 97.92% | 97.96% | 98.08% | 98.08% | 98.14% | 98.15% | 98.19% | 98.22% | 98.26% | 98.49% | 98.5% | 98.39% | 98.53% | 0 | No Time Shift | 0 | 100% | 0.44311 | 0.55689 | 2.7201 | 0.70964 | 0.29036 | 0.29036 |  | 75.85%
218 | 0:36 | 89.4742 | 90 | 3 | 0.5 | 90 | 5 | 20 | -11.6454 | -2.9114 | -2.9114 | 87.0886 | 87.0886 | -0.52583 | 98.53% | 98.54% | 98.49% | 98.46% | 98.3% | 98.22% | 98.22% | 98.11% | 98.02% | 97.95% | 97.98% | 97.91% | 97.91% | 97.93% | 97.99% | 97.77% | 97.82% | 97.91% | 97.92% | 98.02% | 98.03% | 98.08% | 98.11% | 98.14% | 98.17% | 98.25% | 98.51% | 98.52% | 98.43% | 98.26% | 98.54% | 1 | +10s | 0 | 100% | 0.4771 | 0.5229 | 2.9114 | 0.76409 | 0.23591 | 0.23591 |  | 74.04%
219 | 0:36 | 89.2363 | 90 | 3 | 0.5 | 90 | 5 | 20 | -12.3854 | -3.0964 | -3.0964 | 86.9036 | 86.9036 | -0.76375 | 98.57% | 98.53% | 98.49% | 98.33% | 98.26% | 98.27% | 98.15% | 98.06% | 97.99% | 98.02% | 97.94% | 97.93% | 97.93% | 97.98% | 97.73% | 97.8% | 97.9% | 97.87% | 97.95% | 97.96% | 98.02% | 98.07% | 98.09% | 98.11% | 98.24% | 98.52% | 98.53% | 98.46% | 98.31% | 97.67% | 98.57% | 0 | No Time Shift | 0 | 100% | 0.46652 | 0.53348 | 3.0964 | 0.74714 | 0.25286 | 0.25286 |  | 74.62%
220 | 0:36 | 89.1161 | 90 | 3 | 0.5 | 90 | 5 | 20 | -13.0989 | -3.2747 | -3.2747 | 86.7253 | 86.7253 | -0.88391 | 98.56% | 98.52% | 98.35% | 98.3% | 98.31% | 98.17% | 98.09% | 98.03% | 98.05% | 97.96% | 97.95% | 97.93% | 97.97% | 97.69% | 97.77% | 97.87% | 97.82% | 97.87% | 97.89% | 97.95% | 98.01% | 98.03% | 98.05% | 98.21% | 98.53% | 98.53% | 98.48% | 98.36% | 97.75% | 97.15% | 98.56% | 0 | No Time Shift | 0 | 100% | 0.47816 | 0.52184 | 3.2747 | 0.76579 | 0.23421 | 0.23421 |  | 73.99%
221 | 0:37 | 88.8136 | 90 | 3 | 0.5 | 90 | 5 | 20 | -13.7843 | -3.4461 | -3.4461 | 86.5539 | 86.5539 | -1.1864 | 98.55% | 98.36% | 98.32% | 98.34% | 98.19% | 98.12% | 98.06% | 98.08% | 97.98% | 97.96% | 97.92% | 97.95% | 97.63% | 97.74% | 97.84% | 97.76% | 97.79% | 97.82% | 97.87% | 97.95% | 97.96% | 97.98% | 98.19% | 98.52% | 98.52% | 98.5% | 98.4% | 97.82% | 97.25% | 96.87% | 98.55% | 0 | No Time Shift | 0 | 100% | 0.45194 | 0.54806 | 3.4461 | 0.72379 | 0.27621 | 0.27621 |  | 75.39%
222 | 0:37 | 88.0095 | 90 | 3 | 0.5 | 90 | 5 | 20 | -14.4402 | -3.6101 | -3.6101 | 86.3899 | 86.3899 | -1.9905 | 98.37% | 98.34% | 98.37% | 98.19% | 98.13% | 98.08% | 98.09% | 97.99% | 97.97% | 97.9% | 97.92% | 97.57% | 97.69% | 97.81% | 97.69% | 97.7% | 97.73% | 97.78% | 97.88% | 97.88% | 97.9% | 98.15% | 98.51% | 98.51% | 98.51% | 98.43% | 97.89% | 97.34% | 96.98% | 96.34% | 98.51% | 23 | +230s | 220 | 26.67% | 0.32392 | 0.67608 | 3.6101 | 0.51876 | 0.48124 | 0.48124 |  | 57.77%
223 | 0:37 | 88.5626 | 90 | 3 | 0.5 | 90 | 5 | 20 | -15.0651 | -3.7663 | -3.7663 | 86.2337 | 86.2337 | -1.4374 | 98.35% | 98.39% | 98.2% | 98.14% | 98.09% | 98.1% | 97.98% | 97.96% | 97.87% | 97.89% | 97.5% | 97.64% | 97.76% | 97.61% | 97.61% | 97.64% | 97.69% | 97.81% | 97.8% | 97.81% | 98.1% | 98.49% | 98.49% | 98.51% | 98.45% | 97.95% | 97.43% | 97.08% | 96.46% | 93.25% | 98.51% | 23 | +230s | 220 | 26.67% | 0.46578 | 0.53422 | 3.7663 | 0.74596 | 0.25404 | 0.25404 |  | 50.19%
224 | 0:37 | 88.1106 | 90 | 3 | 0.5 | 90 | 5 | 20 | -15.6578 | -3.9144 | -3.9144 | 86.0856 | 86.0856 | -1.8894 | 98.4% | 98.19% | 98.14% | 98.1% | 98.1% | 97.98% | 97.95% | 97.83% | 97.85% | 97.42% | 97.59% | 97.71% | 97.52% | 97.5% | 97.53% | 97.58% | 97.72% | 97.7% | 97.71% | 98.05% | 98.46% | 98.46% | 98.5% | 98.47% | 98.01% | 97.51% | 97.18% | 96.58% | 93.45% | 90.77% | 98.5% | 22 | +220s | 210 | 30% | 0.40501 | 0.59499 | 3.9144 | 0.64863 | 0.35137 | 0.35137 |  | 54.55%
225 | 0:37 | 87.5962 | 90 | 3 | 0.5 | 90 | 5 | 20 | -16.2169 | -4.0542 | -4.0542 | 85.9458 | 85.9458 | -2.4038 | 98.18% | 98.14% | 98.1% | 98.1% | 97.96% | 97.93% | 97.79% | 97.79% | 97.33% | 97.52% | 97.64% | 97.43% | 97.38% | 97.42% | 97.47% | 97.62% | 97.6% | 97.61% | 97.99% | 98.43% | 98.43% | 98.48% | 98.48% | 98.05% | 97.58% | 97.27% | 96.7% | 93.64% | 91.05% | 88.83% | 98.48% | 21 | +210s | 200 | 33.33% | 0.33009 | 0.66991 | 4.0542 | 0.52865 | 0.47135 | 0.47135 |  | 59.65%
226 | 0:37 | 88.0992 | 90 | 3 | 0.5 | 90 | 5 | 20 | -16.7412 | -4.1853 | -4.1853 | 85.8147 | 85.8147 | -1.9008 | 98.12% | 98.09% | 98.08% | 97.93% | 97.9% | 97.73% | 97.73% | 97.24% | 97.44% | 97.57% | 97.32% | 97.25% | 97.3% | 97.34% | 97.52% | 97.49% | 97.49% | 97.91% | 98.38% | 98.38% | 98.46% | 98.48% | 98.09% | 97.65% | 97.35% | 96.81% | 93.83% | 91.33% | 89.15% | 84.25% | 98.48% | 21 | +210s | 200 | 33.33% | 0.4569 | 0.5431 | 4.1853 | 0.73173 | 0.26827 | 0.26827 |  | 52.88%
227 | 0:38 | 87.9207 | 90 | 3 | 0.5 | 90 | 5 | 20 | -17.2297 | -4.3074 | -4.3074 | 85.6926 | 85.6926 | -2.0793 | 98.07% | 98.06% | 97.9% | 97.86% | 97.66% | 97.66% | 97.13% | 97.35% | 97.48% | 97.2% | 97.11% | 97.16% | 97.21% | 97.4% | 97.36% | 97.36% | 97.83% | 98.33% | 98.32% | 98.43% | 98.47% | 98.12% | 97.71% | 97.43% | 96.91% | 94.02% | 91.61% | 89.48% | 84.67% | 78.96% | 98.47% | 20 | +200s | 190 | 36.67% | 0.44561 | 0.55439 | 4.3074 | 0.71366 | 0.28634 | 0.28634 |  | 54.59%
228 | 0:38 | 87.8144 | 90 | 3 | 0.5 | 90 | 5 | 20 | -17.6812 | -4.4203 | -4.4203 | 85.5797 | 85.5797 | -2.1856 | 98.02% | 97.85% | 97.81% | 97.59% | 97.58% | 97% | 97.25% | 97.39% | 97.07% | 96.96% | 97.01% | 97.06% | 97.27% | 97.22% | 97.22% | 97.73% | 98.26% | 98.26% | 98.38% | 98.46% | 98.14% | 97.76% | 97.5% | 97% | 94.2% | 91.89% | 89.8% | 85.09% | 79.49% | 73.25% | 98.46% | 19 | +190s | 180 | 40% | 0.44694 | 0.55306 | 4.4203 | 0.71578 | 0.28422 | 0.28422 |  | 55.63%
229 | 0:38 | 87.0999 | 90 | 3 | 0.5 | 90 | 5 | 20 | -18.0949 | -4.5237 | -4.5237 | 85.4763 | 85.4763 | -2.9001 | 97.8% | 97.75% | 97.5% | 97.48% | 96.86% | 97.14% | 97.28% | 96.93% | 96.78% | 96.85% | 96.89% | 97.12% | 97.06% | 97.06% | 97.62% | 98.18% | 98.18% | 98.33% | 98.43% | 98.16% | 97.81% | 97.56% | 97.09% | 94.38% | 92.18% | 90.13% | 85.52% | 80.03% | 73.86% | 61.13% | 98.43% | 18 | +180s | 170 | 43.33% | 0.32472 | 0.67528 | 4.5237 | 0.52004 | 0.47996 | 0.47996 |  | 63.25%
230 | 0:38 | 87.2856 | 90 | 3 | 0.5 | 90 | 5 | 20 | -18.4697 | -4.6174 | -4.6174 | 85.3826 | 85.3826 | -2.7144 | 97.67% | 97.39% | 97.37% | 96.71% | 97% | 97.15% | 96.76% | 96.6% | 96.66% | 96.7% | 96.96% | 96.89% | 96.88% | 97.5% | 98.09% | 98.08% | 98.26% | 98.39% | 98.16% | 97.84% | 97.62% | 97.18% | 94.55% | 92.46% | 90.47% | 85.96% | 80.59% | 74.5% | 61.89% | 84.39% | 98.39% | 17 | +170s | 160 | 46.67% | 0.38061 | 0.61939 | 4.6174 | 0.60955 | 0.39045 | 0.39045 |  | 61.37%
231 | 0:38 | 86.7999 | 90 | 3 | 0.5 | 90 | 5 | 20 | -18.805 | -4.7013 | -4.7013 | 85.2987 | 85.2987 | -3.2001 | 97.27% | 97.24% | 96.54% | 96.86% | 97.01% | 96.58% | 96.39% | 96.46% | 96.5% | 96.77% | 96.7% | 96.69% | 97.36% | 97.98% | 97.97% | 98.17% | 98.33% | 98.15% | 97.87% | 97.66% | 97.25% | 94.73% | 92.74% | 90.8% | 86.41% | 81.17% | 75.16% | 62.68% | 84.89% | 83.54% | 98.33% | 16 | +160s | 150 | 50% | 0.30023 | 0.69977 | 4.7013 | 0.48082 | 0.51918 | 0.51918 |  | 66.75%
232 | 0:38 | 87.0531 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.1 | -4.775 | -4.775 | 85.225 | 85.225 | -2.9469 | 97.09% | 96.34% | 96.69% | 96.84% | 96.37% | 96.15% | 96.23% | 96.27% | 96.57% | 96.48% | 96.47% | 97.19% | 97.85% | 97.84% | 98.07% | 98.26% | 98.13% | 97.88% | 97.7% | 97.32% | 94.9% | 93.03% | 91.15% | 86.87% | 81.76% | 75.84% | 63.5% | 85.42% | 84.07% | 82.27% | 98.26% | 15 | +150s | 140 | 53.33% | 0.36563 | 0.63437 | 4.775 | 0.58556 | 0.41444 | 0.41444 |  | 64.35%
233 | 0:39 | 86.0896 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.3541 | -4.8385 | -4.8385 | 85.1615 | 85.1615 | -3.9104 | 96.12% | 96.49% | 96.65% | 96.14% | 95.89% | 95.97% | 96.01% | 96.33% | 96.24% | 96.22% | 97% | 97.7% | 97.68% | 97.95% | 98.17% | 98.09% | 97.88% | 97.72% | 97.37% | 95.06% | 93.32% | 91.5% | 87.34% | 82.38% | 76.55% | 64.36% | 85.99% | 84.64% | 82.84% | 81.13% | 98.17% | 14 | +140s | 130 | 56.67% | 0.18562 | 0.81438 | 4.8385 | 0.29727 | 0.70273 | 0.70273 |  | 75.04%
234 | 0:39 | 86.7302 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.5667 | -4.8917 | -4.8917 | 85.1083 | 85.1083 | -3.2698 | 96.27% | 96.43% | 95.87% | 95.59% | 95.68% | 95.72% | 96.07% | 95.96% | 95.94% | 96.79% | 97.52% | 97.5% | 97.8% | 98.06% | 98.03% | 97.86% | 97.73% | 97.41% | 95.22% | 93.61% | 91.85% | 87.83% | 83.02% | 77.29% | 65.27% | 86.61% | 85.25% | 83.46% | 81.74% | 79.62% | 98.06% | 13 | +130s | 120 | 60% | 0.32438 | 0.67562 | 4.8917 | 0.5195 | 0.4805 | 0.4805 |  | 68.7%
235 | 0:39 | 85.9286 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.7374 | -4.9343 | -4.9343 | 85.0657 | 85.0657 | -4.0714 | 96.18% | 95.57% | 95.26% | 95.35% | 95.39% | 95.77% | 95.65% | 95.62% | 96.53% | 97.31% | 97.29% | 97.62% | 97.92% | 97.95% | 97.82% | 97.71% | 97.44% | 95.37% | 93.91% | 92.22% | 88.33% | 83.69% | 78.07% | 66.23% | 87.25% | 85.9% | 84.1% | 82.39% | 80.27% | 78.94% | 97.95% | 13 | +130s | 120 | 60% | 0.17259 | 0.82741 | 4.9343 | 0.2764 | 0.7236 | 0.7236 |  | 76.77%
236 | 0:39 | 85.6637 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.8657 | -4.9664 | -4.9664 | 85.0336 | 85.0336 | -4.3363 | 95.22% | 94.87% | 94.98% | 95.01% | 95.42% | 95.28% | 95.26% | 96.24% | 97.06% | 97.04% | 97.4% | 97.74% | 97.83% | 97.76% | 97.68% | 97.44% | 95.51% | 94.21% | 92.59% | 88.86% | 84.4% | 78.89% | 67.24% | 87.94% | 86.59% | 84.79% | 83.07% | 80.95% | 79.63% | 0% | 97.83% | 12 | +120s | 110 | 63.33% | 0.12602 | 0.87398 | 4.9664 | 0.20182 | 0.79818 | 0.79818 |  | 80.33%
237 | 0:39 | 85.681 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.9515 | -4.9879 | -4.9879 | 85.0121 | 85.0121 | -4.319 | 94.43% | 94.54% | 94.57% | 95.01% | 94.87% | 94.83% | 95.89% | 96.76% | 96.74% | 97.14% | 97.53% | 97.69% | 97.66% | 97.61% | 97.42% | 95.64% | 94.5% | 92.97% | 89.41% | 85.14% | 79.77% | 68.33% | 88.66% | 87.31% | 85.51% | 83.79% | 81.67% | 80.35% | 0% | 0% | 97.69% | 11 | +110s | 100 | 66.67% | 0.13378 | 0.86622 | 4.9879 | 0.21426 | 0.78574 | 0.78574 |  | 80.98%
238 | 0:39 | 86.0871 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.9945 | -4.9986 | -4.9986 | 85.0014 | 85.0014 | -3.9129 | 94.04% | 94.06% | 94.54% | 94.38% | 94.34% | 95.49% | 96.41% | 96.38% | 96.83% | 97.26% | 97.49% | 97.52% | 97.51% | 97.37% | 95.75% | 94.8% | 93.35% | 89.98% | 85.92% | 80.7% | 69.5% | 89.41% | 88.06% | 86.26% | 84.54% | 82.42% | 81.1% | 0% | 0% | 0% | 97.52% | 11 | +110s | 100 | 66.67% | 0.21715 | 0.78285 | 4.9986 | 0.34777 | 0.65223 | 0.65223 |  | 76.47%
239 | 0:40 | 85.2793 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.9947 | -4.9987 | -4.9987 | 85.0013 | 85.0013 | -4.7207 | 93.46% | 93.98% | 93.8% | 93.76% | 95% | 95.97% | 95.95% | 96.44% | 96.93% | 97.24% | 97.34% | 97.36% | 97.27% | 95.83% | 95.09% | 93.74% | 90.57% | 86.76% | 81.69% | 70.76% | 90.19% | 88.84% | 87.04% | 85.32% | 83.2% | 81.88% | 0% | 0% | 0% | 0% | 97.36% | 11 | +110s | 100 | 66.67% | 0.055602 | 0.9444 | 4.9987 | 0.089048 | 0.91095 | 0.91095 |  | 85.04%
240 | 0:40 | 85.6463 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.9521 | -4.988 | -4.988 | 85.012 | 85.012 | -4.3537 | 93.32% | 93.12% | 93.07% | 94.41% | 95.45% | 95.42% | 95.97% | 96.51% | 96.92% | 97.08% | 97.14% | 97.11% | 95.88% | 95.36% | 94.12% | 91.19% | 87.64% | 82.76% | 72.13% | 91% | 89.65% | 87.85% | 86.13% | 84.01% | 82.69% | 0% | 0% | 0% | 0% | 0% | 97.14% | 10 | +100s | 90 | 70% | 0.12686 | 0.87314 | 4.988 | 0.20317 | 0.79683 | 0.79683 |  | 82.27%
241 | 0:40 | 84.9739 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.8667 | -4.9667 | -4.9667 | 85.0333 | 85.0333 | -5.0261 | 92.29% | 92.24% | 93.69% | 94.8% | 94.77% | 95.38% | 95.99% | 96.49% | 96.73% | 96.84% | 96.88% | 95.87% | 95.61% | 94.5% | 91.82% | 88.58% | 83.9% | 73.62% | 91.84% | 90.49% | 88.69% | 86.97% | 84.85% | 83.53% | 0% | 0% | 0% | 0% | 0% | 0% | 96.88% | 10 | +100s | 90 | 70% | 0.011878 | 0.98812 | 4.9667 | 0.019023 | 0.98098 | 0.98098 |  | 88.33%
242 | 0:40 | 84.5979 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.7387 | -4.9347 | -4.9347 | 85.0653 | 85.0653 | -5.4021 | 91.22% | 92.81% | 94% | 93.96% | 94.63% | 95.32% | 95.94% | 96.27% | 96.43% | 96.54% | 95.79% | 95.83% | 94.85% | 92.48% | 89.58% | 85.14% | 75.26% | 92.7% | 91.35% | 89.55% | 87.84% | 85.71% | 84.39% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 96.54% | 9 | +90s | 80 | 73.33% | 0.093489 | 0.90651 | 4.9347 | 0.14972 | 0.85028 | 0.85028 |  | 84.97%
243 | 0:40 | 85.2626 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.5684 | -4.8921 | -4.8921 | 85.1079 | 85.1079 | -4.7374 | 91.7% | 92.98% | 92.93% | 93.68% | 94.45% | 95.2% | 95.63% | 95.85% | 96.05% | 95.6% | 95.97% | 95.16% | 93.13% | 90.64% | 86.48% | 77.06% | 93.59% | 92.24% | 90.44% | 88.73% | 86.6% | 85.28% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 96.05% | 8 | +80s | 70 | 76.67% | 0.030942 | 0.96906 | 4.8921 | 0.049554 | 0.95045 | 0.95045 |  | 89.25%
244 | 0:40 | 84.5909 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.3562 | -4.839 | -4.839 | 85.161 | 85.161 | -5.4091 | 91.66% | 91.62% | 92.45% | 93.32% | 94.22% | 94.77% | 95.05% | 95.35% | 95.26% | 96.01% | 95.39% | 93.77% | 91.75% | 87.91% | 79.05% | 94.5% | 93.15% | 91.35% | 89.64% | 87.51% | 86.19% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 96.01% | 9 | +90s | 80 | 73.33% | 0.114 | 0.886 | 4.839 | 0.18258 | 0.81742 | 0.81742 |  | 83.7%
245 | 0:41 | 84.5005 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.1025 | -4.7756 | -4.7756 | 85.2244 | 85.2244 | -5.4995 | 89.89% | 90.83% | 91.8% | 92.89% | 93.57% | 93.94% | 94.36% | 94.67% | 95.88% | 95.49% | 94.34% | 92.88% | 89.44% | 81.25% | 95.43% | 94.08% | 92.28% | 90.57% | 88.44% | 87.12% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 95.88% | 8 | +80s | 70 | 76.67% | 0.14478 | 0.85522 | 4.7756 | 0.23186 | 0.76814 | 0.76814 |  | 83.12%
246 | 0:41 | 84.6168 | 90 | 3 | 0.5 | 90 | 5 | 20 | -18.8078 | -4.702 | -4.702 | 85.298 | 85.298 | -5.3832 | 88.65% | 89.75% | 91.05% | 91.89% | 92.35% | 92.91% | 93.71% | 95.46% | 95.35% | 94.78% | 93.98% | 91.02% | 83.66% | 96.38% | 95.03% | 93.23% | 91.52% | 89.39% | 88.07% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 96.38% | 13 | +130s | 120 | 60% | 0.13624 | 0.86376 | 4.702 | 0.21819 | 0.78181 | 0.78181 |  | 78.19%
247 | 0:41 | 84.5673 | 90 | 3 | 0.5 | 90 | 5 | 20 | -18.4729 | -4.6182 | -4.6182 | 85.3818 | 85.3818 | -5.4327 | 86.91% | 88.45% | 89.49% | 90.06% | 90.79% | 92.18% | 94.59% | 94.81% | 94.94% | 94.96% | 92.59% | 86.27% | 97.34% | 95.99% | 94.2% | 92.48% | 90.36% | 89.03% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 97.34% | 12 | +120s | 110 | 63.33% | 0.1629 | 0.8371 | 4.6182 | 0.26089 | 0.73911 | 0.73911 |  | 78.2%
248 | 0:41 | 84.9744 | 90 | 3 | 0.5 | 90 | 5 | 20 | -18.0983 | -4.5246 | -4.5246 | 85.4754 | 85.4754 | -5.0256 | 84.73% | 86% | 86.71% | 87.64% | 89.75% | 92.95% | 93.58% | 94.57% | 95.61% | 93.99% | 88.97% | 98.32% | 96.97% | 95.17% | 93.46% | 91.33% | 90.01% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 98.32% | 11 | +110s | 100 | 66.67% | 0.10019 | 0.89981 | 4.5246 | 0.16046 | 0.83954 | 0.83954 |  | 82.98%
249 | 0:41 | 84.8818 | 90 | 3 | 0.5 | 90 | 5 | 20 | -17.685 | -4.4213 | -4.4213 | 85.5787 | 85.5787 | -5.1182 | 88.34% | 88.94% | 89.76% | 91.17% | 92.05% | 93.16% | 94.51% | 95.69% | 97.14% | 99.07% | 99.31% | 97.96% | 96.16% | 94.45% | 92.33% | 91% | 88.93% | 87.64% | 86.5% | 85.45% | 84.01% | 83.05% | 81.81% | 80.94% | 80.17% | 79.19% | 78.62% | 78.68% | 78.61% | 78.33% | 99.31% | 10 | +100s | 90 | 70% | 0.13939 | 0.86061 | 4.4213 | 0.22324 | 0.77676 | 0.77676 |  | 82.33%
250 | 0:41 | 84.5697 | 90 | 3 | 0.5 | 90 | 5 | 20 | -17.2338 | -4.3085 | -4.3085 | 85.6915 | 85.6915 | -5.4303 | 87.94% | 88.76% | 90.17% | 91.05% | 92.16% | 93.51% | 94.69% | 96.14% | 98.07% | 99.69% | 98.96% | 97.16% | 95.45% | 93.33% | 92% | 89.93% | 88.64% | 87.5% | 86.45% | 85.01% | 84.05% | 82.81% | 81.94% | 81.17% | 80.19% | 79.62% | 79.68% | 79.61% | 79.33% | 79.16% | 99.69% | 9 | +90s | 80 | 73.33% | 0.22437 | 0.77563 | 4.3085 | 0.35933 | 0.64067 | 0.64067 |  | 79.03%
251 | 0:42 | 84.7584 | 90 | 3 | 0.5 | 90 | 5 | 20 | -16.7457 | -4.1864 | -4.1864 | 85.8136 | 85.8136 | -5.2416 | 87.75% | 89.16% | 90.04% | 91.16% | 92.51% | 93.68% | 95.14% | 97.07% | 98.68% | 99.97% | 98.17% | 96.46% | 94.33% | 93.01% | 90.94% | 89.65% | 88.5% | 87.46% | 86.02% | 85.06% | 83.81% | 82.95% | 82.18% | 81.19% | 80.62% | 80.69% | 80.62% | 80.33% | 80.16% | 79.84% | 99.97% | 9 | +90s | 80 | 73.33% | 0.21104 | 0.78896 | 4.1864 | 0.33798 | 0.66202 | 0.66202 |  | 79.84%
252 | 0:42 | 85.7739 | 90 | 3 | 0.5 | 90 | 5 | 20 | -16.2216 | -4.0554 | -4.0554 | 85.9446 | 85.9446 | -4.2261 | 88.15% | 89.02% | 90.14% | 91.49% | 92.67% | 94.12% | 96.05% | 97.67% | 99.02% | 99.19% | 97.47% | 95.35% | 94.02% | 91.95% | 90.66% | 89.52% | 88.47% | 87.03% | 86.07% | 84.83% | 83.96% | 83.19% | 82.21% | 81.64% | 81.7% | 81.63% | 81.35% | 81.18% | 80.85% | 80.76% | 99.19% | 9 | +90s | 80 | 73.33% | 0.034131 | 0.96587 | 4.0554 | 0.054661 | 0.94534 | 0.94534 |  | 89.02%
253 | 0:42 | 85.5382 | 90 | 3 | 0.5 | 90 | 5 | 20 | -15.6629 | -3.9157 | -3.9157 | 86.0843 | 86.0843 | -4.4618 | 88.01% | 89.13% | 90.48% | 91.65% | 93.11% | 95.04% | 96.65% | 98% | 99.8% | 98.49% | 96.36% | 95.04% | 92.97% | 91.68% | 90.53% | 89.48% | 88.05% | 87.09% | 85.84% | 84.98% | 84.2% | 83.22% | 82.65% | 82.72% | 82.65% | 82.36% | 82.19% | 81.87% | 81.77% | 82.24% | 99.8% | 8 | +80s | 70 | 76.67% | 0.10921 | 0.89079 | 3.9157 | 0.1749 | 0.8251 | 0.8251 |  | 86.32%
254 | 0:42 | 85.1857 | 90 | 3 | 0.5 | 90 | 5 | 20 | -15.0705 | -3.7676 | -3.7676 | 86.2324 | 86.2324 | -4.8143 | 88.11% | 89.46% | 90.63% | 92.09% | 94.02% | 95.63% | 96.98% | 98.78% | 99.5% | 97.38% | 96.06% | 93.98% | 92.69% | 91.55% | 90.5% | 89.07% | 88.11% | 86.86% | 85.99% | 85.22% | 84.24% | 83.67% | 83.74% | 83.66% | 83.38% | 83.21% | 82.89% | 82.79% | 83.25% | 82.86% | 99.5% | 8 | +80s | 70 | 76.67% | 0.20933 | 0.79067 | 3.7676 | 0.33525 | 0.66475 | 0.66475 |  | 80.88%
255 | 0:42 | 85.8264 | 90 | 3 | 0.5 | 90 | 5 | 20 | -14.4458 | -3.6115 | -3.6115 | 86.3885 | 86.3885 | -4.1736 | 88.44% | 89.62% | 91.07% | 93% | 94.62% | 95.97% | 97.76% | 99.48% | 98.4% | 97.07% | 95% | 93.71% | 92.57% | 91.52% | 90.08% | 89.12% | 87.88% | 87.01% | 86.24% | 85.26% | 84.69% | 84.75% | 84.68% | 84.4% | 84.23% | 83.9% | 83.81% | 84.27% | 83.88% | 83.58% | 99.48% | 7 | +70s | 60 | 80% | 0.11242 | 0.88758 | 3.6115 | 0.18004 | 0.81996 | 0.81996 |  | 87.16%
256 | 0:42 | 85.9297 | 90 | 3 | 0.5 | 90 | 5 | 20 | -13.7902 | -3.4476 | -3.4476 | 86.5524 | 86.5524 | -4.0703 | 88.6% | 90.06% | 91.99% | 93.6% | 94.95% | 96.75% | 98.47% | 99.41% | 98.09% | 96.01% | 94.72% | 93.58% | 92.53% | 91.1% | 90.14% | 88.89% | 88.02% | 87.25% | 86.27% | 85.7% | 85.77% | 85.69% | 85.41% | 85.24% | 84.92% | 84.82% | 85.28% | 84.89% | 84.6% | 85.03% | 99.41% | 7 | +70s | 60 | 80% | 0.12455 | 0.87545 | 3.4476 | 0.19947 | 0.80053 | 0.80053 |  | 86.49%
257 | 0:43 | 85.7499 | 90 | 3 | 0.5 | 90 | 5 | 20 | -13.1051 | -3.2763 | -3.2763 | 86.7237 | 86.7237 | -4.2501 | 89.05% | 90.98% | 92.59% | 93.94% | 95.74% | 97.46% | 99.58% | 99.1% | 97.02% | 95.73% | 94.59% | 93.54% | 92.1% | 91.14% | 89.9% | 89.03% | 88.26% | 87.28% | 86.71% | 86.77% | 86.7% | 86.42% | 86.25% | 85.93% | 85.83% | 86.29% | 85.9% | 85.6% | 86.04% | 86.1% | 99.58% | 6 | +60s | 50 | 83.33% | 0.19477 | 0.80523 | 3.2763 | 0.31193 | 0.68807 | 0.68807 |  | 83.91%
258 | 0:43 | 86.5694 | 90 | 3 | 0.5 | 90 | 5 | 20 | -12.3918 | -3.098 | -3.098 | 86.902 | 86.902 | -3.4306 | 89.98% | 91.59% | 92.94% | 94.74% | 96.46% | 98.58% | 99.9% | 98.02% | 96.73% | 95.59% | 94.54% | 93.1% | 92.14% | 90.9% | 90.03% | 89.26% | 88.28% | 87.71% | 87.77% | 87.7% | 87.42% | 87.25% | 86.93% | 86.83% | 87.29% | 86.9% | 86.6% | 87.04% | 87.1% | 86.99% | 99.9% | 6 | +60s | 50 | 83.33% | 0.066535 | 0.93346 | 3.098 | 0.10656 | 0.89344 | 0.89344 |  | 90.86%
259 | 0:43 | 86.0659 | 90 | 3 | 0.5 | 90 | 5 | 20 | -11.652 | -2.913 | -2.913 | 87.087 | 87.087 | -3.9341 | 90.6% | 91.95% | 93.75% | 95.47% | 97.59% | 98.91% | 92.67% | 94.37% | 94.74% | 93.7% | 92.36% | 90.72% | 88.55% | 87.11% | 86.96% | 84.95% | 84.33% | 82.04% | 80.55% | 80.87% | 79.37% | 79.57% | 81.24% | 80.72% | 79.53% | 79.6% | 79.45% | 78.54% | 78.77% | 80.54% | 98.91% | 5 | +50s | 40 | 86.67% | 0.20421 | 0.79579 | 2.913 | 0.32705 | 0.67295 | 0.67295 |  | 84.29%
260 | 0:43 | 86.2779 | 90 | 3 | 0.5 | 90 | 5 | 20 | -10.8873 | -2.7218 | -2.7218 | 87.2782 | 87.2782 | -3.7221 | 90.98% | 92.77% | 94.49% | 96.61% | 97.94% | 90.76% | 93.41% | 94.55% | 94.33% | 94.06% | 92.96% | 91.51% | 90.39% | 90.3% | 88.7% | 88.19% | 86.16% | 84.85% | 85.13% | 83.81% | 83.99% | 85.46% | 84.98% | 83.96% | 84.02% | 83.88% | 83.08% | 83.28% | 84.84% | 84.48% | 97.94% | 4 | +40s | 30 | 90% | 0.20005 | 0.79995 | 2.7218 | 0.32039 | 0.67961 | 0.67961 |  | 85.3%
261 | 0:43 | 86.7655 | 90 | 3 | 0.5 | 90 | 5 | 20 | -10.0992 | -2.5248 | -2.5248 | 87.4752 | 87.4752 | -3.2345 | 91.81% | 93.53% | 95.65% | 96.97% | 88.78% | 92.18% | 93.94% | 94.4% | 94.98% | 94.33% | 93.46% | 92.61% | 92.57% | 91.31% | 90.89% | 89.08% | 87.92% | 88.17% | 87.01% | 87.16% | 88.46% | 88.03% | 87.15% | 87.2% | 87.07% | 86.35% | 86.53% | 87.91% | 87.6% | 87.91% | 96.97% | 3 | +30s | 20 | 93.33% | 0.14194 | 0.85806 | 2.5248 | 0.22732 | 0.77268 | 0.77268 |  | 89.19%
262 | 0:43 | 87.1127 | 90 | 3 | 0.5 | 90 | 5 | 20 | -9.2894 | -2.3224 | -2.3224 | 87.6776 | 87.6776 | -2.8873 | 92.58% | 94.7% | 96.02% | 86.87% | 90.87% | 93.13% | 94.15% | 95.44% | 95.16% | 94.77% | 94.15% | 94.14% | 93.17% | 92.81% | 91.2% | 90.17% | 90.39% | 89.36% | 89.49% | 90.65% | 90.26% | 89.49% | 89.53% | 89.42% | 88.77% | 88.92% | 90.16% | 89.89% | 90.17% | 90.8% | 96.02% | 2 | +20s | 10 | 96.67% | 0.11299 | 0.88701 | 2.3224 | 0.18095 | 0.81905 | 0.81905 |  | 91.53%
263 | 0:44 | 87.5372 | 90 | 3 | 0.5 | 90 | 5 | 20 | -8.4598 | -2.1149 | -2.1149 | 87.8851 | 87.8851 | -2.4628 | 93.77% | 95.09% | 85.07% | 89.58% | 92.25% | 93.73% | 95.6% | 95.64% | 95.66% | 95.22% | 95.24% | 94.52% | 94.22% | 92.76% | 91.85% | 92.04% | 91.13% | 91.24% | 92.28% | 91.92% | 91.25% | 91.29% | 91.18% | 90.6% | 90.73% | 91.84% | 91.6% | 91.86% | 92.43% | 92.66% | 95.66% | 8 | +80s | 70 | 76.67% | 0.069578 | 0.93042 | 2.1149 | 0.11143 | 0.88857 | 0.88857 |  | 87.06%
264 | 0:44 | 87.2726 | 90 | 3 | 0.5 | 90 | 5 | 20 | -7.612 | -1.903 | -1.903 | 88.097 | 88.097 | -2.7274 | 94.18% | 83.41% | 88.33% | 91.36% | 93.22% | 95.59% | 95.89% | 96.25% | 95.98% | 96.02% | 95.51% | 95.26% | 93.95% | 93.13% | 93.3% | 92.49% | 92.58% | 93.51% | 93.18% | 92.6% | 92.63% | 92.53% | 92% | 92.12% | 93.12% | 92.91% | 93.14% | 93.67% | 93.88% | 92.67% | 96.25% | 7 | +70s | 60 | 80% | 0.16488 | 0.83512 | 1.903 | 0.26406 | 0.73594 | 0.73594 |  | 83.28%
265 | 0:44 | 87.9108 | 90 | 3 | 0.5 | 90 | 5 | 20 | -6.7479 | -1.687 | -1.687 | 88.313 | 88.313 | -2.0892 | 81.88% | 87.16% | 90.48% | 92.68% | 95.47% | 96% | 96.66% | 96.52% | 96.59% | 96.25% | 96.05% | 94.85% | 94.12% | 94.27% | 93.55% | 93.63% | 94.47% | 94.16% | 93.65% | 93.68% | 93.59% | 93.1% | 93.2% | 94.11% | 93.92% | 94.14% | 94.63% | 94.82% | 93.7% | 92.61% | 96.66% | 6 | +60s | 50 | 83.33% | 0.080452 | 0.91955 | 1.687 | 0.12885 | 0.87115 | 0.87115 |  | 89.03%
266 | 0:44 | 87.5481 | 90 | 3 | 0.5 | 90 | 5 | 20 | -5.8694 | -1.4673 | -1.4673 | 88.5327 | 88.5327 | -2.4519 | 86.06% | 89.64% | 92.12% | 95.28% | 96% | 96.92% | 96.9% | 96.99% | 96.81% | 96.65% | 95.56% | 94.9% | 95.03% | 94.38% | 94.46% | 95.21% | 94.93% | 94.48% | 94.51% | 94.42% | 93.98% | 94.07% | 94.89% | 94.72% | 94.93% | 95.38% | 95.56% | 94.52% | 93.53% | 93.73% | 96.99% | 7 | +70s | 60 | 80% | 0.19692 | 0.80308 | 1.4673 | 0.31536 | 0.68464 | 0.68464 |  | 81.82%
267 | 0:44 | 87.6965 | 90 | 3 | 0.5 | 90 | 5 | 20 | -4.9782 | -1.2446 | -1.2446 | 88.7554 | 88.7554 | -2.3035 | 88.83% | 91.57% | 95.05% | 95.94% | 97.09% | 97.18% | 97.28% | 97.24% | 97.11% | 96.12% | 95.52% | 95.64% | 95.06% | 95.12% | 95.81% | 95.54% | 95.15% | 95.17% | 95.1% | 94.69% | 94.77% | 95.51% | 95.37% | 95.56% | 95.98% | 96.14% | 95.18% | 94.27% | 94.45% | 93.95% | 97.28% | 6 | +60s | 50 | 83.33% | 0.21179 | 0.78821 | 1.2446 | 0.33918 | 0.66082 | 0.66082 |  | 82.23%
268 | 0:44 | 87.6585 | 90 | 3 | 0.5 | 90 | 5 | 20 | -4.0764 | -1.0191 | -1.0191 | 88.9809 | 88.9809 | -2.3415 | 91.03% | 94.79% | 95.84% | 97.18% | 97.37% | 97.49% | 97.56% | 97.47% | 96.56% | 96.02% | 96.13% | 95.61% | 95.66% | 96.28% | 96.03% | 95.7% | 95.71% | 95.64% | 95.27% | 95.34% | 96.01% | 95.89% | 96.07% | 96.46% | 96.61% | 95.72% | 94.89% | 95.04% | 94.6% | 93.99% | 97.56% | 6 | +60s | 50 | 83.33% | 0.26449 | 0.73551 | 1.0191 | 0.42358 | 0.57642 | 0.57642 |  | 79.51%
269 | 0:45 | 87.9946 | 90 | 3 | 0.5 | 90 | 5 | 20 | -3.1659 | -0.79147 | -0.79147 | 89.2085 | 89.2085 | -2.0054 | 94.52% | 95.7% | 97.23% | 97.5% | 97.63% | 97.82% | 97.75% | 96.92% | 96.43% | 96.53% | 96.06% | 96.11% | 96.67% | 96.44% | 96.15% | 96.16% | 96.09% | 95.75% | 95.81% | 96.42% | 96.31% | 96.48% | 96.85% | 96.99% | 96.16% | 95.39% | 95.53% | 95.14% | 94.57% | 94.87% | 97.82% | 5 | +50s | 40 | 86.67% | 0.24278 | 0.75722 | 0.79147 | 0.38881 | 0.61119 | 0.61119 |  | 81.87%
270 | 0:45 | 88.1984 | 90 | 3 | 0.5 | 90 | 5 | 20 | -2.2486 | -0.56214 | -0.56214 | 89.4379 | 89.4379 | -1.8016 | 95.55% | 97.23% | 97.58% | 97.73% | 98.01% | 97.97% | 97.21% | 96.77% | 96.86% | 96.44% | 96.48% | 96.99% | 96.77% | 96.52% | 96.53% | 96.47% | 96.15% | 96.2% | 96.76% | 96.67% | 96.83% | 97.17% | 97.3% | 96.52% | 95.82% | 95.95% | 95.59% | 95.05% | 95.32% | 95.22% | 98.01% | 4 | +40s | 30 | 90% | 0.24789 | 0.75211 | 0.56214 | 0.39701 | 0.60299 | 0.60299 |  | 82.77%
271 | 0:45 | 88.4759 | 90 | 3 | 0.5 | 90 | 5 | 20 | -1.3264 | -0.33161 | -0.33161 | 89.6684 | 89.6684 | -1.5241 | 97.21% | 97.63% | 97.78% | 98.16% | 98.14% | 97.45% | 97.05% | 97.13% | 96.76% | 96.79% | 97.25% | 97.04% | 96.83% | 96.84% | 96.78% | 96.49% | 96.53% | 97.04% | 96.96% | 97.11% | 97.44% | 97.55% | 96.83% | 96.18% | 96.3% | 95.97% | 95.47% | 95.71% | 95.61% | 96.07% | 98.16% | 3 | +30s | 20 | 93.33% | 0.2385 | 0.7615 | 0.33161 | 0.38197 | 0.61803 | 0.61803 |  | 84.43%
272 | 0:45 | 88.752 | 90 | 3 | 0.5 | 90 | 5 | 20 | -0.40146 | -0.10036 | -0.10036 | 89.8996 | 89.8996 | -1.248 | 97.65% | 97.81% | 98.28% | 98.28% | 97.64% | 97.29% | 97.35% | 97.02% | 97.05% | 97.46% | 97.27% | 97.1% | 97.1% | 97.05% | 96.77% | 96.81% | 97.27% | 97.21% | 97.35% | 97.65% | 97.76% | 97.08% | 96.49% | 96.59% | 96.31% | 95.83% | 96.04% | 95.94% | 96.36% | 96.5% | 98.28% | 3 | +30s | 20 | 93.33% | 0.22953 | 0.77047 | 0.10036 | 0.36759 | 0.63241 | 0.63241 |  | 84.95%
273 | 0:45 | 89.2482 | 90 | 3 | 0.5 | 90 | 5 | 20 | 0.52438 | 0.13109 | 0.13109 | 90.1311 | 90.1311 | -0.75183 | 97.82% | 98.36% | 98.38% | 97.8% | 97.48% | 97.54% | 97.25% | 97.27% | 97.64% | 97.46% | 97.32% | 97.32% | 97.27% | 97.02% | 97.05% | 97.47% | 97.41% | 97.55% | 97.84% | 97.94% | 97.3% | 96.76% | 96.85% | 96.59% | 96.14% | 96.33% | 96.23% | 96.6% | 96.73% | 96.95% | 98.38% | 2 | +20s | 10 | 96.67% | 0.17659 | 0.82341 | 0.13109 | 0.2828 | 0.7172 | 0.7172 |  | 88.92%
274 | 0:45 | 89.1962 | 90 | 3 | 0.5 | 90 | 5 | 20 | 1.4491 | 0.36227 | 0.36227 | 90.3623 | 90.3623 | -0.80376 | 98.42% | 98.46% | 97.93% | 97.65% | 97.7% | 97.44% | 97.46% | 97.79% | 97.62% | 97.51% | 97.51% | 97.47% | 97.23% | 97.26% | 97.64% | 97.59% | 97.72% | 97.99% | 98.08% | 97.48% | 96.99% | 97.07% | 96.84% | 96.41% | 96.58% | 96.48% | 96.81% | 96.93% | 97.13% | 97.23% | 98.46% | 1 | +10s | 0 | 100% | 0.23321 | 0.76679 | 0.36227 | 0.37349 | 0.62651 | 0.62651 |  | 87.04%
275 | 0:46 | 89.4937 | 90 | 3 | 0.5 | 90 | 5 | 20 | 2.3707 | 0.59268 | 0.59268 | 90.5927 | 90.5927 | -0.50627 | 98.52% | 98.04% | 97.79% | 97.83% | 97.61% | 97.62% | 97.92% | 97.76% | 97.68% | 97.67% | 97.63% | 97.42% | 97.44% | 97.78% | 97.74% | 97.86% | 98.11% | 98.2% | 97.64% | 97.19% | 97.26% | 97.06% | 96.66% | 96.79% | 96.71% | 96.99% | 97.1% | 97.28% | 97.37% | 97.12% | 98.52% | 0 | No Time Shift | 0 | 100% | 0.21979 | 0.78021 | 0.59268 | 0.352 | 0.648 | 0.648 |  | 87.77%
276 | 0:46 | 88.8681 | 90 | 3 | 0.5 | 90 | 5 | 20 | 3.2872 | 0.82181 | 0.82181 | 90.8218 | 90.8218 | -1.1319 | 98.13% | 97.91% | 97.94% | 97.75% | 97.76% | 98.02% | 97.87% | 97.82% | 97.81% | 97.77% | 97.57% | 97.59% | 97.89% | 97.87% | 97.98% | 98.22% | 98.3% | 97.78% | 97.37% | 97.42% | 97.26% | 96.87% | 96.99% | 96.9% | 97.15% | 97.25% | 97.41% | 97.49% | 97.27% | 97.19% | 98.3% | 16 | +160s | 150 | 50% | 0.39074 | 0.60926 | 0.82181 | 0.62577 | 0.37423 | 0.37423 |  | 61.91%
277 | 0:46 | 89.2655 | 90 | 3 | 0.5 | 90 | 5 | 20 | 4.1967 | 1.0492 | 1.0492 | 91.0492 | 91.0492 | -0.73453 | 98.01% | 98.03% | 97.88% | 97.88% | 98.11% | 97.96% | 97.94% | 97.93% | 97.89% | 97.71% | 97.73% | 97.99% | 97.97% | 98.08% | 98.31% | 98.38% | 97.89% | 97.52% | 97.57% | 97.43% | 97.06% | 97.16% | 97.08% | 97.28% | 97.37% | 97.52% | 97.59% | 97.4% | 97.33% | 97.09% | 98.38% | 15 | +150s | 140 | 53.33% | 0.35674 | 0.64326 | 1.0492 | 0.57133 | 0.42867 | 0.42867 |  | 64.86%
278 | 0:46 | 89.9707 | 90 | 3 | 0.5 | 90 | 5 | 20 | 5.0972 | 1.2743 | 1.2743 | 91.2743 | 91.2743 | -0.0293 | 98.11% | 97.98% | 97.98% | 98.18% | 98.04% | 98.04% | 98.03% | 98% | 97.83% | 97.84% | 98.08% | 98.07% | 98.17% | 98.38% | 98.45% | 97.99% | 97.66% | 97.7% | 97.58% | 97.23% | 97.31% | 97.23% | 97.4% | 97.48% | 97.61% | 97.68% | 97.51% | 97.45% | 97.23% | 97.38% | 98.45% | 14 | +140s | 130 | 56.67% | 0.26072 | 0.73928 | 1.2743 | 0.41755 | 0.58245 | 0.58245 |  | 71.12%
279 | 0:46 | 89.7146 | 90 | 3 | 0.5 | 90 | 5 | 20 | 5.9868 | 1.4967 | 1.4967 | 91.4967 | 91.4967 | -0.28537 | 98.07% | 98.06% | 98.23% | 98.11% | 98.13% | 98.12% | 98.09% | 97.94% | 97.94% | 98.14% | 98.14% | 98.24% | 98.44% | 98.5% | 98.08% | 97.78% | 97.81% | 97.71% | 97.39% | 97.45% | 97.37% | 97.5% | 97.58% | 97.69% | 97.75% | 97.6% | 97.55% | 97.36% | 97.5% | 97.7% | 98.5% | 13 | +130s | 120 | 60% | 0.35641 | 0.64359 | 1.4967 | 0.5708 | 0.4292 | 0.4292 |  | 67.14%
280 | 0:46 | 90.3795 | 90 | 3 | 0.5 | 90 | 5 | 20 | 6.8635 | 1.7159 | 1.7159 | 91.7159 | 91.7159 | 0.37952 | 98.14% | 98.28% | 98.16% | 98.21% | 98.2% | 98.16% | 98.03% | 98.03% | 98.2% | 98.21% | 98.3% | 98.48% | 98.54% | 98.15% | 97.89% | 97.91% | 97.83% | 97.52% | 97.57% | 97.49% | 97.59% | 97.66% | 97.76% | 97.8% | 97.69% | 97.64% | 97.47% | 97.6% | 97.79% | 97.78% | 98.54% | 12 | +120s | 110 | 63.33% | 0.26727 | 0.73273 | 1.7159 | 0.42804 | 0.57196 | 0.57196 |  | 73.02%
281 | 0:47 | 90.7073 | 90 | 3 | 0.5 | 90 | 5 | 20 | 7.7255 | 1.9314 | 1.9314 | 91.9314 | 91.9314 | 0.7073 | 98.31% | 98.2% | 98.27% | 98.26% | 98.23% | 98.11% | 98.1% | 98.25% | 98.26% | 98.35% | 98.52% | 98.57% | 98.21% | 97.98% | 97.99% | 97.94% | 97.65% | 97.67% | 97.6% | 97.67% | 97.73% | 97.81% | 97.85% | 97.76% | 97.71% | 97.57% | 97.69% | 97.86% | 97.85% | 98.03% | 98.57% | 11 | +110s | 100 | 66.67% | 0.24482 | 0.75518 | 1.9314 | 0.39208 | 0.60792 | 0.60792 |  | 75.34%
282 | 0:47 | 89.9869 | 90 | 3 | 0.5 | 90 | 5 | 20 | 8.571 | 2.1428 | 2.1428 | 92.1428 | 92.1428 | -0.013139 | 98.23% | 98.32% | 98.31% | 98.28% | 98.18% | 98.17% | 98.28% | 98.31% | 98.39% | 98.54% | 98.59% | 98.26% | 98.06% | 98.06% | 98.04% | 97.76% | 97.77% | 97.7% | 97.74% | 97.79% | 97.86% | 97.89% | 97.82% | 97.78% | 97.65% | 97.77% | 97.93% | 97.92% | 98.07% | 98% | 98.59% | 10 | +100s | 90 | 70% | 0.43118 | 0.56882 | 2.1428 | 0.69054 | 0.30946 | 0.30946 |  | 66.51%
283 | 0:47 | 90.6701 | 90 | 3 | 0.5 | 90 | 5 | 20 | 9.3981 | 2.3495 | 2.3495 | 92.3495 | 92.3495 | 0.67009 | 98.37% | 98.35% | 98.33% | 98.24% | 98.22% | 98.31% | 98.34% | 98.42% | 98.56% | 98.6% | 98.3% | 98.13% | 98.13% | 98.12% | 97.86% | 97.85% | 97.78% | 97.79% | 97.84% | 97.89% | 97.92% | 97.87% | 97.83% | 97.73% | 97.84% | 97.99% | 97.97% | 98.1% | 98.02% | 98% | 98.6% | 9 | +90s | 80 | 73.33% | 0.33589 | 0.66411 | 2.3495 | 0.53793 | 0.46207 | 0.46207 |  | 72.71%
284 | 0:47 | 91.0843 | 90 | 3 | 0.5 | 90 | 5 | 20 | 10.2051 | 2.5513 | 2.5513 | 92.5513 | 92.5513 | 1.0843 | 98.39% | 98.36% | 98.29% | 98.27% | 98.33% | 98.36% | 98.44% | 98.57% | 98.61% | 98.33% | 98.2% | 98.18% | 98.2% | 97.95% | 97.93% | 97.86% | 97.84% | 97.88% | 97.92% | 97.94% | 97.91% | 97.88% | 97.8% | 97.9% | 98.04% | 98.02% | 98.12% | 98.02% | 98.03% | 98.22% | 98.61% | 8 | +80s | 70 | 76.67% | 0.29339 | 0.70661 | 2.5513 | 0.46986 | 0.53014 | 0.53014 |  | 76.1%
285 | 0:47 | 90.6269 | 90 | 3 | 0.5 | 90 | 5 | 20 | 10.9902 | 2.7475 | 2.7475 | 92.7475 | 92.7475 | 0.62694 | 98.39% | 98.33% | 98.31% | 98.34% | 98.38% | 98.45% | 98.57% | 98.6% | 98.35% | 98.25% | 98.23% | 98.26% | 98.04% | 98% | 97.93% | 97.88% | 97.91% | 97.94% | 97.95% | 97.94% | 97.92% | 97.85% | 97.95% | 98.08% | 98.06% | 98.13% | 98.02% | 98.06% | 98.23% | 98.05% | 98.6% | 7 | +70s | 60 | 80% | 0.42412 | 0.57588 | 2.7475 | 0.67924 | 0.32076 | 0.32076 |  | 70.23%
286 | 0:47 | 90.9104 | 90 | 3 | 0.5 | 90 | 5 | 20 | 11.7517 | 2.9379 | 2.9379 | 92.9379 | 92.9379 | 0.91035 | 98.36% | 98.34% | 98.34% | 98.39% | 98.45% | 98.56% | 98.59% | 98.37% | 98.3% | 98.27% | 98.32% | 98.11% | 98.06% | 97.99% | 97.91% | 97.94% | 97.95% | 97.96% | 97.96% | 97.95% | 97.9% | 97.99% | 98.11% | 98.09% | 98.13% | 98.01% | 98.07% | 98.23% | 98.08% | 97.87% | 98.59% | 6 | +60s | 50 | 83.33% | 0.40552 | 0.59448 | 2.9379 | 0.64944 | 0.35056 | 0.35056 |  | 72.33%
287 | 0:48 | 91.4468 | 90 | 3 | 0.5 | 90 | 5 | 20 | 12.4881 | 3.122 | 3.122 | 93.122 | 93.122 | 1.4468 | 98.36% | 98.34% | 98.39% | 98.45% | 98.55% | 98.57% | 98.37% | 98.33% | 98.3% | 98.37% | 98.18% | 98.11% | 98.04% | 97.94% | 97.96% | 97.95% | 97.95% | 97.98% | 97.97% | 97.95% | 98.03% | 98.13% | 98.11% | 98.13% | 98% | 98.08% | 98.23% | 98.09% | 97.92% | 97.67% | 98.57% | 5 | +50s | 40 | 86.67% | 0.33505 | 0.66495 | 3.122 | 0.53658 | 0.46342 | 0.46342 |  | 77.19%
288 | 0:48 | 91.8889 | 90 | 3 | 0.5 | 90 | 5 | 20 | 13.1977 | 3.2994 | 3.2994 | 93.2994 | 93.2994 | 1.8889 | 98.32% | 98.39% | 98.44% | 98.53% | 98.54% | 98.38% | 98.37% | 98.32% | 98.42% | 98.24% | 98.15% | 98.09% | 97.95% | 97.97% | 97.95% | 97.94% | 97.99% | 97.99% | 97.98% | 98.06% | 98.15% | 98.13% | 98.12% | 97.97% | 98.09% | 98.22% | 98.1% | 97.95% | 97.72% | 96.72% | 98.54% | 4 | +40s | 30 | 90% | 0.2821 | 0.7179 | 3.2994 | 0.45179 | 0.54821 | 0.54821 |  | 81.12%
289 | 0:48 | 91.8965 | 90 | 3 | 0.5 | 90 | 5 | 20 | 13.879 | 3.4698 | 3.4698 | 93.4698 | 93.4698 | 1.8965 | 98.38% | 98.42% | 98.5% | 98.51% | 98.37% | 98.39% | 98.34% | 98.45% | 98.29% | 98.19% | 98.13% | 97.96% | 97.97% | 97.93% | 97.93% | 98% | 98% | 98.01% | 98.08% | 98.16% | 98.14% | 98.1% | 97.94% | 98.08% | 98.21% | 98.1% | 97.99% | 97.76% | 96.8% | 96.23% | 98.51% | 3 | +30s | 20 | 93.33% | 0.31466 | 0.68534 | 3.4698 | 0.50393 | 0.49607 | 0.49607 |  | 80.48%
290 | 0:48 | 91.6967 | 90 | 3 | 0.5 | 90 | 5 | 20 | 14.5306 | 3.6327 | 3.6327 | 93.6327 | 93.6327 | 1.6967 | 98.4% | 98.46% | 98.47% | 98.35% | 98.4% | 98.35% | 98.48% | 98.34% | 98.22% | 98.16% | 97.96% | 97.96% | 97.92% | 97.9% | 97.99% | 98% | 98.03% | 98.09% | 98.16% | 98.14% | 98.07% | 97.9% | 98.07% | 98.18% | 98.09% | 98.01% | 97.8% | 96.86% | 96.32% | 94.26% | 98.48% | 6 | +60s | 50 | 83.33% | 0.3872 | 0.6128 | 3.6327 | 0.6201 | 0.3799 | 0.3799 |  | 73.27%
291 | 0:48 | 91.9894 | 90 | 3 | 0.5 | 90 | 5 | 20 | 15.151 | 3.7878 | 3.7878 | 93.7878 | 93.7878 | 1.9894 | 98.41% | 98.42% | 98.33% | 98.41% | 98.35% | 98.5% | 98.37% | 98.24% | 98.18% | 97.96% | 97.95% | 97.89% | 97.87% | 97.98% | 97.99% | 98.04% | 98.1% | 98.15% | 98.13% | 98.04% | 97.85% | 98.05% | 98.15% | 98.08% | 98.03% | 97.83% | 96.93% | 96.42% | 94.44% | 91.27% | 98.5% | 5 | +50s | 40 | 86.67% | 0.35967 | 0.64033 | 3.7878 | 0.57602 | 0.42398 | 0.42398 |  | 75.86%
292 | 0:48 | 92.2821 | 90 | 3 | 0.5 | 90 | 5 | 20 | 15.739 | 3.9348 | 3.9348 | 93.9348 | 93.9348 | 2.2821 | 98.36% | 98.3% | 98.41% | 98.34% | 98.52% | 98.4% | 98.25% | 98.2% | 97.94% | 97.93% | 97.85% | 97.82% | 97.96% | 97.98% | 98.05% | 98.1% | 98.14% | 98.11% | 97.99% | 97.8% | 98.02% | 98.11% | 98.05% | 98.04% | 97.85% | 96.98% | 96.5% | 94.61% | 91.53% | 88.23% | 98.52% | 4 | +40s | 30 | 90% | 0.33052 | 0.66948 | 3.9348 | 0.52934 | 0.47066 | 0.47066 |  | 78.53%
293 | 0:49 | 91.7731 | 90 | 3 | 0.5 | 90 | 5 | 20 | 16.2933 | 4.0733 | 4.0733 | 94.0733 | 94.0733 | 1.7731 | 98.26% | 98.41% | 98.33% | 98.52% | 98.43% | 98.26% | 98.21% | 97.92% | 97.9% | 97.81% | 97.77% | 97.93% | 97.95% | 98.05% | 98.09% | 98.12% | 98.09% | 97.94% | 97.73% | 97.98% | 98.06% | 98.02% | 98.04% | 97.86% | 97.03% | 96.58% | 94.77% | 91.78% | 88.55% | 85.11% | 98.52% | 3 | +30s | 20 | 93.33% | 0.46003 | 0.53997 | 4.0733 | 0.73675 | 0.26325 | 0.26325 |  | 72.73%
294 | 0:49 | 92.0797 | 90 | 3 | 0.5 | 90 | 5 | 20 | 16.8126 | 4.2031 | 4.2031 | 94.2031 | 94.2031 | 2.0797 | 98.39% | 98.3% | 98.52% | 98.44% | 98.25% | 98.21% | 97.89% | 97.86% | 97.76% | 97.71% | 97.89% | 97.92% | 98.03% | 98.07% | 98.09% | 98.06% | 97.88% | 97.66% | 97.94% | 98% | 97.98% | 98.03% | 97.86% | 97.07% | 96.66% | 94.93% | 92.04% | 88.88% | 85.51% | 79.68% | 98.52% | 2 | +20s | 10 | 96.67% | 0.42469 | 0.57531 | 4.2031 | 0.68015 | 0.31985 | 0.31985 |  | 75.72%
295 | 0:49 | 92.7655 | 90 | 3 | 0.5 | 90 | 5 | 20 | 17.2959 | 4.324 | 4.324 | 94.324 | 94.324 | 2.7655 | 98.27% | 98.51% | 98.45% | 98.24% | 98.2% | 97.85% | 97.81% | 97.69% | 97.64% | 97.84% | 97.88% | 98.01% | 98.04% | 98.04% | 98.02% | 97.81% | 97.57% | 97.88% | 97.93% | 97.93% | 98.01% | 97.85% | 97.1% | 96.72% | 95.09% | 92.29% | 89.21% | 85.91% | 80.18% | 69.69% | 98.51% | 1 | +10s | 0 | 100% | 0.31169 | 0.68831 | 4.324 | 0.49918 | 0.50082 | 0.50082 |  | 82.86%
296 | 0:49 | 92.7472 | 90 | 3 | 0.5 | 90 | 5 | 20 | 17.7421 | 4.4355 | 4.4355 | 94.4355 | 94.4355 | 2.7472 | 98.49% | 98.44% | 98.22% | 98.18% | 97.8% | 97.75% | 97.62% | 97.56% | 97.78% | 97.83% | 97.98% | 98% | 97.99% | 97.96% | 97.72% | 97.47% | 97.81% | 97.84% | 97.87% | 97.99% | 97.84% | 97.13% | 96.78% | 95.24% | 92.55% | 89.54% | 86.31% | 80.69% | 70.32% | 60.86% | 98.49% | 0 | No Time Shift | 0 | 100% | 0.33766 | 0.66234 | 4.4355 | 0.54077 | 0.45923 | 0.45923 |  | 81.47%
297 | 0:49 | 92.4972 | 90 | 3 | 0.5 | 90 | 5 | 20 | 18.1503 | 4.5376 | 4.5376 | 94.5376 | 94.5376 | 2.4972 | 98.43% | 98.19% | 98.15% | 97.73% | 97.68% | 97.53% | 97.46% | 97.71% | 97.76% | 97.94% | 97.95% | 97.93% | 97.9% | 97.63% | 97.36% | 97.73% | 97.75% | 97.79% | 97.95% | 97.81% | 97.14% | 96.83% | 95.39% | 92.8% | 89.87% | 86.72% | 81.22% | 70.96% | 61.57% | 83.6% | 98.43% | 0 | No Time Shift | 0 | 100% | 0.40808 | 0.59192 | 4.5376 | 0.65355 | 0.34645 | 0.34645 |  | 77.69%
298 | 0:49 | 93.3679 | 90 | 3 | 0.5 | 90 | 5 | 20 | 18.5196 | 4.6299 | 4.6299 | 94.6299 | 94.6299 | 3.3679 | 98.14% | 98.11% | 97.65% | 97.59% | 97.42% | 97.35% | 97.62% | 97.68% | 97.88% | 97.89% | 97.85% | 97.82% | 97.51% | 97.23% | 97.64% | 97.64% | 97.7% | 97.9% | 97.78% | 97.14% | 96.88% | 95.54% | 93.05% | 90.21% | 87.14% | 81.75% | 71.62% | 62.32% | 84.06% | 82.74% | 98.14% | 0 | No Time Shift | 0 | 100% | 0.25241 | 0.74759 | 4.6299 | 0.40423 | 0.59577 | 0.59577 |  | 85.91%
299 | 0:50 | 92.8582 | 90 | 3 | 0.5 | 90 | 5 | 20 | 18.8493 | 4.7123 | 4.7123 | 94.7123 | 94.7123 | 2.8582 | 98.05% | 97.56% | 97.49% | 97.3% | 97.22% | 97.52% | 97.59% | 97.81% | 97.81% | 97.76% | 97.72% | 97.38% | 97.08% | 97.52% | 97.51% | 97.6% | 97.83% | 97.72% | 97.14% | 96.91% | 95.67% | 93.31% | 90.55% | 87.56% | 82.3% | 72.3% | 63.09% | 84.56% | 83.24% | 81.58% | 98.05% | 0 | No Time Shift | 0 | 100% | 0.37083 | 0.62917 | 4.7123 | 0.5939 | 0.4061 | 0.4061 |  | 79.55%
300 | 0:50 | 93.8579 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.1385 | 4.7846 | 4.7846 | 94.7846 | 94.7846 | 3.8579 | 97.45% | 97.37% | 97.16% | 97.07% | 97.4% | 97.47% | 97.73% | 97.71% | 97.64% | 97.61% | 97.23% | 96.92% | 97.39% | 97.36% | 97.47% | 97.75% | 97.65% | 97.12% | 96.93% | 95.81% | 93.56% | 90.89% | 88% | 82.87% | 73.01% | 63.89% | 85.1% | 83.78% | 82.12% | 80.89% | 97.75% | 15 | +150s | 140 | 53.33% | 0.18535 | 0.81465 | 4.7846 | 0.29684 | 0.70316 | 0.70316 |  | 73.8%
301 | 0:50 | 93.5125 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.3867 | 4.8467 | 4.8467 | 94.8467 | 94.8467 | 3.5125 | 97.22% | 97% | 96.9% | 97.25% | 97.34% | 97.62% | 97.6% | 97.51% | 97.47% | 97.05% | 96.72% | 97.24% | 97.19% | 97.32% | 97.64% | 97.57% | 97.08% | 96.94% | 95.93% | 93.82% | 91.25% | 88.45% | 83.46% | 73.75% | 64.73% | 85.68% | 84.36% | 82.7% | 81.47% | 79.51% | 97.64% | 14 | +140s | 130 | 56.67% | 0.26683 | 0.73317 | 4.8467 | 0.42733 | 0.57267 | 0.57267 |  | 70.53%
302 | 0:50 | 93.9347 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.5934 | 4.8984 | 4.8984 | 94.8984 | 94.8984 | 3.9347 | 96.8% | 96.7% | 97.08% | 97.17% | 97.49% | 97.45% | 97.35% | 97.31% | 96.85% | 96.5% | 97.05% | 96.99% | 97.15% | 97.52% | 97.46% | 97.02% | 96.93% | 96.05% | 94.07% | 91.61% | 88.92% | 84.07% | 74.52% | 65.61% | 86.3% | 84.97% | 83.31% | 82.09% | 80.13% | 79.09% | 97.52% | 13 | +130s | 120 | 60% | 0.19272 | 0.80728 | 4.8984 | 0.30865 | 0.69135 | 0.69135 |  | 75.55%
303 | 0:50 | 94.0374 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.7581 | 4.9395 | 4.9395 | 94.9395 | 94.9395 | 4.0374 | 96.46% | 96.88% | 96.98% | 97.32% | 97.28% | 97.15% | 97.11% | 96.61% | 96.24% | 96.84% | 96.75% | 96.94% | 97.36% | 97.32% | 96.94% | 96.9% | 96.16% | 94.33% | 91.98% | 89.39% | 84.71% | 75.34% | 66.55% | 86.95% | 85.63% | 83.97% | 82.74% | 80.78% | 79.74% | 0% | 97.36% | 12 | +120s | 110 | 63.33% | 0.18042 | 0.81958 | 4.9395 | 0.28894 | 0.71106 | 0.71106 |  | 77.27%
304 | 0:50 | 93.8952 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.8805 | 4.9701 | 4.9701 | 94.9701 | 94.9701 | 3.8952 | 96.64% | 96.75% | 97.13% | 97.07% | 96.92% | 96.88% | 96.33% | 95.94% | 96.58% | 96.47% | 96.7% | 97.17% | 97.15% | 96.83% | 96.84% | 96.25% | 94.58% | 92.36% | 89.89% | 85.39% | 76.21% | 67.54% | 87.64% | 86.31% | 84.66% | 83.43% | 81.47% | 80.43% | 0% | 0% | 97.17% | 11 | +110s | 100 | 66.67% | 0.21499 | 0.78501 | 4.9701 | 0.34431 | 0.65569 | 0.65569 |  | 76.47%
305 | 0:51 | 94.22 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.9602 | 4.9901 | 4.9901 | 94.9901 | 94.9901 | 4.22 | 96.47% | 96.89% | 96.82% | 96.65% | 96.6% | 96% | 95.58% | 96.28% | 96.14% | 96.4% | 96.94% | 96.93% | 96.68% | 96.76% | 96.32% | 94.83% | 92.74% | 90.41% | 86.09% | 77.12% | 68.61% | 88.36% | 87.04% | 85.38% | 84.16% | 82.19% | 81.15% | 0% | 0% | 0% | 96.94% | 10 | +100s | 90 | 70% | 0.154 | 0.846 | 4.9901 | 0.24664 | 0.75336 | 0.75336 |  | 80.76%
306 | 0:51 | 94.189 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.9972 | 4.9993 | 4.9993 | 94.9993 | 94.9993 | 4.189 | 96.59% | 96.51% | 96.31% | 96.26% | 95.61% | 95.16% | 95.91% | 95.75% | 96.05% | 96.65% | 96.66% | 96.49% | 96.63% | 96.37% | 95.08% | 93.13% | 90.94% | 86.84% | 78.11% | 69.75% | 89.12% | 87.79% | 86.13% | 84.91% | 82.95% | 81.91% | 0% | 0% | 0% | 0% | 96.66% | 10 | +100s | 90 | 70% | 0.16205 | 0.83795 | 4.9993 | 0.25953 | 0.74047 | 0.74047 |  | 80.24%
307 | 0:51 | 94.1339 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.9913 | 4.9978 | 4.9978 | 94.9978 | 94.9978 | 4.1339 | 96.13% | 95.9% | 95.85% | 95.14% | 94.66% | 95.47% | 95.28% | 95.62% | 96.29% | 96.33% | 96.24% | 96.45% | 96.39% | 95.31% | 93.53% | 91.49% | 87.63% | 79.16% | 70.98% | 89.9% | 88.58% | 86.92% | 85.7% | 83.73% | 82.7% | 0% | 0% | 0% | 0% | 0% | 96.45% | 11 | +110s | 100 | 66.67% | 0.17278 | 0.82722 | 4.9978 | 0.27671 | 0.72329 | 0.72329 |  | 78.48%
308 | 0:51 | 94.4887 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.9426 | 4.9856 | 4.9856 | 94.9856 | 94.9856 | 4.4887 | 95.4% | 95.35% | 94.56% | 94.06% | 94.94% | 94.71% | 95.1% | 95.85% | 95.91% | 95.91% | 96.2% | 96.36% | 95.51% | 93.92% | 92.07% | 88.47% | 80.29% | 72.32% | 90.72% | 89.39% | 87.73% | 86.51% | 84.55% | 83.51% | 0% | 0% | 0% | 0% | 0% | 0% | 96.36% | 11 | +110s | 100 | 66.67% | 0.099383 | 0.90062 | 4.9856 | 0.15916 | 0.84084 | 0.84084 |  | 82.37%
309 | 0:51 | 94.8939 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.8511 | 4.9628 | 4.9628 | 94.9628 | 94.9628 | 4.8939 | 94.72% | 93.86% | 93.32% | 94.27% | 94.01% | 94.45% | 95.29% | 95.38% | 95.49% | 95.87% | 96.27% | 95.69% | 94.3% | 92.65% | 89.35% | 81.51% | 73.77% | 91.56% | 90.24% | 88.58% | 87.35% | 85.39% | 84.35% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 96.27% | 10 | +100s | 90 | 70% | 0.013783 | 0.98622 | 4.9628 | 0.022074 | 0.97793 | 0.97793 |  | 88.02%
310 | 0:51 | 95.2613 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.7171 | 4.9293 | 4.9293 | 94.9293 | 94.9293 | 5.2613 | 92.98% | 92.4% | 93.44% | 93.14% | 93.63% | 94.57% | 94.7% | 94.92% | 95.41% | 96.08% | 95.81% | 94.66% | 93.24% | 90.29% | 82.84% | 75.37% | 92.43% | 91.1% | 89.44% | 88.22% | 86.26% | 85.22% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 96.08% | 9 | +90s | 80 | 73.33% | 0.066412 | 0.93359 | 4.9293 | 0.10636 | 0.89364 | 0.89364 |  | 86.26%
311 | 0:52 | 95.674 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.5409 | 4.8852 | 4.8852 | 94.8852 | 94.8852 | 5.674 | 91.25% | 92.39% | 92.04% | 92.6% | 93.65% | 93.82% | 94.18% | 94.78% | 95.77% | 95.85% | 94.97% | 93.82% | 91.26% | 84.27% | 77.13% | 93.32% | 92% | 90.34% | 89.11% | 87.15% | 86.11% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 95.85% | 9 | +90s | 80 | 73.33% | 0.15776 | 0.84224 | 4.8852 | 0.25265 | 0.74735 | 0.74735 |  | 81.31%
312 | 0:52 | 95.1366 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.3227 | 4.8307 | 4.8307 | 94.8307 | 94.8307 | 5.1366 | 91.03% | 90.63% | 91.26% | 92.45% | 92.67% | 93.18% | 93.91% | 95.27% | 95.76% | 95.21% | 94.37% | 92.28% | 85.83% | 79.07% | 94.23% | 92.91% | 91.25% | 90.03% | 88.06% | 87.03% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 95.76% | 8 | +80s | 70 | 76.67% | 0.061174 | 0.93883 | 4.8307 | 0.097971 | 0.90203 | 0.90203 |  | 87.54%
313 | 0:52 | 95.3013 | 90 | 3 | 0.5 | 90 | 5 | 20 | 19.0632 | 4.7658 | 4.7658 | 94.7658 | 94.7658 | 5.3013 | 88.79% | 89.51% | 90.85% | 91.12% | 91.81% | 92.71% | 94.49% | 95.47% | 95.29% | 94.82% | 93.29% | 87.49% | 81.2% | 95.16% | 93.84% | 92.18% | 90.96% | 89% | 87.96% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 95.47% | 7 | +70s | 60 | 80% | 0.1071 | 0.8929 | 4.7658 | 0.17152 | 0.82848 | 0.82848 |  | 86.11%
314 | 0:52 | 95.1833 | 90 | 3 | 0.5 | 90 | 5 | 20 | 18.7628 | 4.6907 | 4.6907 | 94.6907 | 94.6907 | 5.1833 | 87.15% | 88.67% | 89.01% | 89.92% | 91% | 93.3% | 94.85% | 95.13% | 95.11% | 94.24% | 89.24% | 83.53% | 96.12% | 94.79% | 93.13% | 91.91% | 89.95% | 88.91% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 96.12% | 12 | +120s | 110 | 63.33% | 0.098509 | 0.90149 | 4.6907 | 0.15776 | 0.84224 | 0.84224 |  | 81.22%
315 | 0:52 | 95.2332 | 90 | 3 | 0.5 | 90 | 5 | 20 | 18.4222 | 4.6056 | 4.6056 | 94.6056 | 94.6056 | 5.2332 | 85.66% | 86.07% | 87.24% | 88.55% | 91.46% | 93.7% | 94.53% | 95.06% | 95.01% | 91.01% | 86.02% | 97.08% | 95.76% | 94.1% | 92.88% | 90.91% | 89.88% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 97.08% | 11 | +110s | 100 | 66.67% | 0.12552 | 0.87448 | 4.6056 | 0.20102 | 0.79898 | 0.79898 |  | 81.22%
316 | 0:52 | 95.173 | 90 | 3 | 0.5 | 90 | 5 | 20 | 18.0422 | 4.5105 | 4.5105 | 94.5105 | 94.5105 | 5.173 | 81.9% | 83.38% | 84.96% | 88.61% | 91.7% | 93.21% | 94.4% | 95.37% | 92.62% | 88.57% | 98.06% | 96.74% | 95.08% | 93.86% | 91.89% | 90.86% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 98.06% | 10 | +100s | 90 | 70% | 0.13249 | 0.86751 | 4.5105 | 0.21218 | 0.78782 | 0.78782 |  | 82.28%
317 | 0:53 | 94.7554 | 90 | 3 | 0.5 | 90 | 5 | 20 | 17.6234 | 4.4059 | 4.4059 | 94.4059 | 94.4059 | 4.7554 | 90.38% | 90.85% | 91.59% | 92.58% | 93.71% | 94.72% | 95.91% | 97.81% | 99.33% | 99.05% | 97.73% | 96.07% | 94.85% | 92.89% | 91.85% | 90.23% | 88.83% | 87.63% | 86.42% | 84.88% | 83.58% | 82.02% | 80.69% | 80.05% | 79.73% | 79.84% | 79.52% | 79.45% | 79.06% | 78.99% | 99.33% | 8 | +80s | 70 | 76.67% | 0.069907 | 0.93009 | 4.4059 | 0.11196 | 0.88804 | 0.88804 |  | 88.27%
318 | 0:53 | 95.1647 | 90 | 3 | 0.5 | 90 | 5 | 20 | 17.1669 | 4.2917 | 4.2917 | 94.2917 | 94.2917 | 5.1647 | 89.85% | 90.59% | 91.57% | 92.71% | 93.72% | 94.91% | 96.81% | 98.33% | 99.94% | 98.73% | 97.07% | 95.85% | 93.89% | 92.85% | 91.23% | 89.83% | 88.63% | 87.42% | 85.88% | 84.58% | 83.03% | 81.7% | 81.05% | 80.73% | 80.84% | 80.52% | 80.45% | 80.06% | 79.99% | 79.76% | 99.94% | 8 | +80s | 70 | 76.67% | 0.1746 | 0.8254 | 4.2917 | 0.27963 | 0.72037 | 0.72037 |  | 82.88%
319 | 0:53 | 94.4802 | 90 | 3 | 0.5 | 90 | 5 | 20 | 16.6736 | 4.1684 | 4.1684 | 94.1684 | 94.1684 | 4.4802 | 89.58% | 90.57% | 91.7% | 92.71% | 93.9% | 95.8% | 97.32% | 98.94% | 99.74% | 98.08% | 96.86% | 94.9% | 93.86% | 92.24% | 90.84% | 89.64% | 88.43% | 86.89% | 85.59% | 84.03% | 82.7% | 82.06% | 81.74% | 81.85% | 81.53% | 81.46% | 81.07% | 81% | 80.77% | 80.84% | 99.74% | 8 | +80s | 70 | 76.67% | 0.062362 | 0.93764 | 4.1684 | 0.099874 | 0.90013 | 0.90013 |  | 88.81%
320 | 0:53 | 94.2523 | 90 | 3 | 0.5 | 90 | 5 | 20 | 16.1446 | 4.0362 | 4.0362 | 94.0362 | 94.0362 | 4.2523 | 89.55% | 90.69% | 91.7% | 92.89% | 94.79% | 96.31% | 97.92% | 99.25% | 99.1% | 97.87% | 95.91% | 94.87% | 93.25% | 91.85% | 90.66% | 89.44% | 87.9% | 86.6% | 85.05% | 83.72% | 83.07% | 82.75% | 82.86% | 82.55% | 82.47% | 82.08% | 82.02% | 81.78% | 81.85% | 81.96% | 99.25% | 7 | +70s | 60 | 80% | 0.043228 | 0.95677 | 4.0362 | 0.069231 | 0.93077 | 0.93077 |  | 90.77%
321 | 0:53 | 94.3633 | 90 | 3 | 0.5 | 90 | 5 | 20 | 15.581 | 3.8952 | 3.8952 | 93.8952 | 93.8952 | 4.3633 | 89.67% | 90.68% | 91.87% | 93.77% | 95.29% | 96.91% | 98.23% | 99.89% | 98.89% | 96.93% | 95.89% | 94.27% | 92.87% | 91.67% | 90.46% | 88.92% | 87.62% | 86.06% | 84.73% | 84.09% | 83.77% | 83.88% | 83.56% | 83.49% | 83.1% | 83.03% | 82.8% | 82.87% | 82.98% | 82.96% | 99.89% | 7 | +70s | 60 | 80% | 0.093603 | 0.9064 | 3.8952 | 0.14991 | 0.85009 | 0.85009 |  | 88.3%
322 | 0:53 | 94.4424 | 90 | 3 | 0.5 | 90 | 5 | 20 | 14.984 | 3.746 | 3.746 | 93.746 | 93.746 | 4.4424 | 89.67% | 90.85% | 92.75% | 94.27% | 95.89% | 97.21% | 98.87% | 99.91% | 97.94% | 96.91% | 95.29% | 93.88% | 92.69% | 91.47% | 89.94% | 88.64% | 87.08% | 85.75% | 85.1% | 84.79% | 84.9% | 84.58% | 84.51% | 84.12% | 84.05% | 83.81% | 83.89% | 84% | 83.97% | 83.76% | 99.91% | 7 | +70s | 60 | 80% | 0.13928 | 0.86072 | 3.746 | 0.22306 | 0.77694 | 0.77694 |  | 85.87%
323 | 0:54 | 94.0017 | 90 | 3 | 0.5 | 90 | 5 | 20 | 14.3549 | 3.5887 | 3.5887 | 93.5887 | 93.5887 | 4.0017 | 89.84% | 91.74% | 93.26% | 94.87% | 96.19% | 97.85% | 99.08% | 98.96% | 97.92% | 96.3% | 94.9% | 93.71% | 92.49% | 90.95% | 89.65% | 88.1% | 86.77% | 86.12% | 85.8% | 85.91% | 85.6% | 85.53% | 85.13% | 85.07% | 84.83% | 84.9% | 85.01% | 84.99% | 84.77% | 84.88% | 99.08% | 6 | +60s | 50 | 83.33% | 0.082598 | 0.9174 | 3.5887 | 0.13228 | 0.86772 | 0.86772 |  | 89.73%
324 | 0:54 | 93.4757 | 90 | 3 | 0.5 | 90 | 5 | 20 | 13.695 | 3.4237 | 3.4237 | 93.4237 | 93.4237 | 3.4757 | 90.72% | 92.24% | 93.86% | 95.18% | 96.84% | 98.06% | 99.97% | 98.93% | 97.32% | 95.91% | 94.72% | 93.5% | 91.96% | 90.67% | 89.11% | 87.78% | 87.13% | 86.82% | 86.93% | 86.61% | 86.54% | 86.14% | 86.08% | 85.84% | 85.92% | 86.03% | 86% | 85.78% | 85.89% | 86.19% | 99.97% | 6 | +60s | 50 | 83.33% | 0.010394 | 0.98961 | 3.4237 | 0.016646 | 0.98335 | 0.98335 |  | 93.88%
325 | 0:54 | 93.896 | 90 | 3 | 0.5 | 90 | 5 | 20 | 13.0058 | 3.2514 | 3.2514 | 93.2514 | 93.2514 | 3.896 | 91.24% | 92.85% | 94.18% | 95.83% | 97.06% | 99.02% | 99.94% | 98.32% | 96.92% | 95.73% | 94.51% | 92.97% | 91.67% | 90.12% | 88.79% | 88.14% | 87.82% | 87.93% | 87.62% | 87.54% | 87.15% | 87.09% | 86.85% | 86.92% | 87.03% | 87.01% | 86.79% | 86.9% | 87.2% | 86.84% | 99.94% | 6 | +60s | 50 | 83.33% | 0.12892 | 0.87108 | 3.2514 | 0.20647 | 0.79353 | 0.79353 |  | 87.54%
326 | 0:54 | 93.1255 | 90 | 3 | 0.5 | 90 | 5 | 20 | 12.2887 | 3.0722 | 3.0722 | 93.0722 | 93.0722 | 3.1255 | 91.85% | 93.18% | 94.84% | 96.06% | 98.02% | 99.06% | 99.32% | 97.92% | 96.73% | 95.51% | 93.97% | 92.67% | 91.12% | 89.79% | 89.14% | 88.82% | 88.93% | 88.61% | 88.54% | 88.15% | 88.09% | 87.85% | 87.92% | 88.03% | 88.01% | 87.79% | 87.9% | 88.19% | 87.84% | 87.83% | 99.32% | 6 | +60s | 50 | 83.33% | 0.010666 | 0.98933 | 3.0722 | 0.017081 | 0.98292 | 0.98292 |  | 93.65%
327 | 0:54 | 93.6522 | 90 | 3 | 0.5 | 90 | 5 | 20 | 11.5452 | 2.8863 | 2.8863 | 92.8863 | 92.8863 | 3.6522 | 92.19% | 93.85% | 95.07% | 97.03% | 98.07% | 89.01% | 92.57% | 93.77% | 93.47% | 93.63% | 92.38% | 91.08% | 89.54% | 86.91% | 84.78% | 83.52% | 82.02% | 80.86% | 81.07% | 80.89% | 81.83% | 80.05% | 81.37% | 80.47% | 79.98% | 79.44% | 79.57% | 80.89% | 78.84% | 80.53% | 98.07% | 4 | +40s | 30 | 90% | 0.15317 | 0.84683 | 2.8863 | 0.2453 | 0.7547 | 0.7547 |  | 87.85%
328 | 0:54 | 93.4241 | 90 | 3 | 0.5 | 90 | 5 | 20 | 10.7771 | 2.6943 | 2.6943 | 92.6943 | 92.6943 | 3.4241 | 92.87% | 94.09% | 96.06% | 97.09% | 86.75% | 91.18% | 93.24% | 93.96% | 94.69% | 94.16% | 93.51% | 92.43% | 90.26% | 88.44% | 87.32% | 86.03% | 85.01% | 85.19% | 85.03% | 85.85% | 84.27% | 85.45% | 84.65% | 84.22% | 83.74% | 83.85% | 85% | 83.18% | 84.65% | 84.57% | 97.09% | 3 | +30s | 20 | 93.33% | 0.14596 | 0.85404 | 2.6943 | 0.23376 | 0.76624 | 0.76624 |  | 89.02%
329 | 0:55 | 93.2777 | 90 | 3 | 0.5 | 90 | 5 | 20 | 9.9858 | 2.4964 | 2.4964 | 92.4964 | 92.4964 | 3.2777 | 93.13% | 95.09% | 96.13% | 84.52% | 89.64% | 92.39% | 93.92% | 95.13% | 95.19% | 95.06% | 94.36% | 92.57% | 91% | 90.01% | 88.89% | 87.99% | 88.15% | 88% | 88.72% | 87.31% | 88.37% | 87.66% | 87.28% | 86.85% | 86.95% | 87.94% | 86.33% | 87.62% | 87.55% | 88.64% | 96.13% | 2 | +20s | 10 | 96.67% | 0.15625 | 0.84375 | 2.4964 | 0.25024 | 0.74976 | 0.74976 |  | 89.26%
330 | 0:55 | 92.5919 | 90 | 3 | 0.5 | 90 | 5 | 20 | 9.1731 | 2.2933 | 2.2933 | 92.2933 | 92.2933 | 2.5919 | 94.15% | 95.19% | 82.43% | 88.09% | 91.4% | 93.61% | 95.2% | 95.74% | 96.05% | 95.67% | 94.2% | 92.84% | 91.95% | 90.98% | 90.18% | 90.32% | 90.19% | 90.82% | 89.56% | 90.51% | 89.88% | 89.54% | 89.15% | 89.24% | 90.11% | 88.66% | 89.8% | 89.75% | 90.71% | 90.27% | 96.05% | 8 | +80s | 70 | 76.67% | 0.059721 | 0.94028 | 2.2933 | 0.095644 | 0.90436 | 0.90436 |  | 87.72%
331 | 0:55 | 93.0377 | 90 | 3 | 0.5 | 90 | 5 | 20 | 8.3408 | 2.0852 | 2.0852 | 92.0852 | 92.0852 | 3.0377 | 94.26% | 80.49% | 86.61% | 90.38% | 93.15% | 95.05% | 96% | 96.67% | 96.56% | 95.36% | 94.19% | 93.39% | 92.54% | 91.82% | 91.94% | 91.83% | 92.39% | 91.24% | 92.11% | 91.54% | 91.24% | 90.89% | 90.98% | 91.73% | 90.43% | 91.43% | 91.39% | 92.26% | 91.85% | 91.51% | 96.67% | 7 | +70s | 60 | 80% | 0.19049 | 0.80951 | 2.0852 | 0.30508 | 0.69492 | 0.69492 |  | 82.05%
332 | 0:55 | 92.3897 | 90 | 3 | 0.5 | 90 | 5 | 20 | 7.4906 | 1.8726 | 1.8726 | 91.8726 | 91.8726 | 2.3897 | 78.73% | 85.22% | 89.38% | 92.61% | 94.78% | 96.08% | 97.06% | 97.17% | 96.21% | 95.19% | 94.46% | 93.73% | 93.08% | 93.19% | 93.08% | 93.58% | 92.54% | 93.33% | 92.82% | 92.55% | 92.23% | 92.31% | 92.97% | 91.79% | 92.69% | 92.65% | 93.43% | 93.05% | 92.74% | 92.59% | 97.17% | 7 | +70s | 60 | 80% | 0.10342 | 0.89658 | 1.8726 | 0.16563 | 0.83437 | 0.83437 |  | 86.87%
333 | 0:55 | 92.2245 | 90 | 3 | 0.5 | 90 | 5 | 20 | 6.6243 | 1.6561 | 1.6561 | 91.6561 | 91.6561 | 2.2245 | 83.92% | 88.41% | 92.05% | 94.44% | 96.03% | 97.28% | 97.58% | 96.83% | 95.94% | 95.29% | 94.64% | 94.06% | 94.15% | 94.06% | 94.5% | 93.56% | 94.28% | 93.82% | 93.58% | 93.28% | 93.35% | 93.93% | 92.86% | 93.66% | 93.64% | 94.34% | 93.99% | 93.7% | 93.57% | 93.47% | 97.58% | 6 | +60s | 50 | 83.33% | 0.11369 | 0.88631 | 1.6561 | 0.18208 | 0.81792 | 0.81792 |  | 87.57%
334 | 0:55 | 92.3448 | 90 | 3 | 0.5 | 90 | 5 | 20 | 5.7439 | 1.436 | 1.436 | 91.436 | 91.436 | 2.3448 | 87.49% | 91.47% | 94.07% | 95.91% | 97.39% | 97.86% | 97.28% | 96.52% | 95.92% | 95.36% | 94.84% | 94.92% | 94.83% | 95.23% | 94.36% | 95.02% | 94.61% | 94.39% | 94.12% | 94.19% | 94.69% | 93.72% | 94.43% | 94.41% | 95.05% | 94.73% | 94.45% | 94.34% | 94.24% | 93.71% | 97.86% | 5 | +50s | 40 | 86.67% | 0.18177 | 0.81823 | 1.436 | 0.2911 | 0.7089 | 0.7089 |  | 85.14%
335 | 0:56 | 92.344 | 90 | 3 | 0.5 | 90 | 5 | 20 | 4.8511 | 1.2128 | 1.2128 | 91.2128 | 91.2128 | 2.344 | 90.91% | 93.68% | 95.75% | 97.42% | 98.05% | 97.62% | 96.97% | 96.42% | 95.93% | 95.46% | 95.53% | 95.45% | 95.81% | 95.01% | 95.62% | 95.24% | 95.05% | 94.8% | 94.86% | 95.3% | 94.41% | 95.05% | 95.04% | 95.61% | 95.31% | 95.06% | 94.96% | 94.87% | 94.38% | 94.37% | 98.05% | 4 | +40s | 30 | 90% | 0.22624 | 0.77376 | 1.2128 | 0.36233 | 0.63767 | 0.63767 |  | 83.94%
336 | 0:56 | 91.3659 | 90 | 3 | 0.5 | 90 | 5 | 20 | 3.948 | 0.987 | 0.987 | 90.987 | 90.987 | 1.3659 | 93.28% | 95.55% | 97.4% | 98.16% | 97.88% | 97.31% | 96.81% | 96.39% | 95.97% | 96.02% | 95.96% | 96.27% | 95.54% | 96.1% | 95.76% | 95.59% | 95.36% | 95.41% | 95.79% | 94.98% | 95.55% | 95.55% | 96.07% | 95.79% | 95.55% | 95.46% | 95.38% | 94.92% | 94.92% | 95.12% | 98.16% | 3 | +30s | 20 | 93.33% | 0.075786 | 0.92421 | 0.987 | 0.12137 | 0.87863 | 0.87863 |  | 93.12%
337 | 0:56 | 91.6047 | 90 | 3 | 0.5 | 90 | 5 | 20 | 3.0364 | 0.75909 | 0.75909 | 90.7591 | 90.7591 | 1.6047 | 95.33% | 97.34% | 98.22% | 98.06% | 97.59% | 97.13% | 96.77% | 96.38% | 96.43% | 96.37% | 96.65% | 95.98% | 96.5% | 96.18% | 96.03% | 95.82% | 95.87% | 96.2% | 95.46% | 95.97% | 95.96% | 96.43% | 96.17% | 95.95% | 95.87% | 95.79% | 95.37% | 95.37% | 95.56% | 96.37% | 98.22% | 2 | +20s | 10 | 96.67% | 0.16911 | 0.83089 | 0.75909 | 0.27084 | 0.72916 | 0.72916 |  | 89.27%
338 | 0:56 | 91.0627 | 90 | 3 | 0.5 | 90 | 5 | 20 | 2.1182 | 0.52956 | 0.52956 | 90.5296 | 90.5296 | 1.0627 | 97.26% | 98.24% | 98.2% | 97.8% | 97.38% | 97.07% | 96.72% | 96.76% | 96.71% | 96.96% | 96.34% | 96.82% | 96.53% | 96.4% | 96.2% | 96.25% | 96.53% | 95.85% | 96.31% | 96.31% | 96.74% | 96.49% | 96.28% | 96.22% | 96.14% | 95.75% | 95.74% | 95.92% | 96.67% | 96.07% | 98.24% | 1 | +10s | 0 | 100% | 0.10663 | 0.89337 | 0.52956 | 0.17078 | 0.82922 | 0.82922 |  | 93.72%
339 | 0:56 | 90.855 | 90 | 3 | 0.5 | 90 | 5 | 20 | 1.1956 | 0.2989 | 0.2989 | 90.2989 | 90.2989 | 0.855 | 98.23% | 98.29% | 97.97% | 97.58% | 97.32% | 97.01% | 97.04% | 97% | 97.21% | 96.65% | 97.09% | 96.83% | 96.71% | 96.52% | 96.57% | 96.81% | 96.19% | 96.59% | 96.6% | 96.98% | 96.75% | 96.55% | 96.5% | 96.42% | 96.06% | 96.06% | 96.22% | 96.9% | 96.37% | 96.39% | 98.29% | 1 | +10s | 0 | 100% | 0.11122 | 0.88878 | 0.2989 | 0.17812 | 0.82188 | 0.82188 |  | 93.49%
340 | 0:56 | 91.3079 | 90 | 3 | 0.5 | 90 | 5 | 20 | 0.27037 | 0.067592 | 0.067592 | 90.0676 | 90.0676 | 1.3079 | 98.36% | 98.1% | 97.75% | 97.53% | 97.25% | 97.28% | 97.23% | 97.43% | 96.9% | 97.31% | 97.08% | 96.97% | 96.8% | 96.84% | 97.04% | 96.48% | 96.83% | 96.84% | 97.19% | 96.97% | 96.78% | 96.74% | 96.67% | 96.33% | 96.32% | 96.47% | 97.1% | 96.61% | 96.64% | 96.67% | 98.36% | 0 | No Time Shift | 0 | 100% | 0.24806 | 0.75194 | 0.067592 | 0.39727 | 0.60273 | 0.60273 |  | 86.21%
341 | 0:57 | 91.225 | 90 | 3 | 0.5 | 90 | 5 | 20 | -0.65543 | -0.16386 | -0.16386 | 89.8361 | 89.8361 | 1.225 | 98.2% | 97.88% | 97.71% | 97.45% | 97.47% | 97.44% | 97.6% | 97.12% | 97.5% | 97.29% | 97.19% | 97.04% | 97.07% | 97.24% | 96.72% | 97.03% | 97.04% | 97.36% | 97.16% | 96.98% | 96.94% | 96.87% | 96.56% | 96.55% | 96.69% | 97.26% | 96.82% | 96.85% | 96.88% | 96.21% | 98.2% | 0 | No Time Shift | 0 | 100% | 0.27778 | 0.72222 | 0.16386 | 0.44487 | 0.55513 | 0.55513 |  | 84.57%
342 | 0:57 | 91.2194 | 90 | 3 | 0.5 | 90 | 5 | 20 | -1.5798 | -0.39496 | -0.39496 | 89.605 | 89.605 | 1.2194 | 97.98% | 97.85% | 97.62% | 97.64% | 97.61% | 97.75% | 97.31% | 97.66% | 97.47% | 97.39% | 97.24% | 97.27% | 97.4% | 96.93% | 97.2% | 97.22% | 97.5% | 97.31% | 97.14% | 97.11% | 97.04% | 96.75% | 96.75% | 96.87% | 97.4% | 97% | 97.02% | 97.05% | 96.44% | 96.58% | 97.98% | 0 | No Time Shift | 0 | 100% | 0.32288 | 0.67712 | 0.39496 | 0.51709 | 0.48291 | 0.48291 |  | 82.09%
343 | 0:57 | 90.792 | 90 | 3 | 0.5 | 90 | 5 | 20 | -2.5008 | -0.62521 | -0.62521 | 89.3748 | 89.3748 | 0.79198 | 97.97% | 97.77% | 97.78% | 97.75% | 97.87% | 97.47% | 97.79% | 97.62% | 97.55% | 97.41% | 97.44% | 97.54% | 97.12% | 97.35% | 97.36% | 97.62% | 97.44% | 97.28% | 97.26% | 97.19% | 96.92% | 96.92% | 97.03% | 97.51% | 97.16% | 97.17% | 97.2% | 96.65% | 96.77% | 96.88% | 97.97% | 0 | No Time Shift | 0 | 100% | 0.28344 | 0.71656 | 0.62521 | 0.45393 | 0.54607 | 0.54607 |  | 84.19%
344 | 0:57 | 90.7318 | 90 | 3 | 0.5 | 90 | 5 | 20 | -3.4165 | -0.85412 | -0.85412 | 89.1459 | 89.1459 | 0.7318 | 97.89% | 97.9% | 97.87% | 97.97% | 97.61% | 97.9% | 97.75% | 97.69% | 97.56% | 97.59% | 97.66% | 97.28% | 97.47% | 97.49% | 97.71% | 97.55% | 97.39% | 97.38% | 97.32% | 97.07% | 97.06% | 97.17% | 97.6% | 97.29% | 97.3% | 97.32% | 96.83% | 96.93% | 97.03% | 97.06% | 97.97% | 3 | +30s | 20 | 93.33% | 0.31718 | 0.68282 | 0.85412 | 0.50798 | 0.49202 | 0.49202 |  | 80.17%
345 | 0:57 | 90.0201 | 90 | 3 | 0.5 | 90 | 5 | 20 | -4.3248 | -1.0812 | -1.0812 | 88.9188 | 88.9188 | 0.020143 | 98% | 97.98% | 98.06% | 97.72% | 98% | 97.86% | 97.81% | 97.7% | 97.72% | 97.76% | 97.42% | 97.57% | 97.6% | 97.79% | 97.64% | 97.49% | 97.49% | 97.43% | 97.2% | 97.19% | 97.29% | 97.67% | 97.4% | 97.41% | 97.43% | 96.99% | 97.07% | 97.16% | 97.19% | 97.06% | 98.06% | 2 | +20s | 10 | 96.67% | 0.22027 | 0.77973 | 1.0812 | 0.35277 | 0.64723 | 0.64723 |  | 86.48%
346 | 0:57 | 90.1669 | 90 | 3 | 0.5 | 90 | 5 | 20 | -5.2239 | -1.306 | -1.306 | 88.694 | 88.694 | 0.16687 | 98.07% | 98.13% | 97.83% | 98.08% | 97.96% | 97.92% | 97.81% | 97.83% | 97.84% | 97.54% | 97.66% | 97.69% | 97.86% | 97.71% | 97.57% | 97.57% | 97.52% | 97.3% | 97.3% | 97.39% | 97.73% | 97.49% | 97.51% | 97.52% | 97.13% | 97.19% | 97.27% | 97.3% | 97.18% | 97.41% | 98.13% | 1 | +10s | 0 | 100% | 0.29457 | 0.70543 | 1.306 | 0.47176 | 0.52824 | 0.52824 |  | 83.65%
347 | 0:58 | 89.6089 | 90 | 3 | 0.5 | 90 | 5 | 20 | -6.1117 | -1.5279 | -1.5279 | 88.4721 | 88.4721 | -0.39107 | 98.18% | 97.91% | 98.14% | 98.04% | 98.01% | 97.91% | 97.93% | 97.91% | 97.64% | 97.74% | 97.76% | 97.91% | 97.77% | 97.64% | 97.65% | 97.59% | 97.4% | 97.39% | 97.47% | 97.78% | 97.58% | 97.59% | 97.59% | 97.25% | 97.3% | 97.37% | 97.39% | 97.28% | 97.48% | 97.26% | 98.18% | 0 | No Time Shift | 0 | 100% | 0.22737 | 0.77263 | 1.5279 | 0.36414 | 0.63586 | 0.63586 |  | 87.26%
348 | 0:58 | 90.1977 | 90 | 3 | 0.5 | 90 | 5 | 20 | -6.9865 | -1.7466 | -1.7466 | 88.2534 | 88.2534 | 0.19767 | 97.99% | 98.19% | 98.1% | 98.08% | 97.99% | 98.02% | 97.97% | 97.74% | 97.8% | 97.83% | 97.95% | 97.82% | 97.7% | 97.71% | 97.66% | 97.48% | 97.47% | 97.54% | 97.81% | 97.64% | 97.65% | 97.66% | 97.36% | 97.4% | 97.45% | 97.47% | 97.37% | 97.54% | 97.34% | 97.38% | 98.19% | 1 | +10s | 0 | 100% | 0.38886 | 0.61114 | 1.7466 | 0.62276 | 0.37724 | 0.37724 |  | 78.64%
349 | 0:58 | 89.5138 | 90 | 3 | 0.5 | 90 | 5 | 20 | -7.8463 | -1.9616 | -1.9616 | 88.0384 | 88.0384 | -0.48618 | 98.23% | 98.16% | 98.15% | 98.07% | 98.09% | 98.02% | 97.82% | 97.85% | 97.88% | 97.98% | 97.86% | 97.75% | 97.76% | 97.71% | 97.55% | 97.54% | 97.61% | 97.84% | 97.7% | 97.71% | 97.71% | 97.46% | 97.48% | 97.53% | 97.54% | 97.44% | 97.59% | 97.42% | 97.44% | 97.26% | 98.23% | 0 | No Time Shift | 0 | 100% | 0.29508 | 0.70492 | 1.9616 | 0.47257 | 0.52743 | 0.52743 |  | 83.66%
350 | 0:58 | 89.6494 | 90 | 3 | 0.5 | 90 | 5 | 20 | -8.6893 | -2.1723 | -2.1723 | 87.8277 | 87.8277 | -0.35056 | 98.21% | 98.21% | 98.13% | 98.15% | 98.06% | 97.89% | 97.89% | 97.92% | 98% | 97.89% | 97.78% | 97.8% | 97.75% | 97.61% | 97.6% | 97.66% | 97.85% | 97.75% | 97.76% | 97.75% | 97.55% | 97.55% | 97.59% | 97.6% | 97.51% | 97.63% | 97.48% | 97.48% | 97.34% | 97.52% | 98.21% | 0 | No Time Shift | 0 | 100% | 0.36435 | 0.63565 | 2.1723 | 0.58352 | 0.41648 | 0.41648 |  | 79.95%
351 | 0:58 | 89.2469 | 90 | 3 | 0.5 | 90 | 5 | 20 | -9.5137 | -2.3784 | -2.3784 | 87.6216 | 87.6216 | -0.75306 | 98.25% | 98.19% | 98.2% | 98.08% | 97.95% | 97.92% | 97.96% | 98.01% | 97.91% | 97.81% | 97.84% | 97.79% | 97.66% | 97.65% | 97.7% | 97.86% | 97.79% | 97.79% | 97.79% | 97.62% | 97.61% | 97.64% | 97.65% | 97.56% | 97.66% | 97.53% | 97.51% | 97.4% | 97.56% | 97.53% | 98.25% | 0 | No Time Shift | 0 | 100% | 0.32507 | 0.67493 | 2.3784 | 0.52061 | 0.47939 | 0.47939 |  | 82.06%
352 | 0:58 | 89.331 | 90 | 3 | 0.5 | 90 | 5 | 20 | -10.3176 | -2.5794 | -2.5794 | 87.4206 | 87.4206 | -0.66896 | 98.23% | 98.24% | 98.1% | 98% | 97.95% | 97.98% | 98.02% | 97.92% | 97.83% | 97.86% | 97.81% | 97.7% | 97.69% | 97.73% | 97.86% | 97.82% | 97.82% | 97.81% | 97.69% | 97.67% | 97.69% | 97.7% | 97.61% | 97.68% | 97.58% | 97.54% | 97.45% | 97.59% | 97.55% | 97.54% | 98.24% | 1 | +10s | 0 | 100% | 0.38209 | 0.61791 | 2.5794 | 0.61192 | 0.38808 | 0.38808 |  | 79.02%
353 | 0:59 | 89.2302 | 90 | 3 | 0.5 | 90 | 5 | 20 | -11.0995 | -2.7749 | -2.7749 | 87.2251 | 87.2251 | -0.76976 | 98.28% | 98.11% | 98.04% | 97.96% | 98% | 98.01% | 97.93% | 97.84% | 97.88% | 97.83% | 97.73% | 97.73% | 97.76% | 97.85% | 97.84% | 97.84% | 97.83% | 97.75% | 97.71% | 97.72% | 97.73% | 97.65% | 97.7% | 97.61% | 97.55% | 97.5% | 97.62% | 97.56% | 97.55% | 97.57% | 98.28% | 0 | No Time Shift | 0 | 100% | 0.40102 | 0.59898 | 2.7749 | 0.64225 | 0.35775 | 0.35775 |  | 78.02%
354 | 0:59 | 88.2787 | 90 | 3 | 0.5 | 90 | 5 | 20 | -11.8576 | -2.9644 | -2.9644 | 87.0356 | 87.0356 | -1.7213 | 98.12% | 98.08% | 97.97% | 98.01% | 98% | 97.92% | 97.84% | 97.88% | 97.84% | 97.76% | 97.75% | 97.78% | 97.83% | 97.85% | 97.85% | 97.84% | 97.8% | 97.75% | 97.75% | 97.76% | 97.68% | 97.7% | 97.64% | 97.56% | 97.54% | 97.64% | 97.57% | 97.56% | 97.57% | 97.14% | 98.12% | 0 | No Time Shift | 0 | 100% | 0.24862 | 0.75138 | 2.9644 | 0.39816 | 0.60184 | 0.60184 |  | 86.1%
355 | 0:59 | 89.0242 | 90 | 3 | 0.5 | 90 | 5 | 20 | -12.5902 | -3.1476 | -3.1476 | 86.8524 | 86.8524 | -0.97583 | 98.11% | 97.97% | 98.01% | 97.98% | 97.91% | 97.84% | 97.89% | 97.84% | 97.78% | 97.77% | 97.79% | 97.81% | 97.86% | 97.86% | 97.84% | 97.84% | 97.78% | 97.77% | 97.77% | 97.7% | 97.7% | 97.66% | 97.57% | 97.57% | 97.65% | 97.57% | 97.56% | 97.56% | 97.16% | 96.86% | 98.11% | 0 | No Time Shift | 0 | 100% | 0.43435 | 0.56565 | 3.1476 | 0.69561 | 0.30439 | 0.30439 |  | 76.18%
356 | 0:59 | 87.9673 | 90 | 3 | 0.5 | 90 | 5 | 20 | -13.2959 | -3.324 | -3.324 | 86.676 | 86.676 | -2.0327 | 97.96% | 98.01% | 97.95% | 97.89% | 97.82% | 97.88% | 97.84% | 97.79% | 97.78% | 97.79% | 97.78% | 97.86% | 97.86% | 97.84% | 97.88% | 97.8% | 97.79% | 97.78% | 97.72% | 97.69% | 97.68% | 97.56% | 97.59% | 97.66% | 97.56% | 97.55% | 97.55% | 97.16% | 96.88% | 96.09% | 98.01% | 1 | +10s | 0 | 100% | 0.25827 | 0.74173 | 3.324 | 0.41362 | 0.58638 | 0.58638 |  | 85.55%
357 | 0:59 | 87.8091 | 90 | 3 | 0.5 | 90 | 5 | 20 | -13.9731 | -3.4933 | -3.4933 | 86.5067 | 86.5067 | -2.1909 | 98% | 97.92% | 97.87% | 97.8% | 97.86% | 97.83% | 97.79% | 97.78% | 97.78% | 97.74% | 97.85% | 97.85% | 97.83% | 97.91% | 97.82% | 97.79% | 97.79% | 97.73% | 97.67% | 97.68% | 97.55% | 97.6% | 97.65% | 97.55% | 97.53% | 97.53% | 97.16% | 96.89% | 96.16% | 95.68% | 98% | 0 | No Time Shift | 0 | 100% | 0.26047 | 0.73953 | 3.4933 | 0.41715 | 0.58285 | 0.58285 |  | 85.43%
358 | 0:59 | 87.6312 | 90 | 3 | 0.5 | 90 | 5 | 20 | -14.6204 | -3.6551 | -3.6551 | 86.3449 | 86.3449 | -2.3688 | 97.88% | 97.83% | 97.78% | 97.84% | 97.81% | 97.78% | 97.78% | 97.77% | 97.69% | 97.83% | 97.83% | 97.81% | 97.93% | 97.82% | 97.79% | 97.78% | 97.73% | 97.65% | 97.68% | 97.53% | 97.61% | 97.64% | 97.52% | 97.51% | 97.5% | 97.16% | 96.89% | 96.22% | 95.75% | 93.62% | 97.93% | 12 | +120s | 110 | 63.33% | 0.25725 | 0.74275 | 3.6551 | 0.41199 | 0.58801 | 0.58801 |  | 73.35%
359 | 1:00 | 88.2197 | 90 | 3 | 0.5 | 90 | 5 | 20 | -15.2363 | -3.8091 | -3.8091 | 86.1909 | 86.1909 | -1.7803 | 97.79% | 97.74% | 97.81% | 97.78% | 97.77% | 97.76% | 97.75% | 97.64% | 97.81% | 97.8% | 97.78% | 97.94% | 97.82% | 97.78% | 97.77% | 97.72% | 97.62% | 97.67% | 97.5% | 97.61% | 97.62% | 97.49% | 97.48% | 97.46% | 97.14% | 96.89% | 96.28% | 95.82% | 93.77% | 90% | 97.94% | 11 | +110s | 100 | 66.67% | 0.40575 | 0.59425 | 3.8091 | 0.64982 | 0.35018 | 0.35018 |  | 66.54%
360 | 1:00 | 88.1324 | 90 | 3 | 0.5 | 90 | 5 | 20 | -15.8196 | -3.9549 | -3.9549 | 86.0451 | 86.0451 | -1.8676 | 97.7% | 97.78% | 97.74% | 97.75% | 97.74% | 97.72% | 97.58% | 97.77% | 97.77% | 97.74% | 97.94% | 97.81% | 97.77% | 97.75% | 97.71% | 97.58% | 97.66% | 97.46% | 97.6% | 97.6% | 97.45% | 97.44% | 97.42% | 97.12% | 96.87% | 96.33% | 95.88% | 93.91% | 90.25% | 85.29% | 97.94% | 10 | +100s | 90 | 70% | 0.41746 | 0.58254 | 3.9549 | 0.66857 | 0.33143 | 0.33143 |  | 67.03%
361 | 1:00 | 87.429 | 90 | 3 | 0.5 | 90 | 5 | 20 | -16.3689 | -4.0922 | -4.0922 | 85.9078 | 85.9078 | -2.571 | 97.73% | 97.7% | 97.72% | 97.71% | 97.69% | 97.5% | 97.73% | 97.73% | 97.7% | 97.94% | 97.8% | 97.74% | 97.72% | 97.69% | 97.53% | 97.63% | 97.42% | 97.59% | 97.56% | 97.4% | 97.39% | 97.37% | 97.08% | 96.85% | 96.37% | 95.93% | 94.05% | 90.5% | 85.66% | 81.53% | 97.94% | 9 | +90s | 80 | 73.33% | 0.30425 | 0.69575 | 4.0922 | 0.48726 | 0.51274 | 0.51274 |  | 74.18%
362 | 1:00 | 87.8298 | 90 | 3 | 0.5 | 90 | 5 | 20 | -16.8832 | -4.2208 | -4.2208 | 85.7792 | 85.7792 | -2.1702 | 97.64% | 97.68% | 97.68% | 97.64% | 97.42% | 97.68% | 97.67% | 97.64% | 97.93% | 97.77% | 97.7% | 97.68% | 97.65% | 97.47% | 97.6% | 97.36% | 97.56% | 97.51% | 97.34% | 97.33% | 97.3% | 97.04% | 96.82% | 96.4% | 95.98% | 94.19% | 90.75% | 86.02% | 81.96% | 73.98%
363 | 1:00 | 87.5934 | 90 | 3 | 0.5 | 90 | 5 | 20 | -17.3613 | -4.3403 | -4.3403 | 85.6597 | 85.6597 | -2.4066 | 97.63% | 97.63% | 97.58% | 97.33% | 97.62% | 97.61% | 97.57% | 97.91% | 97.74% | 97.66% | 97.64% | 97.61% | 97.4% | 97.55% | 97.3% | 97.53% | 97.46% | 97.27% | 97.26% | 97.23% | 96.99% | 96.78% | 96.43% | 96.02% | 94.32% | 90.99% | 86.4% | 82.39% | 74.51% | 71.17%
364 | 1:00 | 87.0697 | 90 | 3 | 0.5 | 90 | 5 | 20 | -17.8023 | -4.4506 | -4.4506 | 85.5494 | 85.5494 | -2.9303 | 97.57% | 97.52% | 97.22% | 97.55% | 97.54% | 97.5% | 97.88% | 97.69% | 97.6% | 97.58% | 97.56% | 97.32% | 97.49% | 97.22% | 97.48% | 97.39% | 97.19% | 97.18% | 97.14% | 96.93% | 96.73% | 96.45% | 96.05% | 94.44% | 91.24% | 86.77% | 82.83% | 75.05% | 71.74% | 67.08%
365 | 1:01 | 87.0187 | 90 | 3 | 0.5 | 90 | 5 | 20 | -18.205 | -4.5513 | -4.5513 | 85.4487 | 85.4487 | -2.9813 | 97.43% | 97.1% | 97.46% | 97.45% | 97.41% | 97.84% | 97.63% | 97.54% | 97.51% | 97.49% | 97.22% | 97.43% | 97.13% | 97.42% | 97.31% | 97.1% | 97.08% | 97.04% | 96.85% | 96.67% | 96.46% | 96.07% | 94.56% | 91.48% | 87.15% | 83.28% | 75.61% | 72.31% | 67.66% | 62.13%
366 | 1:01 | 86.3994 | 90 | 3 | 0.5 | 90 | 5 | 20 | -18.5688 | -4.6422 | -4.6422 | 85.3578 | 85.3578 | -3.6006 | 96.96% | 97.36% | 97.35% | 97.3% | 97.78% | 97.56% | 97.45% | 97.42% | 97.41% | 97.11% | 97.34% | 97.02% | 97.35% | 97.22% | 96.99% | 96.97% | 96.93% | 96.76% | 96.59% | 96.45% | 96.08% | 94.68% | 91.72% | 87.54% | 83.75% | 76.18% | 72.9% | 68.25% | 62.72% | 57%
367 | 1:01 | 86.9631 | 90 | 3 | 0.5 | 90 | 5 | 20 | -18.8927 | -4.7232 | -4.7232 | 85.2768 | 85.2768 | -3.0369 | 97.24% | 97.23% | 97.18% | 97.71% | 97.47% | 97.35% | 97.32% | 97.32% | 96.98% | 97.24% | 96.9% | 97.26% | 97.11% | 96.86% | 96.85% | 96.79% | 96.65% | 96.5% | 96.44% | 96.08% | 94.78% | 91.97% | 87.93% | 84.22% | 76.77% | 73.52% | 68.86% | 63.33% | 57.61% | 85.85%
368 | 1:01 | 86.4298 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.1762 | -4.794 | -4.794 | 85.206 | 85.206 | -3.5702 | 97.09% | 97.03% | 97.62% | 97.36% | 97.23% | 97.19% | 97.2% | 96.83% | 97.13% | 96.76% | 97.16% | 96.98% | 96.71% | 96.7% | 96.64% | 96.53% | 96.39% | 96.41% | 96.06% | 94.88% | 92.21% | 88.34% | 84.71% | 77.38% | 74.15% | 69.5% | 63.96% | 58.24% | 86.39% | 85.94%
369 | 1:01 | 85.7557 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.4185 | -4.8546 | -4.8546 | 85.1454 | 85.1454 | -4.2443 | 96.86% | 97.51% | 97.24% | 97.09% | 97.05% | 97.06% | 96.66% | 96.99% | 96.59% | 97.03% | 96.82% | 96.54% | 96.53% | 96.46% | 96.38% | 96.25% | 96.36% | 96.03% | 94.98% | 92.46% | 88.75% | 85.21% | 78.02% | 74.81% | 70.16% | 64.62% | 58.9% | 86.98% | 86.52% | 85.29%
370 | 1:01 | 86.5574 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.6193 | -4.9048 | -4.9048 | 85.0952 | 85.0952 | -3.4426 | 97.38% | 97.08% | 96.93% | 96.88% | 96.9% | 96.46% | 96.82% | 96.39% | 96.88% | 96.64% | 96.34% | 96.33% | 96.25% | 96.2% | 96.09% | 96.3% | 95.98% | 95.06% | 92.7% | 89.18% | 85.73% | 78.68% | 75.5% | 70.85% | 65.3% | 59.59% | 87.6% | 87.14% | 85.91% | 84.92%
371 | 1:02 | 85.6219 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.778 | -4.9445 | -4.9445 | 85.0555 | 85.0555 | -4.3781 | 96.9% | 96.73% | 96.67% | 96.71% | 96.22% | 96.62% | 96.16% | 96.69% | 96.42% | 96.1% | 96.09% | 96.01% | 95.99% | 95.9% | 96.21% | 95.91% | 95.12% | 92.95% | 89.62% | 86.27% | 79.38% | 76.22% | 71.57% | 66.02% | 60.31% | 88.26% | 87.8% | 86.57% | 85.58% | 85.14%
372 | 1:02 | 85.6477 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.8943 | -4.9736 | -4.9736 | 85.0264 | 85.0264 | -4.3523 | 96.49% | 96.43% | 96.47% | 95.94% | 96.38% | 95.89% | 96.47% | 96.17% | 95.82% | 95.81% | 95.72% | 95.74% | 95.67% | 96.09% | 95.81% | 95.17% | 93.19% | 90.07% | 86.83% | 80.11% | 76.99% | 72.34% | 66.79% | 61.07% | 88.95% | 88.5% | 87.26% | 86.27% | 85.83% | 84.09%
373 | 1:02 | 85.8566 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.968 | -4.992 | -4.992 | 85.008 | 85.008 | -4.1434 | 96.14% | 96.19% | 95.61% | 96.09% | 95.57% | 96.2% | 95.86% | 95.49% | 95.48% | 95.38% | 95.44% | 95.39% | 95.93% | 95.67% | 95.2% | 93.43% | 90.54% | 87.42% | 80.89% | 77.8% | 73.15% | 67.6% | 61.89% | 89.68% | 89.22% | 87.99% | 87% | 86.56% | 84.82% | 83.98%
374 | 1:02 | 85.7364 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.999 | -4.9997 | -4.9997 | 85.0003 | 85.0003 | -4.2636 | 95.85% | 95.22% | 95.75% | 95.18% | 95.87% | 95.5% | 95.1% | 95.09% | 94.98% | 95.08% | 95.06% | 95.72% | 95.48% | 95.19% | 93.66% | 91.02% | 88.04% | 81.71% | 78.67% | 74.02% | 68.46% | 62.75% | 90.44% | 89.98% | 88.75% | 87.76% | 87.32% | 85.58% | 84.74% | 83.57%
375 | 1:02 | 84.9819 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.987 | -4.9968 | -4.9968 | 85.0032 | 85.0032 | -5.0181 | 94.74% | 95.32% | 94.71% | 95.47% | 95.05% | 94.63% | 94.62% | 94.49% | 94.65% | 94.65% | 95.45% | 95.24% | 95.15% | 93.87% | 91.52% | 88.69% | 82.59% | 79.59% | 74.95% | 69.39% | 63.68% | 91.23% | 90.77% | 89.54% | 88.55% | 88.11% | 86.37% | 85.53% | 84.36% | 82.4%
376 | 1:03 | 85.4407 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.9322 | -4.9831 | -4.9831 | 85.0169 | 85.0169 | -4.5593 | 94.8% | 94.15% | 94.97% | 94.51% | 94.05% | 94.04% | 93.9% | 94.11% | 94.14% | 95.1% | 94.92% | 95.06% | 94.06% | 92.03% | 89.36% | 83.53% | 80.58% | 75.96% | 70.39% | 64.69% | 92.05% | 91.59% | 90.36% | 89.37% | 88.93% | 87.19% | 86.35% | 85.18% | 83.22% | 0%
377 | 1:03 | 84.5438 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.8347 | -4.9587 | -4.9587 | 85.0413 | 85.0413 | -5.4562 | 93.44% | 94.35% | 93.83% | 93.34% | 93.33% | 93.18% | 93.45% | 93.51% | 94.65% | 94.5% | 94.89% | 94.21% | 92.54% | 90.07% | 84.53% | 81.65% | 77.04% | 71.48% | 65.78% | 92.89% | 92.44% | 91.2% | 90.21% | 89.78% | 88.03% | 87.19% | 86.03% | 84.07% | 0% | 0%
378 | 1:03 | 85.0976 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.6947 | -4.9237 | -4.9237 | 85.0763 | 85.0763 | -4.9024 | 93.56% | 92.98% | 92.45% | 92.44% | 92.28% | 92.61% | 92.72% | 94.06% | 93.95% | 94.62% | 94.31% | 93.04% | 90.79% | 85.6% | 82.81% | 78.22% | 72.67% | 66.98% | 93.77% | 93.31% | 92.07% | 91.08% | 90.65% | 88.9% | 88.06% | 86.9% | 84.94% | 0% | 0% | 0%
379 | 1:03 | 84.5764 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.5125 | -4.8781 | -4.8781 | 85.1219 | 85.1219 | -5.4236 | 91.91% | 91.33% | 91.32% | 91.14% | 91.55% | 91.7% | 93.27% | 93.2% | 94.2% | 94.32% | 93.52% | 91.53% | 86.74% | 84.06% | 79.51% | 73.97% | 68.3% | 94.66% | 94.21% | 92.97% | 91.98% | 91.54% | 89.8% | 88.96% | 87.8% | 85.83% | 0% | 0% | 0% | 0%
380 | 1:03 | 84.0223 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.2885 | -4.8221 | -4.8221 | 85.1779 | 85.1779 | -5.9777 | 89.88% | 89.88% | 89.68% | 90.18% | 90.38% | 92.21% | 92.2% | 93.57% | 94.19% | 93.95% | 92.25% | 87.93% | 85.41% | 80.92% | 75.41% | 69.76% | 95.58% | 95.12% | 93.89% | 92.89% | 92.46% | 90.71% | 89.87% | 88.71% | 86.75% | 0% | 0% | 0% | 0% | 0%
381 | 1:03 | 84.4651 | 90 | 3 | 0.5 | 90 | 5 | 20 | -19.0231 | -4.7558 | -4.7558 | 85.2442 | 85.2442 | -5.5349 | 87.98% | 87.76% | 88.37% | 88.63% | 90.77% | 90.81% | 92.64% | 93.84% | 94.25% | 92.92% | 89.17% | 86.86% | 82.47% | 77% | 71.4% | 96.51% | 96.06% | 94.82% | 93.83% | 93.39% | 91.65% | 90.81% | 89.65% | 87.69% | 0% | 0% | 0% | 0% | 0% | 0%
382 | 1:04 | 83.9631 | 90 | 3 | 0.5 | 90 | 5 | 20 | -18.717 | -4.6793 | -4.6793 | 85.3207 | 85.3207 | -6.0369 | 85.2% | 85.93% | 86.26% | 88.77% | 88.89% | 91.25% | 93.14% | 94.34% | 93.44% | 90.39% | 88.38% | 84.15% | 78.77% | 73.23% | 97.47% | 97.01% | 95.77% | 94.78% | 94.35% | 92.6% | 91.76% | 90.6% | 88.64% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
383 | 1:04 | 84.7283 | 90 | 3 | 0.5 | 90 | 5 | 20 | -18.3708 | -4.5927 | -4.5927 | 85.4073 | 85.4073 | -5.2717 | 82.59% | 83% | 85.95% | 86.15% | 89.15% | 91.89% | 94.03% | 93.67% | 91.49% | 89.93% | 85.94% | 80.72% | 75.29% | 98.43% | 97.98% | 96.74% | 95.75% | 95.31% | 93.57% | 92.73% | 91.57% | 89.61% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
384 | 1:04 | 84.5736 | 90 | 3 | 0.5 | 90 | 5 | 20 | -17.9852 | -4.4963 | -4.4963 | 85.5037 | 85.5037 | -5.4264 | 78.4% | 81.87% | 82.18% | 85.95% | 89.72% | 93.03% | 93.33% | 92.24% | 91.37% | 87.81% | 82.85% | 77.6% | 99.42% | 98.96% | 97.73% | 96.73% | 96.3% | 94.55% | 93.71% | 92.55% | 90.59% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
385 | 1:04 | 84.8821 | 90 | 3 | 0.5 | 90 | 5 | 20 | -17.5611 | -4.3903 | -4.3903 | 85.6097 | 85.6097 | -5.1179 | 89.24% | 90.11% | 90.9% | 91.95% | 93.09% | 94.39% | 96.13% | 96.49% | 97.28% | 98.13% | 98.78% | 99.59% | 99.95% | 98.72% | 97.73% | 97.29% | 95.55% | 94.71% | 93.55% | 91.58% | 89.2% | 87.85% | 84.8% | 83.56% | 79.98% | 77.39% | 77.11% | 74.92% | 76.82% | 74.39%
386 | 1:04 | 84.61 | 90 | 3 | 0.5 | 90 | 5 | 20 | -17.0993 | -4.2748 | -4.2748 | 85.7252 | 85.7252 | -5.39 | 89.11% | 89.9% | 90.95% | 92.09% | 93.38% | 95.13% | 95.49% | 96.28% | 97.12% | 97.77% | 98.59% | 99.04% | 99.72% | 98.73% | 98.29% | 96.55% | 95.71% | 94.55% | 92.59% | 90.2% | 88.85% | 85.8% | 84.56% | 80.99% | 78.39% | 78.11% | 75.92% | 77.82% | 75.39% | 75.43%
387 | 1:04 | 85.3103 | 90 | 3 | 0.5 | 90 | 5 | 20 | -16.6009 | -4.1502 | -4.1502 | 85.8498 | 85.8498 | -4.6897 | 88.89% | 89.94% | 91.08% | 92.37% | 94.12% | 94.48% | 95.27% | 96.11% | 96.76% | 97.58% | 98.03% | 99.27% | 99.74% | 99.3% | 97.56% | 96.72% | 95.56% | 93.59% | 91.21% | 89.86% | 86.81% | 85.57% | 82% | 79.4% | 79.12% | 76.93% | 78.83% | 76.4% | 76.44% | 74.63%
388 | 1:05 | 85.7258 | 90 | 3 | 0.5 | 90 | 5 | 20 | -16.0669 | -4.0167 | -4.0167 | 85.9833 | 85.9833 | -4.2742 | 88.92% | 90.06% | 91.36% | 93.11% | 93.47% | 94.26% | 95.1% | 95.75% | 96.56% | 97.02% | 98.25% | 99.25% | 99.68% | 98.57% | 97.73% | 96.57% | 94.61% | 92.22% | 90.88% | 87.83% | 86.58% | 83.01% | 80.41% | 80.14% | 77.95% | 79.85% | 77.41% | 77.45% | 75.64% | 85.67%
389 | 1:05 | 85.9344 | 90 | 3 | 0.5 | 90 | 5 | 20 | -15.4985 | -3.8746 | -3.8746 | 86.1254 | 86.1254 | -4.0656 | 89.05% | 90.34% | 92.09% | 92.45% | 93.24% | 94.08% | 94.73% | 95.55% | 96% | 97.24% | 98.23% | 98.67% | 99.59% | 98.75% | 97.59% | 95.63% | 93.24% | 91.89% | 88.84% | 87.6% | 84.03% | 81.43% | 81.15% | 78.96% | 80.87% | 78.43% | 78.47% | 76.66% | 86.69% | 93.32%
390 | 1:05 | 85.4495 | 90 | 3 | 0.5 | 90 | 5 | 20 | -14.8968 | -3.7242 | -3.7242 | 86.2758 | 86.2758 | -4.5505 | 89.32% | 91.07% | 91.43% | 92.22% | 93.07% | 93.72% | 94.53% | 94.98% | 96.22% | 97.21% | 97.65% | 99.39% | 99.77% | 98.61% | 96.64% | 94.26% | 92.91% | 89.86% | 88.62% | 85.05% | 82.45% | 82.17% | 79.98% | 81.88% | 79.45% | 79.49% | 77.68% | 87.71% | 94.33% | 92.38%
391 | 1:05 | 86.1028 | 90 | 3 | 0.5 | 90 | 5 | 20 | -14.2633 | -3.5658 | -3.5658 | 86.4342 | 86.4342 | -3.8972 | 90.06% | 90.42% | 91.21% | 92.05% | 92.7% | 93.51% | 93.97% | 95.2% | 96.2% | 96.63% | 98.38% | 99.22% | 99.62% | 97.66% | 95.27% | 93.93% | 90.88% | 89.63% | 86.06% | 83.46% | 83.19% | 81% | 82.9% | 80.46% | 80.5% | 78.69% | 88.72% | 95.35% | 93.39% | 36.48%
Note on C8: This quantity is the resource (net) output/consumption, as telemetered to PJM
Note on D8: This is the economic basepoint / non-regulation setpoint
Note on E8: This is the economic ramp rate limit of the resource, as submitted to eMKT
Note on H8: This is the regulation assignment, in MW
Note on I8: This is the fleet TREG, as telemetered to PJM
Note on J8: This is the regulation signal, as sent from PJM, calculated by the EMS

## Sheet3 (hidden)
0 | 1 | 0 | 1 | 0.024973 | 0.02582
0 | 1 | 0 | 1 |  | 0.00084679
0 | 1 | 0 | 1
0 | 1 | 0 | 1
0 | 1 | 0 | 1
0 | 1 | 0 | 1
0 | 1 | 0 | 1
0 | 1 | 0 | 1 |  |  | #NAME?
0 | 1 | 0 | 1
0 | 1 | 0 | 1
0 | 1 | 0.1 | 1.1
0 | 1 | 0 | 1
0 | 1 | 0 | 1
0 | 1 | 0 | 1
0 | 1 | 0 | 1
0 | 1 | 0 | 0.9
0 | 1 | 0 | 1
0 | 1 | 0 | 1
0 | 1 | 0 | 1
0 | 1 | 0 | 1
0 | 1 | 0.1 | 1
0 | 1 | 0 | 1
0 | 1 | 0 | 1
0 | 1 | 0 | 1
0 | 1 | 0 | 1
0 | 1 | 0 | 1
0 | 1 | 0 | 1
0 | 1 | 0 | 1
0 | 1 | 0 | 1
0 | 1 | 0 | 1
0 | 1 | 0 | 1

## Score Template 2
|  | Factor | Weight |  |  |  | Hrly Avg | [14 empty] | Partial Scores | [74 empty] | Slope Check | [109 empty] | 1 | Max Correlation&Slope
| Accuracy | A | 0.33333 |  | Accuracy Score |  | 0.88446 | [5 empty] | 3.7667 |  | FALSE |  | Start Time |  | End Time |  | Accuracy Score |  | 0.88446 | [73 empty] | 0 | [109 empty] | 2 | Max Accuracy x Delay
| Delay | B | 0.33333 |  | Delay Score |  | 0.86185 |  |  |  |  | Avg Delay | 00:00:38 |  |  |  | B39 |  | B398 |  | Delay Score |  | 0.86185 |  |  | Time Shift (min) |  | +0.17m | +0.33m | +0.50m | +0.67m | +0.83m | +1.00m | +1.17m | +1.33m | +1.50m | +1.67m | +1.83m | +2.00m | +2.17m | +2.33m | +2.50m | +2.67m | +2.83m | +3.00m | +3.17m | +3.33m | +3.50m | +3.67m | +3.83m | +4.00m | +4.17m | +4.33m | +4.50m | +4.67m | +4.83m | +5.00m | [9 empty] | +0.00m | +0.00m | +0.01m | +0.01m | +0.01m | +0.01m | +0.01m | +0.01m | +0.02m | +0.02m | +0.02m | +0.02m | +0.02m | +0.02m | +0.03m | +0.03m | +0.03m | +0.03m | +0.03m | +0.03m | +0.04m | +0.04m | +0.04m | +0.04m | +0.04m | +0.04m | +0.05m | +0.05m | +0.05m | +0.05m |  | +0.00m | +0.00m | +0.01m | +0.01m | +0.01m | +0.01m | +0.01m | +0.01m | +0.02m | +0.02m | +0.02m | +0.02m | +0.02m | +0.02m | +0.03m | +0.03m | +0.03m | +0.03m | +0.03m | +0.03m | +0.04m | +0.04m | +0.04m | +0.04m | +0.04m | +0.04m | +0.05m | +0.05m | +0.05m | +0.05m |  |  | +0.00m | +0.00m | +0.01m | +0.01m | +0.01m | +0.01m | +0.01m | +0.01m | +0.02m | +0.02m | +0.02m | +0.02m | +0.02m | +0.02m | +0.03m | +0.03m | +0.03m | +0.03m | +0.03m | +0.03m | +0.04m | +0.04m | +0.04m | +0.04m | +0.04m | +0.04m | +0.05m | +0.05m | +0.05m | +0.05m | [5 empty] | +0.00m | +0.00m | +0.01m | +0.01m | +0.01m | +0.01m | +0.01m | +0.01m | +0.02m | +0.02m | +0.02m | +0.02m | +0.02m | +0.02m | +0.03m | +0.03m | +0.03m | +0.03m | +0.03m | +0.03m | +0.04m | +0.04m | +0.04m | +0.04m | +0.04m | +0.04m | +0.05m | +0.05m | +0.05m | +0.05m
| Precision | C | 0.33333 |  | Precision Score |  | 0.0031543 |  |  |  |  | Denominator | 0.055555 | [7 empty] | Precision Score |  | 0.0031543 |  |  | Time Shift (sec) | No Time Shift | +10s | +20s | +30s | +40s | +50s | +60s | +70s | +80s | +90s | +100s | +110s | +120s | +130s | +140s | +150s | +160s | +170s | +180s | +190s | +200s | +210s | +220s | +230s | +240s | +250s | +260s | +270s | +280s | +290s | +300s |  |  | SlopeToUse | 1 | Signal |  |  |  | No Time Shift | +10s | +20s | +30s | +40s | +50s | +60s | +70s | +80s | +90s | +100s | +110s | +120s | +130s | +140s | +150s | +160s | +170s | +180s | +190s | +200s | +210s | +220s | +230s | +240s | +250s | +260s | +270s | +280s | +290s | +300s | No Time Shift | +10s | +20s | +30s | +40s | +50s | +60s | +70s | +80s | +90s | +100s | +110s | +120s | +130s | +140s | +150s | +160s | +170s | +180s | +190s | +200s | +210s | +220s | +230s | +240s | +250s | +260s | +270s | +280s | +290s | +300s |  | No Time Shift | +10s | +20s | +30s | +40s | +50s | +60s | +70s | +80s | +90s | +100s | +110s | +120s | +130s | +140s | +150s | +160s | +170s | +180s | +190s | +200s | +210s | +220s | +230s | +240s | +250s | +260s | +270s | +280s | +290s | +300s |  |  |  |  | No Time Shift | +10s | +20s | +30s | +40s | +50s | +60s | +70s | +80s | +90s | +100s | +110s | +120s | +130s | +140s | +150s | +160s | +170s | +180s | +190s | +200s | +210s | +220s | +230s | +240s | +250s | +260s | +270s | +280s | +290s | +300s | [12 empty] | 1 | AREG Denominator
| Slope Limit |  | 0 |  | Composite Score |  | 0.58315 |  |  |  |  | Hourly Mileage | 0.17207 | [7 empty] | Composite Score |  | 0.58315 |  |  | Time Shift (intervals) | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  |  | 2 | 2 | Percent |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 00:02:18 |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 |  | 00:00:38 | Acc #2 |  | Delay #2 |  |  |  | Prec. 2 |  |  |  | 2 | AvgAbsSignal Denominator |  |  | Mileage
| StDev Limit |  | 0.05 | [22 empty] | Delay Score | 100% | 100% | 96.67% | 93.33% | 90% | 86.67% | 83.33% | 80% | 76.67% | 73.33% | 70% | 66.67% | 63.33% | 60% | 56.67% | 53.33% | 50% | 46.67% | 43.33% | 40% | 36.67% | 33.33% | 30% | 26.67% | 23.33% | 20% | 16.67% | 13.33% | 10% | 6.667% | 3.333% | [8 empty] | 100% | 100% | 96.67% | 93.33% | 90% | 86.67% | 83.33% | 80% | 76.67% | 73.33% | 70% | 66.67% | 63.33% | 60% | 56.67% | 53.33% | 50% | 46.67% | 43.33% | 40% | 36.67% | 33.33% | 30% | 26.67% | 23.33% | 20% | 16.67% | 13.33% | 10% | 6.667% | 3.333% | 100% | 100% | 96.67% | 93.33% | 90% | 86.67% | 83.33% | 80% | 76.67% | 73.33% | 70% | 66.67% | 63.33% | 60% | 56.67% | 53.33% | 50% | 46.67% | 43.33% | 40% | 36.67% | 33.33% | 30% | 26.67% | 23.33% | 20% | 16.67% | 13.33% | 10% | 6.667% | 3.333% |  | 100% | 100% | 96.67% | 93.33% | 90% | 86.67% | 83.33% | 80% | 76.67% | 73.33% | 70% | 66.67% | 63.33% | 60% | 56.67% | 53.33% | 50% | 46.67% | 43.33% | 40% | 36.67% | 33.33% | 30% | 26.67% | 23.33% | 20% | 16.67% | 13.33% | 10% | 6.667% | 3.333% |  | 13.7778 |  |  | 100% | 100% | 96.67% | 93.33% | 90% | 86.67% | 83.33% | 80% | 76.67% | 73.33% | 70% | 66.67% | 63.33% | 60% | 56.67% | 53.33% | 50% | 46.67% | 43.33% | 40% | 36.67% | 33.33% | 30% | 26.67% | 23.33% | 20% | 16.67% | 13.33% | 10% | 6.667% | 3.333% |  | 3.7667 | 0.88446 |  | 0.86185 |  |  |  | 0.0031543 | [7 empty] | 0.17207
|  | Feedback | [6 empty] | Command | Signal |  | Response
Interval | TIME | AGC MW | Raw ECOBP | Energy RR at AGC MW (MW/min) | RR MW/10sec | Ramped EcoBP | Unit AREG | Fleet TREG | Fleet Regulation Control Signal | Raw Unit REG | Raw EcoBP + Raw Reg | Unit Resp. | Mileage | RESOURCE REPORT | [12 empty] | Correl Signal to Response | Correl Signal to Response +10s | Correl Signal to Response +20s | Correl Signal to Response +30s | Correl Signal to Response +40s | Correl Signal to Response +50s | Correl Signal to Response +60s | Correl Signal to Response +70s | Correl Signal to Response +80s | Correl Signal to Response +90s | Correl Signal to Response +100s | Correl Signal to Response +110s | Correl Signal to Response +120s | Correl Signal to Response +130s | Correl Signal to Response +140s | Correl Signal to Response +150s | Correl Signal to Response +160s | Correl Signal to Response +170s | Correl Signal to Response +180s | Correl Signal to Response +190s | Correl Signal to Response +200s | Correl Signal to Response +210s | Correl Signal to Response +220s | Correl Signal to Response +230s | Correl Signal to Response +240s | Correl Signal to Response +250s | Correl Signal to Response +260s | Correl Signal to Response +270s | Correl Signal to Response +280s | Correl Signal to Response +290s | Correl Signal to Response +300s | Reg Signal Percent | 5-minute Signal Slope | 5-minute Signal Percent Slope | Slope Used | Slope Limit | -Slope Limit | StDev Used | StDev Limit | Response Slope | Response Slope +10s | Response Slope +20s | Response Slope +30s | Response Slope +40s | Response Slope +50s | Response Slope +60s | Response Slope +70s | Response Slope +80s | Response Slope +90s | Response Slope +100s | Response Slope +110s | Response Slope +120s | Response Slope +130s | Response Slope +140s | Response Slope +150s | Response Slope +160s | Response Slope +170s | Response Slope +180s | Response Slope +190s | Response Slope +200s | Response Slope +210s | Response Slope +220s | Response Slope +230s | Response Slope +240s | Response Slope +250s | Response Slope +260s | Response Slope +270s | Response Slope +280s | Response Slope +290s | Response Slope +300s | Accuracy Scoring Mode | Accuracy Scoring Mode +10s | Accuracy Scoring Mode +20s | Accuracy Scoring Mode +30s | Accuracy Scoring Mode +40s | Accuracy Scoring Mode +50s | Accuracy Scoring Mode +60s | Accuracy Scoring Mode +70s | Accuracy Scoring Mode +80s | Accuracy Scoring Mode +90s | Accuracy Scoring Mode +100s | Accuracy Scoring Mode +110s | Accuracy Scoring Mode +120s | Accuracy Scoring Mode +130s | Accuracy Scoring Mode +140s | Accuracy Scoring Mode +150s | Accuracy Scoring Mode +160s | Accuracy Scoring Mode +170s | Accuracy Scoring Mode +180s | Accuracy Scoring Mode +190s | Accuracy Scoring Mode +200s | Accuracy Scoring Mode +210s | Accuracy Scoring Mode +220s | Accuracy Scoring Mode +230s | Accuracy Scoring Mode +240s | Accuracy Scoring Mode +250s | Accuracy Scoring Mode +260s | Accuracy Scoring Mode +270s | Accuracy Scoring Mode +280s | Accuracy Scoring Mode +290s | Accuracy Scoring Mode +300s |  | Accuracy Score | Accuracy Score +10s | Accuracy Score +20s | Accuracy Score +30s | Accuracy Score +40s | Accuracy Score +50s | Accuracy Score +60s | Accuracy Score +70s | Accuracy Score +80s | Accuracy Score +90s | Accuracy Score +100s | Accuracy Score +110s | Accuracy Score +120s | Accuracy Score +130s | Accuracy Score +140s | Accuracy Score +150s | Accuracy Score +160s | Accuracy Score +170s | Accuracy Score +180s | Accuracy Score +190s | Accuracy Score +200s | Accuracy Score +210s | Accuracy Score +220s | Accuracy Score +230s | Accuracy Score +240s | Accuracy Score +250s | Accuracy Score +260s | Accuracy Score +270s | Accuracy Score +280s | Accuracy Score +290s | Accuracy Score +300s | Max Accuracy Score | Offset | Accuracy Method Used | Delay Score | Weighted Acc. & Delay | Weighted Acc. & Delay +10s | Weighted Acc. & Delay +20s | Weighted Acc. & Delay +30s | Weighted Acc. & Delay +40s | Weighted Acc. & Delay +50s | Weighted Acc. & Delay +60s | Weighted Acc. & Delay +70s | Weighted Acc. & Delay +80s | Weighted Acc. & Delay +90s | Weighted Acc. & Delay +100s | Weighted Acc. & Delay +110s | Weighted Acc. & Delay +120s | Weighted Acc. & Delay +130s | Weighted Acc. & Delay +140s | Weighted Acc. & Delay +150s | Weighted Acc. & Delay +160s | Weighted Acc. & Delay +170s | Weighted Acc. & Delay +180s | Weighted Acc. & Delay +190s | Weighted Acc. & Delay +200s | Weighted Acc. & Delay +210s | Weighted Acc. & Delay +220s | Weighted Acc. & Delay +230s | Weighted Acc. & Delay +240s | Weighted Acc. & Delay +250s | Weighted Acc. & Delay +260s | Weighted Acc. & Delay +270s | Weighted Acc. & Delay +280s | Weighted Acc. & Delay +290s | Weighted Acc. & Delay +300s | Max Weighted Acc/Del Score | Offset1 | Accuracy Score Adjust | Accuracy Method Used | Delay Score | Absolute Signal | Average Absolute Signal | Precis. Score AREG | Precis. Score AbsSig | Accuracy Score | Accuracy Method Used | Accuracy Method Number | Delay Score | Precision Score | +AREG | -AREG | Mileage | StdDev of Slopes | StdDev of Percent Signal
| 23:55 | 0 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.8568 | -0.078568 | -0.078568 | 0 | [196 empty] | 20 | -20
| 23:55 | -7.8568 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.5172 | -0.075172 | -0.075172 | -7.8568 | [196 empty] | 20 | -20
| 23:55 | -7.5172 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -6.6477 | -0.066477 | -0.066477 | -7.5172 | [196 empty] | 20 | -20
| 23:56 | -6.6477 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -6.3605 | -0.063605 | -0.063605 | -6.6477 | [196 empty] | 20 | -20
| 23:56 | -6.3605 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.8965 | -0.058965 | -0.058965 | -6.3605 | [196 empty] | 20 | -20
| 23:56 | -5.8965 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.0547 | -0.050547 | -0.050547 | -5.8965 | [196 empty] | 20 | -20
| 23:56 | -5.0547 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.8119 | -0.028119 | -0.028119 | -5.0547 | [196 empty] | 20 | -20
| 23:56 | -2.8119 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -0.055731 | -0.00055731 | -0.00055731 | -2.8119 | [196 empty] | 20 | -20
| 23:56 | -0.055731 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.3715 | 0.023715 | 0.023715 | -0.055731 | [196 empty] | 20 | -20
| 23:57 | 2.3715 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 4.3667 | 0.043667 | 0.043667 | 2.3715 | [196 empty] | 20 | -20
| 23:57 | 4.3667 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 6.5911 | 0.065911 | 0.065911 | 4.3667 | [196 empty] | 20 | -20
| 23:57 | 6.5911 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 9.4018 | 0.094018 | 0.094018 | 6.5911 | [196 empty] | 20 | -20
| 23:57 | 9.4018 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 12.6695 | 0.12669 | 0.12669 | 9.4018 | [196 empty] | 20 | -20
| 23:57 | 12.6695 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 14.85 | 0.1485 | 0.1485 | 12.6695 | [196 empty] | 20 | -20
| 23:57 | 14.85 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 16.3988 | 0.16399 | 0.16399 | 14.85 | [196 empty] | 20 | -20
| 23:58 | 16.3988 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 16.3291 | 0.16329 | 0.16329 | 16.3988 | [196 empty] | 20 | -20
| 23:58 | 16.3291 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 15.5681 | 0.15568 | 0.15568 | 16.3291 | [196 empty] | 20 | -20
| 23:58 | 15.5681 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 14.7497 | 0.1475 | 0.1475 | 15.5681 | [196 empty] | 20 | -20
| 23:58 | 14.7497 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 12.7175 | 0.12717 | 0.12717 | 14.7497 | [196 empty] | 20 | -20
| 23:58 | 12.7175 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 10.2591 | 0.10259 | 0.10259 | 12.7175 | [196 empty] | 20 | -20
| 23:58 | 10.2591 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 8.4124 | 0.084124 | 0.084124 | 10.2591 | [196 empty] | 20 | -20
| 23:59 | 8.4124 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 6.6796 | 0.066796 | 0.066796 | 8.4124 | [196 empty] | 20 | -20
| 23:59 | 6.6796 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 4.9512 | 0.049512 | 0.049512 | 6.6796 | [196 empty] | 20 | -20
| 23:59 | 4.9512 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 4.3565 | 0.043565 | 0.043565 | 4.9512 | [196 empty] | 20 | -20
| 23:59 | 4.3565 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.8812 | 0.038812 | 0.038812 | 4.3565 | [196 empty] | 20 | -20
| 23:59 | 3.8812 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.7952 | 0.037952 | 0.037952 | 3.8812 | [196 empty] | 20 | -20
| 23:59 | 3.7952 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 4.0236 | 0.040236 | 0.040236 | 3.7952 | [196 empty] | 20 | -20
| 24:00 | 4.0236 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 4.0526 | 0.040526 | 0.040526 | 4.0236 | [196 empty] | 20 | -20
| 24:00 | 4.0526 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.7779 | 0.027779 | 0.027779 | 4.0526 | [196 empty] | 20 | -20
| 24:00 | 2.7779 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.3005 | 0.013005 | 0.013005 | 2.7779 | [196 empty] | 20 | -20
1 | 0:00 | 1.3005 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 0.65133 | 0.0065133 | 0.0065133 | 1.3005 | 0.00032567 | [13 empty] | 0.95702 | 1 | 0.95853 | 0.85837 | 0.73139 | 0.60108 | 0.48515 | 0.38531 | 0.29781 | 0.21067 | 0.13322 | 0.057386 | -0.022832 | -0.10335 | -0.17797 | -0.23328 | -0.26983 | -0.28689 | -0.29468 | -0.30176 | -0.31599 | -0.36568 | -0.44851 | -0.56317 | -0.68591 | -0.79664 | -0.85901 | -0.85722 | -0.8159 | -0.75761 | -0.69274 | 0.00032567 | 0.00052756 | 2.6378e-05 | 2.6378e-05 | 0 | 0 | 0.001902 | 0.05 | -0.021698 | 0.052756 | 0.12527 | 0.19264 | 0.25673 | 0.3066 | 0.34487 | 0.37505 | 0.39866 | 0.42033 | 0.43417 | 0.45277 | 0.47367 | 0.49032 | 0.50156 | 0.50197 | 0.48572 | 0.44859 | 0.39062 | 0.32721 | 0.26235 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.97828 | 0.94727 | 0.87475 | 0.80738 | 0.7433 | 0.69342 | 0.65515 | 0.62498 | 0.60136 | 0.5797 | 0.56586 | 0.54725 | 0.52636 | 0.50971 | 0.49847 | 0.49806 | 0.51431 | 0.55144 | 0.6094 | 0.67282 | 0.73768 | 0.79921 | 0.85617 | 0.90633 | 0.9523 | 0.99606 | 0.9398 | 0.88478 | 0.83614 | 0.79095 | 0.74922 | 0.99606 | 25 | Slope | 0.2 | 0.65943 | 0.64909 | 0.61381 | 0.58024 | 0.54777 | 0.52003 | 0.49616 | 0.47499 | 0.45601 | 0.43768 | 0.42195 | 0.40464 | 0.38656 | 0.3699 | 0.35505 | 0.3438 | 0.3381 | 0.33937 | 0.34758 | 0.35761 | 0.36812 | 0.37752 | 0.38539 | 0.391 | 0.39521 | 0.39869 | 0.36882 | 0.33937 | 0.31205 | 0.28587 | 0.26085 | 0.65943 | 0 | 0.97828 | Slope | 1 | 0.0065133 | 0.055555 | 0.96776 | 0 | 0.97828 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00032567 | 0.00012332 | 0.001902
2 | 0:00 | 0.65133 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -0.3605 | -0.003605 | -0.003605 | 0.65133 | 0.00050592 | [13 empty] | 0.95853 | 1 | 0.96207 | 0.87199 | 0.75508 | 0.63773 | 0.53192 | 0.43881 | 0.35572 | 0.28502 | 0.21803 | 0.14599 | 0.068632 | -0.0066263 | -0.068921 | -0.11302 | -0.1405 | -0.15835 | -0.17684 | -0.19679 | -0.24265 | -0.31991 | -0.43107 | -0.56259 | -0.69742 | -0.8063 | -0.86187 | -0.86452 | -0.84367 | -0.80915 | -0.76172 | -0.00018025 | 0.0012527 | 6.2636e-05 | 6.2636e-05 | 0 | 0 | 0.0019372 | 0.05 | 0.052756 | 0.12527 | 0.19264 | 0.25673 | 0.3066 | 0.34487 | 0.37505 | 0.39866 | 0.42033 | 0.43417 | 0.45277 | 0.47367 | 0.49032 | 0.50156 | 0.50197 | 0.48572 | 0.44859 | 0.39062 | 0.32721 | 0.26235 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.94731 | 0.87479 | 0.80742 | 0.74334 | 0.69346 | 0.65519 | 0.62501 | 0.6014 | 0.57973 | 0.56589 | 0.54729 | 0.52639 | 0.50975 | 0.49851 | 0.4981 | 0.51434 | 0.55147 | 0.60944 | 0.67285 | 0.73772 | 0.79925 | 0.85621 | 0.90637 | 0.95233 | 0.99603 | 0.93976 | 0.88474 | 0.8361 | 0.79091 | 0.74918 | 0.70955 | 0.99603 | 24 | Slope | 0.23333 | 0.6491 | 0.62493 | 0.59136 | 0.55889 | 0.53115 | 0.50729 | 0.48611 | 0.46713 | 0.4488 | 0.43308 | 0.41576 | 0.39769 | 0.38103 | 0.36617 | 0.35492 | 0.34923 | 0.35049 | 0.3587 | 0.36873 | 0.37924 | 0.38864 | 0.39651 | 0.40212 | 0.40633 | 0.40979 | 0.37992 | 0.35047 | 0.32315 | 0.29697 | 0.27195 | 0.24763 | 0.6491 | 0 | 0.94731 | Slope | 1 | 0.003605 |  | 0.98216 | 0 | 0.94731 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00050592 | 0.00013193 | 0.0019372
3 | 0:00 | -0.3605 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -1.2035 | -0.012035 | -0.012035 | -0.3605 | 0.00042152 | [13 empty] | 0.96207 | 1 | 0.96592 | 0.88331 | 0.77755 | 0.67022 | 0.57171 | 0.484 | 0.41586 | 0.35552 | 0.29281 | 0.22405 | 0.15227 | 0.088843 | 0.037527 | 0.0027966 | -0.024348 | -0.052771 | -0.084857 | -0.13776 | -0.2112 | -0.31696 | -0.44457 | -0.59047 | -0.724 | -0.82094 | -0.86789 | -0.87968 | -0.87491 | -0.85379 | -0.81984 | -0.00060177 | 0.0019264 | 9.6321e-05 | 9.6321e-05 | 0 | 0 | 0.0019994 | 0.05 | 0.12527 | 0.19264 | 0.25673 | 0.3066 | 0.34487 | 0.37505 | 0.39866 | 0.42033 | 0.43417 | 0.45277 | 0.47367 | 0.49032 | 0.50156 | 0.50197 | 0.48572 | 0.44859 | 0.39062 | 0.32721 | 0.26235 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.87482 | 0.80745 | 0.74337 | 0.69349 | 0.65522 | 0.62505 | 0.60143 | 0.57977 | 0.56593 | 0.54732 | 0.52643 | 0.50978 | 0.49854 | 0.49813 | 0.51438 | 0.55151 | 0.60947 | 0.67289 | 0.73775 | 0.79928 | 0.85624 | 0.9064 | 0.95237 | 0.99599 | 0.93973 | 0.88471 | 0.83607 | 0.79088 | 0.74915 | 0.70951 | 0.67123 | 0.99599 | 23 | Slope | 0.26667 | 0.62494 | 0.60248 | 0.57001 | 0.54228 | 0.51841 | 0.49724 | 0.47826 | 0.45992 | 0.4442 | 0.42689 | 0.40881 | 0.39215 | 0.37729 | 0.36604 | 0.36035 | 0.36161 | 0.36982 | 0.37985 | 0.39036 | 0.39976 | 0.40764 | 0.41325 | 0.41746 | 0.42089 | 0.39102 | 0.36157 | 0.33424 | 0.30807 | 0.28305 | 0.25873 | 0.23485 | 0.62494 | 0 | 0.87482 | Slope | 1 | 0.012035 |  | 0.94042 | 0 | 0.87482 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00042152 | 0.00014128 | 0.0019994
4 | 0:00 | -1.2035 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.1812 | -0.021812 | -0.021812 | -1.2035 | 0.00048884 | [13 empty] | 0.96592 | 1 | 0.9678 | 0.89266 | 0.79582 | 0.696 | 0.60377 | 0.53 | 0.47222 | 0.41642 | 0.35692 | 0.29351 | 0.23288 | 0.18027 | 0.13901 | 0.10633 | 0.069063 | 0.026781 | -0.040734 | -0.12275 | -0.22509 | -0.34711 | -0.49173 | -0.63755 | -0.75583 | -0.83441 | -0.87959 | -0.89976 | -0.90337 | -0.89176 | -0.8686 | -0.0010906 | 0.0025673 | 0.00012836 | 0.00012836 | 0 | 0 | 0.0020854 | 0.05 | 0.19264 | 0.25673 | 0.3066 | 0.34487 | 0.37505 | 0.39866 | 0.42033 | 0.43417 | 0.45277 | 0.47367 | 0.49032 | 0.50156 | 0.50197 | 0.48572 | 0.44859 | 0.39062 | 0.32721 | 0.26235 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.80749 | 0.7434 | 0.69353 | 0.65526 | 0.62508 | 0.60146 | 0.5798 | 0.56596 | 0.54736 | 0.52646 | 0.50981 | 0.49857 | 0.49816 | 0.51441 | 0.55154 | 0.60951 | 0.67292 | 0.73778 | 0.79932 | 0.85627 | 0.90644 | 0.9524 | 0.99596 | 0.9397 | 0.88468 | 0.83604 | 0.79085 | 0.74911 | 0.70948 | 0.6712 | 0.63587 | 0.99596 | 22 | Slope | 0.3 | 0.6025 | 0.58113 | 0.5534 | 0.52953 | 0.50836 | 0.48938 | 0.47104 | 0.45532 | 0.43801 | 0.41993 | 0.40327 | 0.38841 | 0.37716 | 0.37147 | 0.37273 | 0.38095 | 0.39097 | 0.40148 | 0.41088 | 0.41876 | 0.42437 | 0.42858 | 0.43199 | 0.40212 | 0.37267 | 0.34535 | 0.31917 | 0.29415 | 0.26983 | 0.24595 | 0.22307 | 0.6025 | 0 | 0.80749 | Slope | 1 | 0.021812 |  | 0.89203 | 0 | 0.80749 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00048884 | 0.00015039 | 0.0020854
5 | 0:01 | -2.1812 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -3.3365 | -0.033365 | -0.033365 | -2.1812 | 0.00057765 | [13 empty] | 0.9678 | 1 | 0.97066 | 0.90126 | 0.81036 | 0.7157 | 0.63435 | 0.56804 | 0.51355 | 0.46037 | 0.40494 | 0.35039 | 0.29954 | 0.25758 | 0.22171 | 0.18191 | 0.13317 | 0.05846 | -0.037212 | -0.14591 | -0.26257 | -0.39997 | -0.54457 | -0.67416 | -0.76716 | -0.83527 | -0.88206 | -0.90711 | -0.91642 | -0.91321 | -0.90155 | -0.0016683 | 0.003066 | 0.0001533 | 0.0001533 | 0 | 0 | 0.0021491 | 0.05 | 0.25673 | 0.3066 | 0.34487 | 0.37505 | 0.39866 | 0.42033 | 0.43417 | 0.45277 | 0.47367 | 0.49032 | 0.50156 | 0.50197 | 0.48572 | 0.44859 | 0.39062 | 0.32721 | 0.26235 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.74343 | 0.69355 | 0.65528 | 0.6251 | 0.60149 | 0.57982 | 0.56598 | 0.54738 | 0.52648 | 0.50984 | 0.4986 | 0.49819 | 0.51443 | 0.55156 | 0.60953 | 0.67294 | 0.73781 | 0.79934 | 0.8563 | 0.90646 | 0.95242 | 0.99594 | 0.93967 | 0.88465 | 0.83601 | 0.79082 | 0.74909 | 0.70946 | 0.67117 | 0.63585 | 0.61136 | 0.99594 | 21 | Slope | 0.33333 | 0.58114 | 0.56452 | 0.54065 | 0.51948 | 0.5005 | 0.48216 | 0.46644 | 0.44913 | 0.43105 | 0.41439 | 0.39953 | 0.38828 | 0.38259 | 0.38385 | 0.39207 | 0.40209 | 0.4126 | 0.422 | 0.42988 | 0.43549 | 0.4397 | 0.44309 | 0.41322 | 0.38377 | 0.35645 | 0.33027 | 0.30525 | 0.28093 | 0.25706 | 0.23417 | 0.2149 | 0.58114 | 0 | 0.74343 | Slope | 1 | 0.033365 |  | 0.83484 | 0 | 0.74343 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00057765 | 0.00015844 | 0.0021491
6 | 0:01 | -3.3365 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.1028 | -0.041028 | -0.041028 | -3.3365 | 0.00038313 | [13 empty] | 0.97066 | 1 | 0.97256 | 0.90687 | 0.82007 | 0.73351 | 0.65813 | 0.59507 | 0.54283 | 0.49264 | 0.44366 | 0.39685 | 0.35548 | 0.31976 | 0.27806 | 0.22809 | 0.14819 | 0.045614 | -0.075944 | -0.19726 | -0.32909 | -0.46724 | -0.59472 | -0.69289 | -0.76883 | -0.83219 | -0.87913 | -0.90604 | -0.92073 | -0.92893 | -0.9269 | -0.0020514 | 0.0034487 | 0.00017244 | 0.00017244 | 0 | 0 | 0.0022053 | 0.05 | 0.3066 | 0.34487 | 0.37505 | 0.39866 | 0.42033 | 0.43417 | 0.45277 | 0.47367 | 0.49032 | 0.50156 | 0.50197 | 0.48572 | 0.44859 | 0.39062 | 0.32721 | 0.26235 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.69357 | 0.6553 | 0.62512 | 0.60151 | 0.57984 | 0.566 | 0.5474 | 0.5265 | 0.50986 | 0.49862 | 0.49821 | 0.51445 | 0.55158 | 0.60955 | 0.67296 | 0.73783 | 0.79936 | 0.85632 | 0.90648 | 0.95244 | 0.99592 | 0.93965 | 0.88463 | 0.83599 | 0.7908 | 0.74907 | 0.70944 | 0.67115 | 0.63583 | 0.61134 | 0.60144 | 0.99592 | 20 | Slope | 0.36667 | 0.56452 | 0.55177 | 0.5306 | 0.51161 | 0.49328 | 0.47756 | 0.46024 | 0.44217 | 0.42551 | 0.41065 | 0.3994 | 0.39371 | 0.39497 | 0.40318 | 0.41321 | 0.42372 | 0.43312 | 0.44099 | 0.4466 | 0.45081 | 0.45419 | 0.42433 | 0.39488 | 0.36755 | 0.34138 | 0.31636 | 0.29204 | 0.26816 | 0.24528 | 0.226 | 0.21159 | 0.56452 | 0 | 0.69357 | Slope | 1 | 0.041028 |  | 0.79691 | 0 | 0.69357 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00038313 | 0.00016516 | 0.0022053
7 | 0:01 | -4.1028 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.6209 | -0.046209 | -0.046209 | -4.1028 | 0.00025904 | [13 empty] | 0.97256 | 1 | 0.97382 | 0.91075 | 0.82978 | 0.7479 | 0.67569 | 0.61502 | 0.56519 | 0.5199 | 0.47748 | 0.43994 | 0.40636 | 0.36642 | 0.31588 | 0.23555 | 0.12724 | -0.0020184 | -0.1364 | -0.27331 | -0.40682 | -0.528 | -0.62176 | -0.69944 | -0.76718 | -0.82742 | -0.87276 | -0.90249 | -0.92759 | -0.94497 | -0.93792 | -0.0023104 | 0.0037505 | 0.00018753 | 0.00018753 | 0 | 0 | 0.0022537 | 0.05 | 0.34487 | 0.37505 | 0.39866 | 0.42033 | 0.43417 | 0.45277 | 0.47367 | 0.49032 | 0.50156 | 0.50197 | 0.48572 | 0.44859 | 0.39062 | 0.32721 | 0.26235 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.65532 | 0.62514 | 0.60152 | 0.57986 | 0.56602 | 0.54741 | 0.52652 | 0.50987 | 0.49863 | 0.49822 | 0.51447 | 0.5516 | 0.60956 | 0.67298 | 0.73784 | 0.79937 | 0.85633 | 0.9065 | 0.95246 | 0.9959 | 0.93964 | 0.88462 | 0.83598 | 0.79079 | 0.74905 | 0.70942 | 0.67114 | 0.63581 | 0.61133 | 0.60142 | 0.59524 | 0.9959 | 19 | Slope | 0.4 | 0.55177 | 0.54171 | 0.52273 | 0.5044 | 0.48867 | 0.47136 | 0.45328 | 0.43662 | 0.42177 | 0.41052 | 0.40482 | 0.40609 | 0.4143 | 0.42433 | 0.43484 | 0.44424 | 0.45211 | 0.45772 | 0.46193 | 0.4653 | 0.43543 | 0.40598 | 0.37866 | 0.35248 | 0.32746 | 0.30314 | 0.27927 | 0.25638 | 0.23711 | 0.2227 | 0.20952 | 0.55177 | 0 | 0.65532 | Slope | 1 | 0.046209 |  | 0.77127 | 0 | 0.65532 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00025904 | 0.00017039 | 0.0022537
8 | 0:01 | -4.6209 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.7019 | -0.047019 | -0.047019 | -4.6209 | 4.053e-05 | [13 empty] | 0.97382 | 1 | 0.97472 | 0.91523 | 0.83734 | 0.75834 | 0.68875 | 0.63039 | 0.58454 | 0.54522 | 0.51243 | 0.48491 | 0.44913 | 0.4024 | 0.32201 | 0.21289 | 0.075994 | -0.067232 | -0.21804 | -0.35728 | -0.47417 | -0.56078 | -0.63281 | -0.70034 | -0.76341 | -0.81982 | -0.86551 | -0.90447 | -0.93811 | -0.95206 | -0.94208 | -0.002351 | 0.0039866 | 0.00019933 | 0.00019933 | 0 | 0 | 0.0022932 | 0.05 | 0.37505 | 0.39866 | 0.42033 | 0.43417 | 0.45277 | 0.47367 | 0.49032 | 0.50156 | 0.50197 | 0.48572 | 0.44859 | 0.39062 | 0.32721 | 0.26235 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.62515 | 0.60154 | 0.57987 | 0.56603 | 0.54743 | 0.52653 | 0.50988 | 0.49864 | 0.49823 | 0.51448 | 0.55161 | 0.60958 | 0.67299 | 0.73785 | 0.79939 | 0.85634 | 0.90651 | 0.95247 | 0.99589 | 0.93962 | 0.88461 | 0.83597 | 0.79078 | 0.74904 | 0.70941 | 0.67113 | 0.6358 | 0.61132 | 0.60141 | 0.59523 | 0.59594 | 0.99589 | 18 | Slope | 0.43333 | 0.54172 | 0.53385 | 0.51551 | 0.49979 | 0.48248 | 0.4644 | 0.44774 | 0.43288 | 0.42163 | 0.41594 | 0.4172 | 0.42541 | 0.43544 | 0.44595 | 0.45535 | 0.46323 | 0.46884 | 0.47305 | 0.47641 | 0.44654 | 0.41709 | 0.38977 | 0.36359 | 0.33857 | 0.31425 | 0.29038 | 0.26749 | 0.24822 | 0.2338 | 0.22063 | 0.20976 | 0.54172 | 0 | 0.62515 | Slope | 1 | 0.047019 |  | 0.76725 | 0 | 0.62515 | Slope | 2 | 1 | 0 | 20 | -20 | 4.053e-05 | 0.00017399 | 0.0022932
9 | 0:01 | -4.7019 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.8313 | -0.058313 | -0.058313 | -4.7019 | 0.00056468 | [13 empty] | 0.97472 | 1 | 0.97674 | 0.919 | 0.84358 | 0.7676 | 0.70068 | 0.64661 | 0.60734 | 0.57928 | 0.55985 | 0.53279 | 0.49282 | 0.41598 | 0.30532 | 0.16383 | 0.010015 | -0.15169 | -0.30605 | -0.42928 | -0.51272 | -0.57823 | -0.63983 | -0.70184 | -0.76018 | -0.81519 | -0.86784 | -0.91394 | -0.94427 | -0.95527 | -0.94032 | -0.0029156 | 0.0042033 | 0.00021016 | 0.00021016 | 0 | 0 | 0.0023302 | 0.05 | 0.39866 | 0.42033 | 0.43417 | 0.45277 | 0.47367 | 0.49032 | 0.50156 | 0.50197 | 0.48572 | 0.44859 | 0.39062 | 0.32721 | 0.26235 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.60155 | 0.57988 | 0.56604 | 0.54744 | 0.52654 | 0.50989 | 0.49865 | 0.49824 | 0.51449 | 0.55162 | 0.60959 | 0.673 | 0.73786 | 0.7994 | 0.85635 | 0.90652 | 0.95248 | 0.99588 | 0.93961 | 0.8846 | 0.83595 | 0.79076 | 0.74903 | 0.7094 | 0.67111 | 0.63579 | 0.61131 | 0.6014 | 0.59522 | 0.59593 | 0.60456 | 0.99588 | 17 | Slope | 0.46667 | 0.53385 | 0.52663 | 0.5109 | 0.49359 | 0.47551 | 0.45885 | 0.444 | 0.43275 | 0.42705 | 0.42832 | 0.43653 | 0.44656 | 0.45707 | 0.46647 | 0.47434 | 0.47995 | 0.48416 | 0.48752 | 0.45765 | 0.4282 | 0.40087 | 0.3747 | 0.34968 | 0.32536 | 0.30148 | 0.2786 | 0.25932 | 0.24491 | 0.23174 | 0.22086 | 0.21263 | 0.53385 | 0 | 0.60155 | Slope | 1 | 0.058313 |  | 0.71135 | 0 | 0.60155 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00056468 | 0.00017576 | 0.0023302
10 | 0:01 | -5.8313 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.6481 | -0.056481 | -0.056481 | -5.8313 | 9.1597e-05 | [13 empty] | 0.97674 | 1 | 0.97702 | 0.92093 | 0.84772 | 0.77349 | 0.70865 | 0.65821 | 0.62675 | 0.6095 | 0.5906 | 0.56004 | 0.49059 | 0.38302 | 0.23908 | 0.0801 | -0.095189 | -0.26231 | -0.39868 | -0.48227 | -0.54039 | -0.59263 | -0.64711 | -0.70269 | -0.75759 | -0.81624 | -0.87255 | -0.91668 | -0.94413 | -0.94993 | -0.9169 | -0.0028241 | 0.0043417 | 0.00021708 | 0.00021708 | 0 | 0 | 0.0023592 | 0.05 | 0.42033 | 0.43417 | 0.45277 | 0.47367 | 0.49032 | 0.50156 | 0.50197 | 0.48572 | 0.44859 | 0.39062 | 0.32721 | 0.26235 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.57989 | 0.56605 | 0.54744 | 0.52655 | 0.5099 | 0.49866 | 0.49825 | 0.5145 | 0.55163 | 0.60959 | 0.67301 | 0.73787 | 0.7994 | 0.85636 | 0.90653 | 0.95249 | 0.99587 | 0.93961 | 0.88459 | 0.83595 | 0.79076 | 0.74903 | 0.70939 | 0.67111 | 0.63578 | 0.6113 | 0.60139 | 0.59521 | 0.59592 | 0.60456 | 0.62786 | 0.99587 | 16 | Slope | 0.5 | 0.52663 | 0.52202 | 0.5047 | 0.48663 | 0.46997 | 0.45511 | 0.44386 | 0.43817 | 0.43943 | 0.44764 | 0.45767 | 0.46818 | 0.47758 | 0.48545 | 0.49106 | 0.49527 | 0.49862 | 0.46876 | 0.43931 | 0.41198 | 0.38581 | 0.36079 | 0.33646 | 0.31259 | 0.28971 | 0.27043 | 0.25602 | 0.24285 | 0.23197 | 0.22374 | 0.2204 | 0.52663 | 0 | 0.57989 | Slope | 1 | 0.056481 |  | 0.72042 | 0 | 0.57989 | Slope | 2 | 1 | 0 | 20 | -20 | 9.1597e-05 | 0.00017525 | 0.0023592
11 | 0:02 | -5.6481 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.3186 | -0.053186 | -0.053186 | -5.6481 | 0.00016477 | [13 empty] | 0.97702 | 1 | 0.97787 | 0.92362 | 0.85257 | 0.78151 | 0.72156 | 0.6802 | 0.66068 | 0.64433 | 0.6232 | 0.56123 | 0.45902 | 0.31327 | 0.14821 | -0.036341 | -0.21936 | -0.36866 | -0.46549 | -0.52385 | -0.5685 | -0.61326 | -0.66114 | -0.71209 | -0.76673 | -0.82484 | -0.87648 | -0.91531 | -0.93549 | -0.91999 | -0.80965 | -0.0026593 | 0.0045277 | 0.00022639 | 0.00022639 | 0 | 0 | 0.0024022 | 0.05 | 0.43417 | 0.45277 | 0.47367 | 0.49032 | 0.50156 | 0.50197 | 0.48572 | 0.44859 | 0.39062 | 0.32721 | 0.26235 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.56606 | 0.54745 | 0.52656 | 0.50991 | 0.49867 | 0.49826 | 0.51451 | 0.55164 | 0.6096 | 0.67302 | 0.73788 | 0.79941 | 0.85637 | 0.90653 | 0.9525 | 0.99586 | 0.9396 | 0.88458 | 0.83594 | 0.79075 | 0.74902 | 0.70938 | 0.6711 | 0.63577 | 0.61129 | 0.60138 | 0.5952 | 0.59591 | 0.60455 | 0.62785 | 0.68378 | 0.99586 | 15 | Slope | 0.53333 | 0.52202 | 0.51582 | 0.49774 | 0.48108 | 0.46622 | 0.45498 | 0.44928 | 0.45055 | 0.45876 | 0.46878 | 0.47929 | 0.48869 | 0.49657 | 0.50218 | 0.50639 | 0.50973 | 0.47987 | 0.45042 | 0.42309 | 0.39692 | 0.37189 | 0.34757 | 0.3237 | 0.30081 | 0.28154 | 0.26713 | 0.25396 | 0.24308 | 0.23485 | 0.23151 | 0.23904 | 0.52202 | 0 | 0.56606 | Slope | 1 | 0.053186 |  | 0.73673 | 0 | 0.56606 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00016477 | 0.00017246 | 0.0024022
12 | 0:02 | -5.3186 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.489 | -0.05489 | -0.05489 | -5.3186 | 8.5238e-05 | [13 empty] | 0.97787 | 1 | 0.97868 | 0.92645 | 0.85963 | 0.7955 | 0.74744 | 0.72089 | 0.70351 | 0.68664 | 0.63382 | 0.53808 | 0.39348 | 0.22309 | 0.029832 | -0.16414 | -0.32993 | -0.44064 | -0.51136 | -0.55615 | -0.59385 | -0.6328 | -0.67627 | -0.72553 | -0.77803 | -0.8303 | -0.87555 | -0.90625 | -0.9041 | -0.80952 | -0.61688 | -0.0027445 | 0.0047367 | 0.00023684 | 0.00023684 | 0 | 0 | 0.0024511 | 0.05 | 0.45277 | 0.47367 | 0.49032 | 0.50156 | 0.50197 | 0.48572 | 0.44859 | 0.39062 | 0.32721 | 0.26235 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.54746 | 0.52657 | 0.50992 | 0.49868 | 0.49827 | 0.51452 | 0.55165 | 0.60961 | 0.67303 | 0.73789 | 0.79942 | 0.85638 | 0.90655 | 0.95251 | 0.99585 | 0.93959 | 0.88457 | 0.83593 | 0.79074 | 0.74901 | 0.70937 | 0.67109 | 0.63576 | 0.61128 | 0.60137 | 0.59519 | 0.5959 | 0.60454 | 0.62784 | 0.68377 | 0.77046 | 0.99585 | 14 | Slope | 0.56667 | 0.51582 | 0.50886 | 0.4922 | 0.47734 | 0.46609 | 0.46039 | 0.46166 | 0.46987 | 0.4799 | 0.49041 | 0.49981 | 0.50768 | 0.51329 | 0.5175 | 0.52084 | 0.49097 | 0.46152 | 0.4342 | 0.40802 | 0.383 | 0.35868 | 0.33481 | 0.31192 | 0.29265 | 0.27824 | 0.26506 | 0.25419 | 0.24596 | 0.24261 | 0.25014 | 0.26793 | 0.52084 | 14 | 0.99585 | Slope | 0.56667 | 0.05489 |  | 0.72829 | 0 | 0.99585 | Slope | 2 | 0.56667 | 0 | 20 | -20 | 8.5238e-05 | 0.00016762 | 0.0024511
13 | 0:02 | -5.489 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.8874 | -0.058874 | -0.058874 | -5.489 | 0.00019917 | [13 empty] | 0.97868 | 1 | 0.97948 | 0.9307 | 0.87115 | 0.82025 | 0.78922 | 0.76565 | 0.74916 | 0.70155 | 0.61556 | 0.47545 | 0.30395 | 0.10338 | -0.10097 | -0.27847 | -0.40434 | -0.48649 | -0.54149 | -0.57908 | -0.61139 | -0.64649 | -0.68861 | -0.73555 | -0.78355 | -0.83012 | -0.8678 | -0.87743 | -0.79906 | -0.62302 | -0.41043 | -0.0029437 | 0.0049032 | 0.00024516 | 0.00024516 | 0 | 0 | 0.0024903 | 0.05 | 0.47367 | 0.49032 | 0.50156 | 0.50197 | 0.48572 | 0.44859 | 0.39062 | 0.32721 | 0.26235 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.52657 | 0.50993 | 0.49869 | 0.49828 | 0.51452 | 0.55165 | 0.60962 | 0.67303 | 0.7379 | 0.79943 | 0.85639 | 0.90655 | 0.95252 | 0.99584 | 0.93958 | 0.88456 | 0.83592 | 0.79073 | 0.749 | 0.70937 | 0.67108 | 0.63576 | 0.61127 | 0.60136 | 0.59518 | 0.59589 | 0.60453 | 0.62783 | 0.68376 | 0.77046 | 0.88478 | 0.99584 | 13 | Slope | 0.6 | 0.50886 | 0.50331 | 0.48845 | 0.4772 | 0.47151 | 0.47277 | 0.48099 | 0.49101 | 0.50152 | 0.51092 | 0.5188 | 0.52441 | 0.52862 | 0.53195 | 0.50208 | 0.47263 | 0.44531 | 0.41913 | 0.39411 | 0.36979 | 0.34592 | 0.32303 | 0.30376 | 0.28934 | 0.27617 | 0.2653 | 0.25707 | 0.25372 | 0.26125 | 0.27904 | 0.30604 | 0.53195 | 13 | 0.99584 | Slope | 0.6 | 0.058874 |  | 0.70857 | 0 | 0.99584 | Slope | 2 | 0.6 | 0 | 20 | -20 | 0.00019917 | 0.00016144 | 0.0024903
14 | 0:02 | -5.8874 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.145 | -0.07145 | -0.07145 | -5.8874 | 0.0006288 | [13 empty] | 0.97948 | 1 | 0.98127 | 0.93905 | 0.89314 | 0.86069 | 0.83328 | 0.81073 | 0.76378 | 0.68321 | 0.55197 | 0.38327 | 0.17914 | -0.03472 | -0.22325 | -0.35922 | -0.45337 | -0.51716 | -0.56323 | -0.59486 | -0.62339 | -0.65725 | -0.69651 | -0.74041 | -0.78341 | -0.82287 | -0.84052 | -0.7765 | -0.61771 | -0.4193 | -0.23501 | -0.0035725 | 0.0050156 | 0.00025078 | 0.00025078 | 0 | 0 | 0.002518 | 0.05 | 0.49032 | 0.50156 | 0.50197 | 0.48572 | 0.44859 | 0.39062 | 0.32721 | 0.26235 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.50993 | 0.49869 | 0.49828 | 0.51453 | 0.55166 | 0.60963 | 0.67304 | 0.73791 | 0.79944 | 0.85639 | 0.90656 | 0.95252 | 0.99584 | 0.93957 | 0.88455 | 0.83591 | 0.79072 | 0.74899 | 0.70936 | 0.67107 | 0.63575 | 0.61127 | 0.60136 | 0.59517 | 0.59588 | 0.60452 | 0.62783 | 0.68375 | 0.77045 | 0.88478 | 0.98605 | 0.99584 | 12 | Slope | 0.63333 | 0.50331 | 0.49956 | 0.48832 | 0.48262 | 0.48389 | 0.4921 | 0.50212 | 0.51264 | 0.52203 | 0.52991 | 0.53552 | 0.53973 | 0.54306 | 0.51319 | 0.48374 | 0.45642 | 0.43024 | 0.40522 | 0.3809 | 0.35702 | 0.33414 | 0.31487 | 0.30045 | 0.28728 | 0.27641 | 0.26817 | 0.26483 | 0.27236 | 0.29015 | 0.31715 | 0.33979 | 0.54306 | 12 | 0.99584 | Slope | 0.63333 | 0.07145 |  | 0.64632 | 0 | 0.99584 | Slope | 2 | 0.63333 | 0 | 20 | -20 | 0.0006288 | 0.00015506 | 0.002518
15 | 0:02 | -7.145 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -8.9076 | -0.089076 | -0.089076 | -7.145 | 0.00088134 | [13 empty] | 0.98127 | 1 | 0.98397 | 0.95185 | 0.92185 | 0.89197 | 0.86414 | 0.81071 | 0.73091 | 0.60659 | 0.44718 | 0.24243 | 0.021642 | -0.1763 | -0.31778 | -0.41677 | -0.48809 | -0.54047 | -0.57836 | -0.60497 | -0.63156 | -0.66101 | -0.69995 | -0.73992 | -0.77641 | -0.79691 | -0.74308 | -0.59971 | -0.41504 | -0.24183 | -0.094293 | -0.0044538 | 0.0050197 | 0.00025098 | 0.00025098 | 0 | 0 | 0.0025191 | 0.05 | 0.50156 | 0.50197 | 0.48572 | 0.44859 | 0.39062 | 0.32721 | 0.26235 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.49869 | 0.49828 | 0.51453 | 0.55166 | 0.60963 | 0.67304 | 0.73791 | 0.79944 | 0.85639 | 0.90656 | 0.95252 | 0.99584 | 0.93957 | 0.88455 | 0.83591 | 0.79072 | 0.74899 | 0.70936 | 0.67107 | 0.63575 | 0.61127 | 0.60136 | 0.59517 | 0.59588 | 0.60452 | 0.62783 | 0.68375 | 0.77045 | 0.88478 | 0.98605 | 0.85222 | 0.99584 | 11 | Slope | 0.66667 | 0.49956 | 0.49943 | 0.49373 | 0.495 | 0.50321 | 0.51324 | 0.52375 | 0.53315 | 0.54102 | 0.54663 | 0.55084 | 0.55417 | 0.5243 | 0.49485 | 0.46753 | 0.44135 | 0.41633 | 0.39201 | 0.36814 | 0.34525 | 0.32598 | 0.31156 | 0.29839 | 0.28752 | 0.27929 | 0.27594 | 0.28347 | 0.30126 | 0.32826 | 0.35091 | 0.29519 | 0.55417 | 11 | 0.99584 | Slope | 0.66667 | 0.089076 |  | 0.55907 | 0 | 0.99584 | Slope | 2 | 0.66667 | 0 | 20 | -20 | 0.00088134 | 0.00014992 | 0.0025191
16 | 0:02 | -8.9076 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -10.9315 | -0.10931 | -0.10931 | -8.9076 | 0.0010119 | [13 empty] | 0.98397 | 1 | 0.98791 | 0.96656 | 0.93717 | 0.90438 | 0.84646 | 0.75995 | 0.64004 | 0.4895 | 0.29049 | 0.064455 | -0.14099 | -0.2842 | -0.38259 | -0.45464 | -0.51237 | -0.5545 | -0.58552 | -0.60967 | -0.63049 | -0.66413 | -0.70145 | -0.73657 | -0.75666 | -0.71026 | -0.57991 | -0.40676 | -0.24299 | -0.1036 | 0.019006 | -0.0054657 | 0.0048572 | 0.00024286 | 0.00024286 | 0 | 0 | 0.0024658 | 0.05 | 0.50197 | 0.48572 | 0.44859 | 0.39062 | 0.32721 | 0.26235 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.49828 | 0.51452 | 0.55165 | 0.60962 | 0.67303 | 0.7379 | 0.79943 | 0.85639 | 0.90655 | 0.95251 | 0.99585 | 0.93958 | 0.88456 | 0.83592 | 0.79073 | 0.749 | 0.70937 | 0.67108 | 0.63576 | 0.61127 | 0.60137 | 0.59518 | 0.59589 | 0.60453 | 0.62783 | 0.68376 | 0.77046 | 0.88479 | 0.98604 | 0.85222 | 0.71391 | 0.99585 | 10 | Slope | 0.7 | 0.49943 | 0.50484 | 0.50611 | 0.51432 | 0.52434 | 0.53485 | 0.54425 | 0.55213 | 0.55774 | 0.56195 | 0.56528 | 0.53542 | 0.50597 | 0.47864 | 0.45247 | 0.42744 | 0.40312 | 0.37925 | 0.35636 | 0.33709 | 0.32268 | 0.30951 | 0.29863 | 0.2904 | 0.28706 | 0.29459 | 0.31237 | 0.33937 | 0.36201 | 0.30629 | 0.24908 | 0.56528 | 10 | 0.99585 | Slope | 0.7 | 0.10931 |  | 0.45889 | 0 | 0.99585 | Slope | 2 | 0.7 | 0 | 20 | -20 | 0.0010119 | 0.00014772 | 0.0024658
17 | 0:03 | -10.9315 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -12.329 | -0.12329 | -0.12329 | -10.9315 | 0.00069878 | [13 empty] | 0.98791 | 1 | 0.991 | 0.96784 | 0.93192 | 0.87046 | 0.77956 | 0.65717 | 0.51378 | 0.31912 | 0.092049 | -0.12106 | -0.26261 | -0.35597 | -0.42362 | -0.48089 | -0.52668 | -0.56043 | -0.58879 | -0.60582 | -0.63702 | -0.67261 | -0.70787 | -0.73077 | -0.69025 | -0.57066 | -0.40527 | -0.24709 | -0.11273 | 0.0056344 | 0.11155 | -0.0061645 | 0.0044859 | 0.0002243 | 0.0002243 | 0 | 0 | 0.002323 | 0.05 | 0.48572 | 0.44859 | 0.39062 | 0.32721 | 0.26235 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.5145 | 0.55163 | 0.6096 | 0.67301 | 0.73788 | 0.79941 | 0.85637 | 0.90653 | 0.9525 | 0.99587 | 0.9396 | 0.88458 | 0.83594 | 0.79075 | 0.74902 | 0.70939 | 0.6711 | 0.63578 | 0.61129 | 0.60138 | 0.5952 | 0.59591 | 0.60455 | 0.62785 | 0.68378 | 0.77048 | 0.8848 | 0.98602 | 0.8522 | 0.71389 | 0.5751 | 0.99587 | 9 | Slope | 0.73333 | 0.50483 | 0.51721 | 0.52542 | 0.53545 | 0.54596 | 0.55536 | 0.56323 | 0.56884 | 0.57305 | 0.5764 | 0.54653 | 0.51708 | 0.48976 | 0.46358 | 0.43856 | 0.41424 | 0.39037 | 0.36748 | 0.34821 | 0.33379 | 0.32062 | 0.30975 | 0.30152 | 0.29817 | 0.3057 | 0.32349 | 0.35049 | 0.37312 | 0.3174 | 0.26018 | 0.20281 | 0.5764 | 9 | 0.99587 | Slope | 0.73333 | 0.12329 |  | 0.38971 | 0 | 0.99587 | Slope | 2 | 0.73333 | 0 | 20 | -20 | 0.00069878 | 0.00015012 | 0.002323
18 | 0:03 | -12.329 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -11.4961 | -0.11496 | -0.11496 | -12.329 | 0.00041645 | [13 empty] | 0.991 | 1 | 0.98841 | 0.95674 | 0.89525 | 0.8013 | 0.67935 | 0.53513 | 0.34322 | 0.11223 | -0.10703 | -0.24813 | -0.33369 | -0.39352 | -0.44641 | -0.49114 | -0.52816 | -0.56112 | -0.58303 | -0.61874 | -0.65749 | -0.69579 | -0.72625 | -0.69972 | -0.59147 | -0.43119 | -0.27323 | -0.13812 | -0.019066 | 0.0884 | 0.18443 | -0.0057481 | 0.0039062 | 0.00019531 | 0.00019531 | 0 | 0 | 0.0020738 | 0.05 | 0.44859 | 0.39062 | 0.32721 | 0.26235 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.5516 | 0.60957 | 0.67298 | 0.73785 | 0.79938 | 0.85634 | 0.9065 | 0.95247 | 0.99589 | 0.93963 | 0.88461 | 0.83597 | 0.79078 | 0.74905 | 0.70942 | 0.67113 | 0.63581 | 0.61132 | 0.60141 | 0.59523 | 0.59594 | 0.60458 | 0.62788 | 0.68381 | 0.77051 | 0.88483 | 0.98599 | 0.85217 | 0.71386 | 0.57507 | 0.43922 | 0.99589 | 8 | Slope | 0.76667 | 0.5172 | 0.53652 | 0.54655 | 0.55706 | 0.56646 | 0.57434 | 0.57995 | 0.58416 | 0.58752 | 0.55765 | 0.5282 | 0.50088 | 0.4747 | 0.44968 | 0.42536 | 0.40149 | 0.3786 | 0.35933 | 0.34492 | 0.33174 | 0.32087 | 0.31264 | 0.30929 | 0.31682 | 0.33461 | 0.36161 | 0.38422 | 0.3285 | 0.27129 | 0.21391 | 0.15752 | 0.58752 | 8 | 0.99589 | Slope | 0.76667 | 0.11496 |  | 0.43094 | 0 | 0.99589 | Slope | 2 | 0.76667 | 0 | 20 | -20 | 0.00041645 | 0.000158 | 0.0020738
19 | 0:03 | -11.4961 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -10.2902 | -0.1029 | -0.1029 | -11.4961 | 0.00060299 | [13 empty] | 0.98841 | 1 | 0.98386 | 0.93183 | 0.83949 | 0.71628 | 0.57327 | 0.37942 | 0.14805 | -0.078991 | -0.22407 | -0.30689 | -0.35806 | -0.40341 | -0.4436 | -0.47975 | -0.51836 | -0.54716 | -0.59391 | -0.64207 | -0.68793 | -0.72838 | -0.72144 | -0.63421 | -0.48379 | -0.32711 | -0.18847 | -0.06525 | 0.046503 | 0.14717 | 0.23656 | -0.0051451 | 0.0032721 | 0.00016361 | 0.00016361 | 0 | 0 | 0.001801 | 0.05 | 0.39062 | 0.32721 | 0.26235 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.60954 | 0.67295 | 0.73782 | 0.79935 | 0.85631 | 0.90647 | 0.95244 | 0.99593 | 0.93966 | 0.88464 | 0.836 | 0.79081 | 0.74908 | 0.70945 | 0.67116 | 0.63584 | 0.61135 | 0.60145 | 0.59526 | 0.59597 | 0.60461 | 0.62791 | 0.68384 | 0.77054 | 0.88486 | 0.98596 | 0.85214 | 0.71383 | 0.57504 | 0.43919 | 0.31312 | 0.99593 | 7 | Slope | 0.8 | 0.53651 | 0.55765 | 0.56816 | 0.57756 | 0.58544 | 0.59105 | 0.59526 | 0.59864 | 0.56878 | 0.53933 | 0.512 | 0.48583 | 0.4608 | 0.43648 | 0.41261 | 0.38972 | 0.37045 | 0.35604 | 0.34287 | 0.33199 | 0.32376 | 0.32042 | 0.32795 | 0.34573 | 0.37273 | 0.39532 | 0.3396 | 0.28239 | 0.22501 | 0.16862 | 0.11549 | 0.59864 | 7 | 0.99593 | Slope | 0.8 | 0.1029 |  | 0.49064 | 0 | 0.99593 | Slope | 2 | 0.8 | 0 | 20 | -20 | 0.00060299 | 0.00017101 | 0.001801
20 | 0:03 | -10.2902 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -8.1304 | -0.081304 | -0.081304 | -10.2902 | 0.0010799 | [13 empty] | 0.98386 | 1 | 0.97384 | 0.89617 | 0.77682 | 0.63233 | 0.43907 | 0.20211 | -0.029138 | -0.18129 | -0.2664 | -0.31398 | -0.35048 | -0.38247 | -0.41387 | -0.45349 | -0.49049 | -0.55086 | -0.61645 | -0.67763 | -0.73409 | -0.7509 | -0.69196 | -0.56211 | -0.41202 | -0.27142 | -0.14147 | -0.022095 | 0.085962 | 0.18313 | 0.26529 | -0.0040652 | 0.0026235 | 0.00013117 | 0.00013117 | 0 | 0 | 0.0015254 | 0.05 | 0.32721 | 0.26235 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.67292 | 0.73779 | 0.79932 | 0.85628 | 0.90644 | 0.9524 | 0.99596 | 0.93969 | 0.88467 | 0.83603 | 0.79084 | 0.74911 | 0.70948 | 0.67119 | 0.63587 | 0.61139 | 0.60148 | 0.59529 | 0.596 | 0.60464 | 0.62795 | 0.68387 | 0.77057 | 0.8849 | 0.98593 | 0.8521 | 0.7138 | 0.575 | 0.43916 | 0.31309 | 0.2006 | 0.99596 | 6 | Slope | 0.83333 | 0.55764 | 0.57926 | 0.58866 | 0.59654 | 0.60215 | 0.60636 | 0.60976 | 0.5799 | 0.55045 | 0.52312 | 0.49695 | 0.47193 | 0.4476 | 0.42373 | 0.40085 | 0.38157 | 0.36716 | 0.35399 | 0.34311 | 0.33488 | 0.33154 | 0.33907 | 0.35686 | 0.38385 | 0.40642 | 0.3507 | 0.29349 | 0.23611 | 0.17972 | 0.12659 | 0.077976 | 0.60976 | 6 | 0.99596 | Slope | 0.83333 | 0.081304 |  | 0.59755 | 0 | 0.99596 | Slope | 2 | 0.83333 | 0 | 20 | -20 | 0.0010799 | 0.00018776 | 0.0015254
21 | 0:03 | -8.1304 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -6.4699 | -0.064699 | -0.064699 | -8.1304 | 0.00083025 | [13 empty] | 0.97384 | 1 | 0.96314 | 0.86542 | 0.72777 | 0.54201 | 0.31275 | 0.076594 | -0.082341 | -0.17581 | -0.2274 | -0.26147 | -0.28457 | -0.30808 | -0.3463 | -0.38905 | -0.46244 | -0.54754 | -0.63319 | -0.71668 | -0.77244 | -0.75475 | -0.66145 | -0.53426 | -0.40062 | -0.26902 | -0.14246 | -0.025853 | 0.080564 | 0.1726 | 0.25288 | -0.0032349 | 0.0020081 | 0.00010041 | 0.00010041 | 0 | 0 | 0.0013114 | 0.05 | 0.26235 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.73775 | 0.79929 | 0.85624 | 0.90641 | 0.95237 | 0.99599 | 0.93972 | 0.8847 | 0.83606 | 0.79087 | 0.74914 | 0.70951 | 0.67122 | 0.6359 | 0.61142 | 0.60151 | 0.59533 | 0.59604 | 0.60467 | 0.62798 | 0.6839 | 0.7706 | 0.88493 | 0.9859 | 0.85207 | 0.71376 | 0.57497 | 0.43913 | 0.31306 | 0.20057 | 0.10083 | 0.99599 | 5 | Slope | 0.86667 | 0.57925 | 0.59976 | 0.60764 | 0.61325 | 0.61746 | 0.62089 | 0.59102 | 0.56157 | 0.53424 | 0.50807 | 0.48305 | 0.45873 | 0.43485 | 0.41197 | 0.39269 | 0.37828 | 0.36511 | 0.35423 | 0.346 | 0.34266 | 0.35019 | 0.36798 | 0.39498 | 0.41752 | 0.3618 | 0.30459 | 0.24721 | 0.19082 | 0.13769 | 0.089077 | 0.044721 | 0.62089 | 5 | 0.99599 | Slope | 0.86667 | 0.064699 |  | 0.67974 | 0 | 0.99599 | Slope | 2 | 0.86667 | 0 | 20 | -20 | 0.00083025 | 0.00020675 | 0.0013114
22 | 0:04 | -6.4699 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.6468 | -0.046468 | -0.046468 | -6.4699 | 0.00091154 | [13 empty] | 0.96314 | 1 | 0.95561 | 0.84488 | 0.67411 | 0.45886 | 0.23199 | 0.063317 | -0.038578 | -0.099359 | -0.13789 | -0.15859 | -0.17291 | -0.20376 | -0.24659 | -0.32775 | -0.42902 | -0.53882 | -0.65631 | -0.75869 | -0.79515 | -0.74953 | -0.66095 | -0.55198 | -0.42948 | -0.30326 | -0.18068 | -0.066131 | 0.035419 | 0.12611 | 0.2071 | -0.0023234 | 0.0014386 | 7.1928e-05 | 7.1928e-05 | 0 | 0 | 0.0011506 | 0.05 | 0.20081 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.79926 | 0.85622 | 0.90638 | 0.95234 | 0.99602 | 0.93975 | 0.88473 | 0.83609 | 0.7909 | 0.74917 | 0.70954 | 0.67125 | 0.63593 | 0.61144 | 0.60154 | 0.59535 | 0.59606 | 0.6047 | 0.62801 | 0.68393 | 0.77063 | 0.88496 | 0.98587 | 0.85204 | 0.71374 | 0.57494 | 0.4391 | 0.31303 | 0.20054 | 0.1008 | 0.013198 | 0.99602 | 4 | Slope | 0.9 | 0.59975 | 0.61874 | 0.62435 | 0.62856 | 0.63201 | 0.60214 | 0.57269 | 0.54536 | 0.51919 | 0.49417 | 0.46985 | 0.44597 | 0.42309 | 0.40381 | 0.3894 | 0.37623 | 0.36535 | 0.35712 | 0.35378 | 0.36131 | 0.3791 | 0.4061 | 0.42862 | 0.3729 | 0.31569 | 0.25831 | 0.20192 | 0.14879 | 0.10018 | 0.055823 | 0.01551 | 0.63201 | 4 | 0.99602 | Slope | 0.9 | 0.046468 |  | 0.76998 | 0 | 0.99602 | Slope | 2 | 0.9 | 0 | 20 | -20 | 0.00091154 | 0.0002266 | 0.0011506
23 | 0:04 | -4.6468 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -3.4866 | -0.034866 | -0.034866 | -4.6468 | 0.00058011 | [13 empty] | 0.95561 | 1 | 0.95107 | 0.82148 | 0.63291 | 0.42396 | 0.25566 | 0.14002 | 0.069312 | 0.021325 | -0.0047051 | -0.017676 | -0.04011 | -0.076676 | -0.15469 | -0.26167 | -0.38691 | -0.53245 | -0.68547 | -0.78227 | -0.79708 | -0.7572 | -0.68802 | -0.59385 | -0.48183 | -0.36423 | -0.24749 | -0.14011 | -0.041929 | 0.047808 | 0.12582 | -0.0017433 | 0.00093691 | 4.6846e-05 | 4.6846e-05 | 0 | 0 | 0.0010624 | 0.05 | 0.14386 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.85619 | 0.90636 | 0.95232 | 0.99604 | 0.93978 | 0.88476 | 0.83612 | 0.79093 | 0.7492 | 0.70956 | 0.67128 | 0.63595 | 0.61147 | 0.60156 | 0.59538 | 0.59609 | 0.60473 | 0.62803 | 0.68396 | 0.77065 | 0.88498 | 0.98584 | 0.85202 | 0.71371 | 0.57492 | 0.43907 | 0.31301 | 0.20051 | 0.10078 | 0.013173 | 0 | 0.99604 | 3 | Slope | 0.93333 | 0.61873 | 0.63545 | 0.63966 | 0.64313 | 0.61326 | 0.58381 | 0.55648 | 0.53031 | 0.50529 | 0.48097 | 0.45709 | 0.43421 | 0.41493 | 0.40052 | 0.38735 | 0.37647 | 0.36824 | 0.3649 | 0.37243 | 0.39022 | 0.41722 | 0.43973 | 0.38401 | 0.32679 | 0.26942 | 0.21302 | 0.15989 | 0.11128 | 0.066925 | 0.026613 | 0.011111 | 0.64313 | 3 | 0.99604 | Slope | 0.93333 | 0.034866 |  | 0.82742 | 0 | 0.99604 | Slope | 2 | 0.93333 | 0 | 20 | -20 | 0.00058011 | 0.00024634 | 0.0010624
24 | 0:04 | -3.4866 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -3.3387 | -0.033387 | -0.033387 | -3.4866 | 7.3942e-05 | [13 empty] | 0.95107 | 1 | 0.94364 | 0.80397 | 0.62196 | 0.46037 | 0.34073 | 0.25642 | 0.1997 | 0.16442 | 0.14594 | 0.12516 | 0.096958 | 0.028546 | -0.072191 | -0.20059 | -0.36216 | -0.55532 | -0.71355 | -0.79042 | -0.80644 | -0.78234 | -0.72748 | -0.64599 | -0.54581 | -0.43764 | -0.33083 | -0.22949 | -0.13468 | -0.049522 | 0.027846 | -0.0016693 | 0.00047728 | 2.3864e-05 | 2.3864e-05 | 0 | 0 | 0.0010209 | 0.05 | 0.093691 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.90633 | 0.9523 | 0.99607 | 0.9398 | 0.88478 | 0.83614 | 0.79095 | 0.74922 | 0.70959 | 0.6713 | 0.63598 | 0.61149 | 0.60159 | 0.5954 | 0.59611 | 0.60475 | 0.62805 | 0.68398 | 0.77068 | 0.885 | 0.98582 | 0.852 | 0.71369 | 0.5749 | 0.43905 | 0.31298 | 0.20049 | 0.10075 | 0.01315 | 0 | 0 | 0.99607 | 2 | Slope | 0.96667 | 0.63544 | 0.65077 | 0.65424 | 0.62438 | 0.59493 | 0.5676 | 0.54143 | 0.51641 | 0.49208 | 0.46821 | 0.44533 | 0.42605 | 0.41164 | 0.39847 | 0.38759 | 0.37936 | 0.37602 | 0.38355 | 0.40134 | 0.42833 | 0.45083 | 0.39511 | 0.3379 | 0.28052 | 0.22413 | 0.17099 | 0.12239 | 0.078029 | 0.037717 | 0.022222 | 0.011111 | 0.65424 | 2 | 0.99607 | Slope | 0.96667 | 0.033387 |  | 0.83474 | 0 | 0.99607 | Slope | 2 | 0.96667 | 0 | 20 | -20 | 7.3942e-05 | 0.00026528 | 0.0010209
25 | 0:04 | -3.3387 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -3.3012 | -0.033012 | -0.033012 | -3.3387 | 1.8738e-05 | [13 empty] | 0.94364 | 1 | 0.94203 | 0.81053 | 0.67285 | 0.56116 | 0.47594 | 0.40879 | 0.36699 | 0.34068 | 0.31337 | 0.28498 | 0.2218 | 0.12924 | 0.0062667 | -0.16443 | -0.39673 | -0.61555 | -0.75687 | -0.82752 | -0.85119 | -0.83683 | -0.79201 | -0.72192 | -0.63211 | -0.53572 | -0.4372 | -0.34148 | -0.25343 | -0.1708 | -0.095165 | -0.0016506 | -3.9104e-05 | -1.9552e-06 | -1.9552e-06 | 0 | 0 | 0.0010122 | 0.05 | 0.047728 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.95227 | 0.99609 | 0.93983 | 0.88481 | 0.83617 | 0.79098 | 0.74924 | 0.70961 | 0.67133 | 0.636 | 0.61152 | 0.60161 | 0.59543 | 0.59614 | 0.60478 | 0.62808 | 0.68401 | 0.7707 | 0.88503 | 0.9858 | 0.85197 | 0.71366 | 0.57487 | 0.43902 | 0.31296 | 0.20046 | 0.10073 | 0.013124 | 0 | 0 | 0 | 0.99609 | 1 | Slope | 1 | 0.65076 | 0.66536 | 0.6355 | 0.60605 | 0.57872 | 0.55255 | 0.52753 | 0.5032 | 0.47933 | 0.45645 | 0.43717 | 0.42276 | 0.40959 | 0.39871 | 0.39048 | 0.38714 | 0.39467 | 0.41246 | 0.43945 | 0.46193 | 0.40621 | 0.349 | 0.29162 | 0.23523 | 0.1821 | 0.13349 | 0.089131 | 0.048819 | 0.033333 | 0.022222 | 0.011111 | 0.66536 | 1 | 0.99609 | Slope | 1 | 0.033012 |  | 0.83659 | 0 | 0.99609 | Slope | 2 | 1 | 0 | 20 | -20 | 1.8738e-05 | 0.00028294 | 0.0010122
26 | 0:04 | -3.3012 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.7638 | -0.027638 | -0.027638 | -3.3012 | 0.00026869 | [13 empty] | 0.94203 | 1 | 0.94765 | 0.85361 | 0.7638 | 0.68833 | 0.62319 | 0.57395 | 0.54337 | 0.51038 | 0.47654 | 0.412 | 0.32452 | 0.21008 | 0.042162 | -0.21507 | -0.48719 | -0.68765 | -0.81185 | -0.87977 | -0.90619 | -0.89738 | -0.86151 | -0.80116 | -0.72414 | -0.63798 | -0.54756 | -0.46118 | -0.37807 | -0.29948 | -0.22664 | -0.0013819 | -0.00060176 | -3.0088e-05 | -3.0088e-05 | 0 | 0 | 0.0010329 | 0.05 | -0.0039104 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.99612 | 0.93985 | 0.88484 | 0.83619 | 0.791 | 0.74927 | 0.70964 | 0.67135 | 0.63603 | 0.61155 | 0.60164 | 0.59546 | 0.59617 | 0.6048 | 0.62811 | 0.68403 | 0.77073 | 0.88506 | 0.98577 | 0.85194 | 0.71363 | 0.57484 | 0.43899 | 0.31293 | 0.20043 | 0.1007 | 0.013096 | 0 | 0 | 0 | 0 | 0.99612 | 0 | Slope | 1 | 0.66537 | 0.64662 | 0.61717 | 0.58984 | 0.56367 | 0.53865 | 0.51432 | 0.49045 | 0.46757 | 0.44829 | 0.43388 | 0.42071 | 0.40983 | 0.4016 | 0.39826 | 0.40579 | 0.42358 | 0.45057 | 0.47303 | 0.41731 | 0.3601 | 0.30273 | 0.24633 | 0.1932 | 0.14459 | 0.10023 | 0.059921 | 0.044444 | 0.033333 | 0.022222 | 0.011111 | 0.66537 | 0 | 0.99612 | Slope | 1 | 0.027638 |  | 0.86319 | 0 | 0.99612 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00026869 | 0.00029878 | 0.0010329
27 | 0:04 | -2.7638 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -1.1566 | -0.011566 | -0.011566 | -2.7638 | 0.00080363 | [13 empty] | 0.94765 | 1 | 0.96616 | 0.90846 | 0.85103 | 0.79588 | 0.74918 | 0.71311 | 0.67989 | 0.64329 | 0.57749 | 0.49185 | 0.38532 | 0.22835 | -0.030592 | -0.33257 | -0.58053 | -0.75009 | -0.85831 | -0.91988 | -0.94542 | -0.94116 | -0.91224 | -0.86292 | -0.79627 | -0.71943 | -0.63988 | -0.56052 | -0.48355 | -0.40986 | -0.34488 | -0.00057828 | -0.0011519 | -5.7597e-05 | -5.7597e-05 | 0 | 0 | 0.0010852 | 0.05 | -0.060176 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.93988 | 0.88486 | 0.83622 | 0.79103 | 0.7493 | 0.70967 | 0.67138 | 0.63606 | 0.61157 | 0.60167 | 0.59548 | 0.59619 | 0.60483 | 0.62814 | 0.68406 | 0.77076 | 0.88509 | 0.98574 | 0.85191 | 0.71361 | 0.57481 | 0.43897 | 0.3129 | 0.20041 | 0.10067 | 0.013069 | 0 | 0 | 0 | 0 | 0 | 0.98574 | 17 | Slope | 0.46667 | 0.64663 | 0.62829 | 0.60096 | 0.57479 | 0.54977 | 0.52545 | 0.50157 | 0.47869 | 0.45941 | 0.445 | 0.43183 | 0.42095 | 0.41272 | 0.40938 | 0.41691 | 0.4347 | 0.4617 | 0.48414 | 0.42842 | 0.3712 | 0.31383 | 0.25743 | 0.2043 | 0.15569 | 0.11134 | 0.071023 | 0.055556 | 0.044444 | 0.033333 | 0.022222 | 0.011111 | 0.64663 | 0 | 0.93988 | Slope | 1 | 0.011566 |  | 0.94275 | 0 | 0.93988 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00080363 | 0.00031235 | 0.0010852
28 | 0:05 | -1.1566 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 0.0093071 | 9.3071e-05 | 9.3071e-05 | -1.1566 | 0.00058294 | [13 empty] | 0.96616 | 1 | 0.97808 | 0.94014 | 0.89816 | 0.85809 | 0.82294 | 0.78534 | 0.74696 | 0.68606 | 0.60389 | 0.50309 | 0.35775 | 0.10783 | -0.19673 | -0.46724 | -0.66544 | -0.79938 | -0.88667 | -0.93657 | -0.95763 | -0.95302 | -0.92837 | -0.88532 | -0.82632 | -0.75909 | -0.68739 | -0.6154 | -0.54487 | -0.47919 | -0.42061 | 4.6536e-06 | -0.0016384 | -8.1918e-05 | -8.1918e-05 | 0 | 0 | 0.0011954 | 0.05 | -0.11519 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.88489 | 0.83625 | 0.79106 | 0.74932 | 0.70969 | 0.67141 | 0.63608 | 0.6116 | 0.60169 | 0.59551 | 0.59622 | 0.60486 | 0.62816 | 0.68409 | 0.77078 | 0.88511 | 0.98572 | 0.85189 | 0.71358 | 0.57479 | 0.43894 | 0.31288 | 0.20038 | 0.10065 | 0.013044 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98572 | 16 | Slope | 0.5 | 0.6283 | 0.61208 | 0.58591 | 0.56089 | 0.53656 | 0.51269 | 0.48981 | 0.47053 | 0.45612 | 0.44295 | 0.43207 | 0.42384 | 0.4205 | 0.42803 | 0.44582 | 0.47281 | 0.49524 | 0.43952 | 0.38231 | 0.32493 | 0.26854 | 0.2154 | 0.16679 | 0.12244 | 0.082126 | 0.066667 | 0.055556 | 0.044444 | 0.033333 | 0.022222 | 0.011111 | 0.6283 | 0 | 0.88489 | Slope | 1 | 9.3071e-05 |  | 0.99954 | 0.83415 | 0.88489 | Slope | 2 | 1 | 0.83415 | 20 | -20 | 0.00058294 | 0.00032336 | 0.0011954
29 | 0:05 | 0.0093071 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 0.81819 | 0.0081819 | 0.0081819 | 0.0093071 | 0.00040444 | [13 empty] | 0.97808 | 1 | 0.98447 | 0.95575 | 0.92424 | 0.89298 | 0.85609 | 0.81249 | 0.75459 | 0.67902 | 0.5828 | 0.44391 | 0.20149 | -0.099747 | -0.37487 | -0.58678 | -0.73708 | -0.84046 | -0.90778 | -0.94581 | -0.95949 | -0.95236 | -0.92842 | -0.88861 | -0.8355 | -0.77423 | -0.70876 | -0.64259 | -0.57871 | -0.51863 | -0.4641 | 0.0004091 | -0.0020903 | -0.00010451 | -0.00010451 | 0 | 0 | 0.0013375 | 0.05 | -0.16384 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.83627 | 0.79108 | 0.74935 | 0.70972 | 0.67143 | 0.63611 | 0.61162 | 0.60171 | 0.59553 | 0.59624 | 0.60488 | 0.62818 | 0.68411 | 0.7708 | 0.88513 | 0.98569 | 0.85187 | 0.71356 | 0.57477 | 0.43892 | 0.31285 | 0.20036 | 0.10062 | 0.013022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98569 | 15 | Slope | 0.53333 | 0.61209 | 0.59703 | 0.572 | 0.54768 | 0.52381 | 0.50092 | 0.48165 | 0.46724 | 0.45407 | 0.44319 | 0.43496 | 0.43162 | 0.43915 | 0.45693 | 0.48393 | 0.50634 | 0.45062 | 0.39341 | 0.33603 | 0.27964 | 0.22651 | 0.1779 | 0.13354 | 0.093229 | 0.077778 | 0.066667 | 0.055556 | 0.044444 | 0.033333 | 0.022222 | 0.011111 | 0.61209 | 0 | 0.83627 | Slope | 1 | 0.0081819 |  | 0.9595 | 0 | 0.83627 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00040444 | 0.00033157 | 0.0013375
30 | 0:05 | 0.81819 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.2351 | 0.012351 | 0.012351 | 0.81819 | 0.00020844 |  | Hourly |  |  |  | Hourly |  |  |  | Hourly |  |  |  | 0.98447 | 1 | 0.98763 | 0.96512 | 0.93975 | 0.90721 | 0.86452 | 0.80557 | 0.73431 | 0.64481 | 0.51132 | 0.27444 | -0.024192 | -0.30137 | -0.51802 | -0.67825 | -0.79401 | -0.87383 | -0.92535 | -0.95221 | -0.95898 | -0.94877 | -0.92438 | -0.88647 | -0.83664 | -0.77944 | -0.71822 | -0.65681 | -0.5971 | -0.54027 | -0.4887 | 0.00061753 | -0.0025076 | -0.00012538 | -0.00012538 | 0 | 0 | 0.0014848 | 0.05 | -0.20903 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.7911 | 0.74937 | 0.70974 | 0.67145 | 0.63613 | 0.61164 | 0.60173 | 0.59555 | 0.59626 | 0.6049 | 0.6282 | 0.68413 | 0.77083 | 0.88515 | 0.98567 | 0.85185 | 0.71354 | 0.57475 | 0.4389 | 0.31283 | 0.20034 | 0.1006 | 0.013001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98567 | 14 | Slope | 0.56667 | 0.59703 | 0.58312 | 0.5588 | 0.53493 | 0.51204 | 0.49277 | 0.47836 | 0.46518 | 0.45431 | 0.44608 | 0.44273 | 0.45027 | 0.46805 | 0.49505 | 0.51745 | 0.46173 | 0.40451 | 0.34714 | 0.29074 | 0.23761 | 0.189 | 0.14465 | 0.10433 | 0.088889 | 0.077778 | 0.066667 | 0.055556 | 0.044444 | 0.033333 | 0.022222 | 0.011111 | 0.59703 | 0 | 0.7911 | Slope | 1 | 0.012351 |  | 0.93886 | 0 | 0.7911 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00020844 | 0.0003365 | 0.0014848
31 | 0:05 | 1.2351 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.6519 | 0.016519 | 0.016519 | 1.2351 | 0.00020844 |  | Score | 0.88446 |  |  | Score | 0.86185 |  |  | Score | 0.0031543 |  |  | 0.98763 | 1 | 0.99009 | 0.97178 | 0.94579 | 0.90812 | 0.85246 | 0.78152 | 0.6966 | 0.57053 | 0.33922 | 0.04217 | -0.23729 | -0.45794 | -0.62288 | -0.74738 | -0.83792 | -0.90007 | -0.93841 | -0.95609 | -0.95754 | -0.94473 | -0.91968 | -0.88278 | -0.83517 | -0.78076 | -0.72291 | -0.66464 | -0.60748 | -0.55303 | -0.4937 | 0.00082597 | -0.0029039 | -0.00014519 | -0.00014519 | 0 | 0 | 0.0016288 | 0.05 | -0.25076 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.74939 | 0.70976 | 0.67147 | 0.63615 | 0.61166 | 0.60175 | 0.59557 | 0.59628 | 0.60492 | 0.62822 | 0.68415 | 0.77085 | 0.88517 | 0.98565 | 0.85183 | 0.71352 | 0.57473 | 0.43888 | 0.31281 | 0.20032 | 0.10058 | 0.012981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98565 | 13 | Slope | 0.6 | 0.58313 | 0.56992 | 0.54605 | 0.52316 | 0.50389 | 0.48947 | 0.4763 | 0.46543 | 0.4572 | 0.45385 | 0.46138 | 0.47917 | 0.50617 | 0.52855 | 0.47283 | 0.41562 | 0.35824 | 0.30185 | 0.24872 | 0.20011 | 0.15575 | 0.11544 | 0.1 | 0.088889 | 0.077778 | 0.066667 | 0.055556 | 0.044444 | 0.033333 | 0.022222 | 0.011111 | 0.58313 | 0 | 0.74939 | Slope | 1 | 0.016519 |  | 0.91823 | 0 | 0.74939 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00020844 | 0.00033784 | 0.0016288
32 | 0:05 | 1.6519 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.0472 | 0.020472 | 0.020472 | 1.6519 | 0.00019761 | [13 empty] | 0.99009 | 1 | 0.99174 | 0.9724 | 0.94088 | 0.89151 | 0.82435 | 0.74004 | 0.61872 | 0.39335 | 0.097592 | -0.1843 | -0.40815 | -0.57632 | -0.70467 | -0.80231 | -0.8732 | -0.92019 | -0.94709 | -0.95751 | -0.95448 | -0.93903 | -0.91315 | -0.87667 | -0.83047 | -0.77809 | -0.72244 | -0.66608 | -0.61071 | -0.54849 | -0.47597 | 0.0010236 | -0.0032868 | -0.00016434 | -0.00016434 | 0 | 0 | 0.0017741 | 0.05 | -0.29039 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.70978 | 0.67149 | 0.63617 | 0.61168 | 0.60177 | 0.59559 | 0.5963 | 0.60494 | 0.62824 | 0.68417 | 0.77086 | 0.88519 | 0.98563 | 0.85181 | 0.7135 | 0.57471 | 0.43886 | 0.31279 | 0.2003 | 0.10057 | 0.012962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98563 | 12 | Slope | 0.63333 | 0.56993 | 0.55716 | 0.53428 | 0.515 | 0.50059 | 0.48742 | 0.47654 | 0.46831 | 0.46497 | 0.4725 | 0.49029 | 0.51729 | 0.53966 | 0.48394 | 0.42672 | 0.36935 | 0.31295 | 0.25982 | 0.21121 | 0.16686 | 0.12654 | 0.11111 | 0.1 | 0.088889 | 0.077778 | 0.066667 | 0.055556 | 0.044444 | 0.033333 | 0.022222 | 0.011111 | 0.56993 | 0 | 0.70978 | Slope | 1 | 0.020472 |  | 0.89867 | 0 | 0.70978 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00019761 | 0.00033543 | 0.0017741
33 | 0:05 | 2.0472 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.3689 | 0.023689 | 0.023689 | 2.0472 | 0.00016087 |  | Weight | 0.33333 |  |  | Weight | 0.33333 |  |  | Weight | 0.33333 |  |  | 0.99174 | 1 | 0.9904 | 0.96567 | 0.9239 | 0.86356 | 0.78329 | 0.66364 | 0.44346 | 0.15041 | -0.13425 | -0.36246 | -0.53452 | -0.66654 | -0.76823 | -0.84566 | -0.90048 | -0.93486 | -0.9533 | -0.95811 | -0.951 | -0.93347 | -0.9066 | -0.87011 | -0.82451 | -0.77321 | -0.71868 | -0.66333 | -0.60017 | -0.52495 | -0.43197 | 0.0011845 | -0.00364 | -0.000182 | -0.000182 | 0 | 0 | 0.0019104 | 0.05 | -0.32868 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.67151 | 0.63618 | 0.6117 | 0.60179 | 0.59561 | 0.59632 | 0.60496 | 0.62826 | 0.68419 | 0.77088 | 0.88521 | 0.98562 | 0.85179 | 0.71348 | 0.57469 | 0.43884 | 0.31278 | 0.20028 | 0.10055 | 0.012944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010032 | 0.98562 | 11 | Slope | 0.66667 | 0.55717 | 0.54539 | 0.52612 | 0.51171 | 0.49854 | 0.48766 | 0.47943 | 0.47609 | 0.48362 | 0.50141 | 0.5284 | 0.55076 | 0.49504 | 0.43783 | 0.38045 | 0.32406 | 0.27093 | 0.22232 | 0.17796 | 0.13765 | 0.12222 | 0.11111 | 0.1 | 0.088889 | 0.077778 | 0.066667 | 0.055556 | 0.044444 | 0.033333 | 0.022222 | 0.014455 | 0.55717 | 0 | 0.67151 | Slope | 1 | 0.023689 |  | 0.88274 | 0 | 0.67151 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00016087 | 0.00032935 | 0.0019104
34 | 0:06 | 2.3689 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.9068 | 0.029068 | 0.029068 | 2.3689 | 0.00026895 | [13 empty] | 0.9904 | 1 | 0.98869 | 0.95783 | 0.90782 | 0.83632 | 0.72548 | 0.51617 | 0.22938 | -0.057945 | -0.29518 | -0.47725 | -0.61765 | -0.72726 | -0.81204 | -0.87627 | -0.92018 | -0.9473 | -0.96082 | -0.96167 | -0.9524 | -0.93347 | -0.9058 | -0.86867 | -0.82294 | -0.77164 | -0.71696 | -0.65477 | -0.5801 | -0.48642 | -0.37046 | 0.0014534 | -0.0038848 | -0.00019424 | -0.00019424 | 0 | 0 | 0.001996 | 0.05 | -0.364 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.6362 | 0.61171 | 0.6018 | 0.59562 | 0.59633 | 0.60497 | 0.62827 | 0.6842 | 0.77089 | 0.88522 | 0.9856 | 0.85178 | 0.71347 | 0.57468 | 0.43883 | 0.31276 | 0.20027 | 0.10054 | 0.012932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01002 | 0.15169 | 0.9856 | 10 | Slope | 0.7 | 0.5454 | 0.53724 | 0.52282 | 0.50965 | 0.49878 | 0.49054 | 0.4872 | 0.49473 | 0.51252 | 0.53952 | 0.56187 | 0.50615 | 0.44893 | 0.39156 | 0.33517 | 0.28203 | 0.23342 | 0.18907 | 0.14876 | 0.13333 | 0.12222 | 0.11111 | 0.1 | 0.088889 | 0.077778 | 0.066667 | 0.055556 | 0.044444 | 0.033333 | 0.025562 | 0.061673 | 0.56187 | 10 | 0.9856 | Slope | 0.7 | 0.029068 |  | 0.85611 | 0 | 0.9856 | Slope | 2 | 0.7 | 0 | 20 | -20 | 0.00026895 | 0.00032016 | 0.001996
35 | 0:06 | 2.9068 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.8746 | 0.018746 | 0.018746 | 2.9068 | 0.0005161 | [9 empty] | Composite Score | 0.58315 |  |  | 0.98869 | 1 | 0.9876 | 0.95205 | 0.89359 | 0.7972 | 0.60668 | 0.33162 | 0.044481 | -0.2015 | -0.39715 | -0.55099 | -0.67252 | -0.76803 | -0.84249 | -0.89749 | -0.93538 | -0.95848 | -0.96835 | -0.96732 | -0.95661 | -0.93663 | -0.90744 | -0.86916 | -0.82245 | -0.76979 | -0.70917 | -0.63696 | -0.54588 | -0.43062 | -0.29125 | 0.0009373 | -0.0039839 | -0.0001992 | -0.0001992 | 0 | 0 | 0.0020277 | 0.05 | -0.38848 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.61172 | 0.60181 | 0.59562 | 0.59633 | 0.60497 | 0.62828 | 0.6842 | 0.7709 | 0.88523 | 0.9856 | 0.85177 | 0.71346 | 0.57467 | 0.43883 | 0.31276 | 0.20027 | 0.10053 | 0.012927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010015 | 0.15168 | 0.31851 | 0.9856 | 9 | Slope | 0.73333 | 0.53724 | 0.53394 | 0.52076 | 0.50989 | 0.50166 | 0.49831 | 0.50585 | 0.52363 | 0.55063 | 0.57298 | 0.51726 | 0.46004 | 0.40267 | 0.34628 | 0.29314 | 0.24453 | 0.20018 | 0.15986 | 0.14444 | 0.13333 | 0.12222 | 0.11111 | 0.1 | 0.088889 | 0.077778 | 0.066667 | 0.055556 | 0.044444 | 0.036672 | 0.072783 | 0.11728 | 0.57298 | 9 | 0.9856 | Slope | 0.73333 | 0.018746 |  | 0.90721 | 0 | 0.9856 | Slope | 2 | 0.73333 | 0 | 20 | -20 | 0.0005161 | 0.00030893 | 0.0020277
36 | 0:06 | 1.8746 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.4582 | 0.014582 | 0.014582 | 1.8746 | 0.0002082 | [13 empty] | 0.9876 | 1 | 0.986 | 0.94537 | 0.86826 | 0.70285 | 0.4488 | 0.17139 | -0.077052 | -0.28349 | -0.45196 | -0.58811 | -0.69713 | -0.78459 | -0.85222 | -0.90317 | -0.93875 | -0.96003 | -0.96942 | -0.96826 | -0.95765 | -0.93765 | -0.90869 | -0.87057 | -0.82397 | -0.76905 | -0.70278 | -0.61947 | -0.51249 | -0.3787 | -0.21675 | 0.0007291 | -0.0040457 | -0.00020229 | -0.00020229 | 0 | 0 | 0.0020429 | 0.05 | -0.39839 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.60181 | 0.59563 | 0.59634 | 0.60498 | 0.62828 | 0.68421 | 0.7709 | 0.88523 | 0.9856 | 0.85177 | 0.71346 | 0.57467 | 0.43882 | 0.31276 | 0.20026 | 0.10053 | 0.012924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010012 | 0.15168 | 0.31851 | 0.49969 | 0.9856 | 8 | Slope | 0.76667 | 0.53394 | 0.53188 | 0.521 | 0.51277 | 0.50943 | 0.51696 | 0.53475 | 0.56174 | 0.58409 | 0.52837 | 0.47115 | 0.41378 | 0.35739 | 0.30425 | 0.25564 | 0.21129 | 0.17097 | 0.15556 | 0.14444 | 0.13333 | 0.12222 | 0.11111 | 0.1 | 0.088889 | 0.077778 | 0.066667 | 0.055556 | 0.047782 | 0.083893 | 0.12839 | 0.17767 | 0.58409 | 8 | 0.9856 | Slope | 0.76667 | 0.014582 |  | 0.92782 | 0 | 0.9856 | Slope | 2 | 0.76667 | 0 | 20 | -20 | 0.0002082 | 0.00029722 | 0.0020429
37 | 0:06 | 1.4582 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.2578 | 0.012578 | 0.012578 | 1.4582 | 0.00010018 | [13 empty] | 0.986 | 1 | 0.98423 | 0.93102 | 0.79478 | 0.56721 | 0.30693 | 0.064597 | -0.14608 | -0.32591 | -0.47694 | -0.60111 | -0.70315 | -0.78498 | -0.84966 | -0.89928 | -0.934 | -0.95567 | -0.96577 | -0.96547 | -0.95569 | -0.93671 | -0.90864 | -0.87146 | -0.8254 | -0.76837 | -0.69545 | -0.60101 | -0.47967 | -0.32608 | -0.14057 | 0.00062892 | -0.0040386 | -0.00020193 | -0.00020193 | 0 | 0 | 0.0020415 | 0.05 | -0.40457 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.59563 | 0.59634 | 0.60498 | 0.62828 | 0.68421 | 0.7709 | 0.88523 | 0.9856 | 0.85177 | 0.71346 | 0.57467 | 0.43882 | 0.31276 | 0.20026 | 0.10053 | 0.012924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010012 | 0.15168 | 0.31851 | 0.49969 | 0.69366 | 0.9856 | 7 | Slope | 0.8 | 0.53188 | 0.53211 | 0.52388 | 0.52054 | 0.52807 | 0.54586 | 0.57285 | 0.5952 | 0.53948 | 0.48227 | 0.42489 | 0.3685 | 0.31536 | 0.26675 | 0.2224 | 0.18209 | 0.16667 | 0.15556 | 0.14444 | 0.13333 | 0.12222 | 0.11111 | 0.1 | 0.088889 | 0.077778 | 0.066667 | 0.058893 | 0.095004 | 0.1395 | 0.18878 | 0.24233 | 0.5952 | 7 | 0.9856 | Slope | 0.8 | 0.012578 |  | 0.93774 | 0 | 0.9856 | Slope | 2 | 0.8 | 0 | 20 | -20 | 0.00010018 | 0.00028679 | 0.0020415
38 | 0:06 | 1.2578 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.0821 | 0.010821 | 0.010821 | 1.2578 | 8.7868e-05 | [13 empty] | 0.98423 | 1 | 0.97808 | 0.87629 | 0.68014 | 0.44261 | 0.21364 | 0.0071769 | -0.17747 | -0.3397 | -0.47863 | -0.59613 | -0.69308 | -0.77256 | -0.83656 | -0.88594 | -0.92173 | -0.94477 | -0.9564 | -0.95761 | -0.94953 | -0.93213 | -0.90575 | -0.87179 | -0.82712 | -0.76793 | -0.68872 | -0.58442 | -0.44678 | -0.27202 | -0.065183 | 0.00054105 | -0.0039523 | -0.00019761 | -0.00019761 | 0 | 0 | 0.0020282 | 0.05 | -0.40386 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.59633 | 0.60497 | 0.62828 | 0.6842 | 0.7709 | 0.88523 | 0.9856 | 0.85177 | 0.71347 | 0.57467 | 0.43883 | 0.31276 | 0.20027 | 0.10053 | 0.012929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010017 | 0.15168 | 0.31851 | 0.49969 | 0.69366 | 0.90577 | 0.9856 | 6 | Slope | 0.83333 | 0.53211 | 0.53499 | 0.53165 | 0.53918 | 0.55697 | 0.58396 | 0.60631 | 0.55059 | 0.49338 | 0.436 | 0.37961 | 0.32648 | 0.27787 | 0.23351 | 0.1932 | 0.17778 | 0.16667 | 0.15556 | 0.14444 | 0.13333 | 0.12222 | 0.11111 | 0.1 | 0.088889 | 0.077778 | 0.070006 | 0.10612 | 0.15061 | 0.1999 | 0.25344 | 0.31303 | 0.60631 | 6 | 0.9856 | Slope | 0.83333 | 0.010821 |  | 0.94644 | 0 | 0.9856 | Slope | 2 | 0.83333 | 0 | 20 | -20 | 8.7868e-05 | 0.00027988 | 0.0020282
39 | 0:06 | 1.0821 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.2267 | 0.012267 | 0.012267 | 1.0821 | 7.2294e-05 | [13 empty] | 0.97808 | 1 | 0.95273 | 0.80351 | 0.59837 | 0.38884 | 0.19248 | 0.010192 | -0.15809 | -0.30917 | -0.44291 | -0.55681 | -0.65287 | -0.73308 | -0.79822 | -0.85002 | -0.88852 | -0.91444 | -0.9289 | -0.93315 | -0.928 | -0.9137 | -0.89522 | -0.86888 | -0.83017 | -0.77354 | -0.69267 | -0.57959 | -0.42796 | -0.23833 | -0.026636 | 0.00061335 | -0.0037192 | -0.00018596 | -0.00018596 | 0 | 0 | 0.0020111 | 0.05 | -0.39523 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.60496 | 0.62826 | 0.68419 | 0.77089 | 0.88521 | 0.98561 | 0.85179 | 0.71348 | 0.57469 | 0.43884 | 0.31277 | 0.20028 | 0.10054 | 0.01294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010028 | 0.15169 | 0.31852 | 0.4997 | 0.69367 | 0.90578 | 0.87079 | 0.98561 | 5 | Slope | 0.86667 | 0.53499 | 0.54275 | 0.55029 | 0.56807 | 0.59507 | 0.61743 | 0.56171 | 0.50449 | 0.44712 | 0.39072 | 0.33759 | 0.28898 | 0.24463 | 0.20431 | 0.18889 | 0.17778 | 0.16667 | 0.15556 | 0.14444 | 0.13333 | 0.12222 | 0.11111 | 0.1 | 0.088889 | 0.081121 | 0.11723 | 0.16173 | 0.21101 | 0.26456 | 0.32415 | 0.30137 | 0.61743 | 5 | 0.98561 | Slope | 0.86667 | 0.012267 |  | 0.93928 | 0 | 0.98561 | Slope | 2 | 0.86667 | 0 | 20 | -20 | 7.2294e-05 | 0.00027861 | 0.0020111
40 | 0:07 | 1.2267 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.5329 | 0.015329 | 0.015329 | 1.2267 | 0.00015308 | [13 empty] | 0.95273 | 1 | 0.94136 | 0.79697 | 0.62203 | 0.44455 | 0.27349 | 0.1082 | -0.04769 | -0.19374 | -0.32374 | -0.4367 | -0.53369 | -0.61539 | -0.68367 | -0.73918 | -0.78187 | -0.81207 | -0.83138 | -0.84072 | -0.84102 | -0.84335 | -0.84433 | -0.83996 | -0.82165 | -0.78041 | -0.7086 | -0.60178 | -0.4582 | -0.27949 | -0.080375 | 0.00076643 | -0.00316 | -0.000158 | -0.000158 | 0 | 0 | 0.0020609 | 0.05 | -0.37192 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.62824 | 0.68416 | 0.77086 | 0.88519 | 0.98564 | 0.85181 | 0.71351 | 0.57471 | 0.43887 | 0.3128 | 0.20031 | 0.10057 | 0.012968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010056 | 0.15172 | 0.31855 | 0.49973 | 0.6937 | 0.90581 | 0.87076 | 0.64869 | 0.98564 | 4 | Slope | 0.9 | 0.54275 | 0.56139 | 0.57918 | 0.60617 | 0.62855 | 0.57283 | 0.51561 | 0.45824 | 0.40184 | 0.34871 | 0.3001 | 0.25575 | 0.21543 | 0.2 | 0.18889 | 0.17778 | 0.16667 | 0.15556 | 0.14444 | 0.13333 | 0.12222 | 0.11111 | 0.1 | 0.092241 | 0.12835 | 0.17285 | 0.22213 | 0.27568 | 0.33527 | 0.31248 | 0.22734 | 0.62855 | 4 | 0.98564 | Slope | 0.9 | 0.015329 |  | 0.92412 | 0 | 0.98564 | Slope | 2 | 0.9 | 0 | 20 | -20 | 0.00015308 | 0.00028448 | 0.0020609
41 | 0:07 | 1.5329 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.6161 | 0.026161 | 0.026161 | 1.5329 | 0.00054162 | [13 empty] | 0.94136 | 1 | 0.94971 | 0.83453 | 0.69349 | 0.54667 | 0.39869 | 0.25278 | 0.10865 | -0.026597 | -0.14897 | -0.25701 | -0.35043 | -0.43117 | -0.49981 | -0.55691 | -0.60187 | -0.63573 | -0.65973 | -0.67463 | -0.69636 | -0.72512 | -0.75838 | -0.7866 | -0.79627 | -0.77877 | -0.73087 | -0.65226 | -0.53382 | -0.37626 | -0.19989 | 0.001308 | -0.002293 | -0.00011465 | -0.00011465 | 0 | 0 | 0.0022578 | 0.05 | -0.316 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.68412 | 0.77082 | 0.88514 | 0.98568 | 0.85186 | 0.71355 | 0.57476 | 0.43891 | 0.31284 | 0.20035 | 0.10061 | 0.013012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0101 | 0.15177 | 0.31859 | 0.49977 | 0.69374 | 0.90585 | 0.87072 | 0.64864 | 0.44091 | 0.98568 | 3 | Slope | 0.93333 | 0.56137 | 0.59027 | 0.61727 | 0.63967 | 0.58395 | 0.52674 | 0.46936 | 0.41297 | 0.35984 | 0.31123 | 0.26687 | 0.22656 | 0.21111 | 0.2 | 0.18889 | 0.17778 | 0.16667 | 0.15556 | 0.14444 | 0.13333 | 0.12222 | 0.11111 | 0.10337 | 0.13948 | 0.18398 | 0.23326 | 0.2868 | 0.34639 | 0.32357 | 0.23844 | 0.15808 | 0.63967 | 3 | 0.98568 | Slope | 0.93333 | 0.026161 |  | 0.8705 | 0 | 0.98568 | Slope | 2 | 0.93333 | 0 | 20 | -20 | 0.00054162 | 0.00029792 | 0.0022578
42 | 0:07 | 2.6161 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.1948 | 0.031948 | 0.031948 | 2.6161 | 0.00028933 | [13 empty] | 0.94971 | 1 | 0.96164 | 0.87213 | 0.75993 | 0.63768 | 0.51211 | 0.38254 | 0.25491 | 0.13353 | 0.022247 | -0.076309 | -0.16362 | -0.24006 | -0.30616 | -0.36129 | -0.4062 | -0.44176 | -0.4684 | -0.50326 | -0.55054 | -0.61159 | -0.67775 | -0.73439 | -0.7703 | -0.7808 | -0.76522 | -0.71105 | -0.61061 | -0.47306 | -0.33284 | 0.0015974 | -0.0011497 | -5.7486e-05 | -5.7486e-05 | 0 | 0 | 0.0025785 | 0.05 | -0.2293 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.77076 | 0.88509 | 0.98574 | 0.85191 | 0.71361 | 0.57481 | 0.43897 | 0.3129 | 0.20041 | 0.10067 | 0.013069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010157 | 0.15182 | 0.31865 | 0.49983 | 0.6938 | 0.90591 | 0.87066 | 0.64859 | 0.44085 | 0.26127 | 0.98574 | 2 | Slope | 0.96667 | 0.59025 | 0.62836 | 0.6508 | 0.59508 | 0.53787 | 0.48049 | 0.4241 | 0.37097 | 0.32236 | 0.278 | 0.23769 | 0.22222 | 0.21111 | 0.2 | 0.18889 | 0.17778 | 0.16667 | 0.15556 | 0.14444 | 0.13333 | 0.12222 | 0.1145 | 0.15061 | 0.19511 | 0.24439 | 0.29793 | 0.35752 | 0.33467 | 0.24953 | 0.16917 | 0.098202 | 0.6508 | 2 | 0.98574 | Slope | 0.96667 | 0.031948 |  | 0.84186 | 0 | 0.98574 | Slope | 2 | 0.96667 | 0 | 20 | -20 | 0.00028933 | 0.00031789 | 0.0025785
43 | 0:07 | 3.1948 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.2412 | 0.032412 | 0.032412 | 3.1948 | 2.3206e-05 | [13 empty] | 0.96164 | 1 | 0.97025 | 0.89953 | 0.80711 | 0.70449 | 0.59441 | 0.48114 | 0.36826 | 0.25974 | 0.16016 | 0.06997 | -0.01078 | -0.082429 | -0.14409 | -0.19669 | -0.24093 | -0.27661 | -0.31996 | -0.37717 | -0.45346 | -0.54397 | -0.63508 | -0.71509 | -0.77575 | -0.81319 | -0.81285 | -0.76587 | -0.67376 | -0.55906 | -0.44621 | 0.0016206 | 0.00014203 | 7.1013e-06 | 7.1013e-06 | 0 | 0 | 0.0029555 | 0.05 | -0.11497 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.88502 | 0.9858 | 0.85198 | 0.71367 | 0.57488 | 0.43903 | 0.31297 | 0.20047 | 0.10074 | 0.013133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010221 | 0.15189 | 0.31872 | 0.49989 | 0.69386 | 0.90597 | 0.8706 | 0.64852 | 0.44079 | 0.26121 | 0.1139 | 0.9858 | 1 | Slope | 1 | 0.62834 | 0.66193 | 0.60622 | 0.549 | 0.49163 | 0.43523 | 0.3821 | 0.33349 | 0.28913 | 0.24882 | 0.23333 | 0.22222 | 0.21111 | 0.2 | 0.18889 | 0.17778 | 0.16667 | 0.15556 | 0.14444 | 0.13333 | 0.12563 | 0.16174 | 0.20624 | 0.25552 | 0.30907 | 0.36866 | 0.34575 | 0.26062 | 0.18026 | 0.10929 | 0.049079 | 0.66193 | 1 | 0.9858 | Slope | 1 | 0.032412 |  | 0.83956 | 0 | 0.9858 | Slope | 2 | 1 | 0 | 20 | -20 | 2.3206e-05 | 0.00034255 | 0.0029555
44 | 0:07 | 3.2412 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.3542 | 0.033542 | 0.033542 | 3.2412 | 5.6525e-05 | [13 empty] | 0.97025 | 1 | 0.97629 | 0.9179 | 0.84005 | 0.75008 | 0.65351 | 0.55304 | 0.45192 | 0.35474 | 0.26379 | 0.18065 | 0.10535 | 0.038974 | -0.019148 | -0.069912 | -0.1129 | -0.16236 | -0.22511 | -0.30835 | -0.41135 | -0.52437 | -0.63656 | -0.73797 | -0.81963 | -0.86353 | -0.86062 | -0.8102 | -0.72497 | -0.62848 | -0.53446 | 0.0016771 | 0.0014803 | 7.4014e-05 | 7.4014e-05 | 0 | 0 | 0.0033407 | 0.05 | 0.014203 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.98587 | 0.85205 | 0.71374 | 0.57495 | 0.4391 | 0.31303 | 0.20054 | 0.1008 | 0.0132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010288 | 0.15195 | 0.31878 | 0.49996 | 0.69393 | 0.90604 | 0.87053 | 0.64846 | 0.44072 | 0.26114 | 0.11384 | 0 | 0.98587 | 0 | Slope | 1 | 0.66196 | 0.61735 | 0.56013 | 0.50276 | 0.44637 | 0.39323 | 0.34462 | 0.30027 | 0.25996 | 0.24444 | 0.23333 | 0.22222 | 0.21111 | 0.2 | 0.18889 | 0.17778 | 0.16667 | 0.15556 | 0.14444 | 0.13676 | 0.17287 | 0.21737 | 0.26665 | 0.3202 | 0.37979 | 0.35684 | 0.27171 | 0.19135 | 0.12038 | 0.060168 | 0.011111 | 0.66196 | 0 | 0.98587 | Slope | 1 | 0.033542 |  | 0.83397 | 0 | 0.98587 | Slope | 2 | 1 | 0 | 20 | -20 | 5.6525e-05 | 0.0003698 | 0.0033407
45 | 0:07 | 3.3542 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.5214 | 0.035214 | 0.035214 | 3.3542 | 8.3599e-05 | [13 empty] | 0.97629 | 1 | 0.9802 | 0.93072 | 0.86236 | 0.78317 | 0.69722 | 0.60695 | 0.51624 | 0.42749 | 0.34376 | 0.26643 | 0.19692 | 0.13478 | 0.079278 | 0.030746 | -0.023626 | -0.090115 | -0.17661 | -0.28468 | -0.40876 | -0.54188 | -0.67406 | -0.79335 | -0.87607 | -0.91087 | -0.89628 | -0.84053 | -0.76525 | -0.68411 | -0.60203 | 0.0017607 | 0.0028634 | 0.00014317 | 0.00014317 | 0 | 0 | 0.003732 | 0.05 | 0.14803 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.85212 | 0.71381 | 0.57502 | 0.43917 | 0.3131 | 0.20061 | 0.10087 | 0.013269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010357 | 0.15202 | 0.31885 | 0.50003 | 0.694 | 0.90611 | 0.87046 | 0.64839 | 0.44065 | 0.26107 | 0.11377 | 0 | 0 | 0.90611 | 23 | Slope | 0.26667 | 0.61737 | 0.57127 | 0.51389 | 0.4575 | 0.40437 | 0.35576 | 0.3114 | 0.27109 | 0.25556 | 0.24444 | 0.23333 | 0.22222 | 0.21111 | 0.2 | 0.18889 | 0.17778 | 0.16667 | 0.15556 | 0.1479 | 0.18401 | 0.22851 | 0.27779 | 0.33133 | 0.39093 | 0.36793 | 0.2828 | 0.20244 | 0.13147 | 0.071256 | 0.022222 | 0.011111 | 0.61737 | 0 | 0.85212 | Slope | 1 | 0.035214 |  | 0.82569 | 0 | 0.85212 | Slope | 2 | 1 | 0 | 20 | -20 | 8.3599e-05 | 0.00039775 | 0.003732
46 | 0:08 | 3.5214 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.3585 | 0.033585 | 0.033585 | 3.5214 | 8.1436e-05 | [13 empty] | 0.9802 | 1 | 0.98312 | 0.9396 | 0.87924 | 0.80849 | 0.73089 | 0.64954 | 0.56633 | 0.48436 | 0.40631 | 0.33486 | 0.26985 | 0.2107 | 0.15799 | 0.10024 | 0.031137 | -0.056805 | -0.16632 | -0.29444 | -0.43844 | -0.59135 | -0.74004 | -0.85726 | -0.92665 | -0.9442 | -0.91524 | -0.86243 | -0.79864 | -0.72821 | -0.65406 | 0.0016793 | 0.0042513 | 0.00021256 | 0.00021256 | 0 | 0 | 0.0041038 | 0.05 | 0.28634 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.71388 | 0.57508 | 0.43924 | 0.31317 | 0.20068 | 0.10094 | 0.013339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010427 | 0.15209 | 0.31892 | 0.5001 | 0.69407 | 0.90618 | 0.87039 | 0.64832 | 0.44058 | 0.261 | 0.1137 | 0 | 0 | 0 | 0.90618 | 22 | Slope | 0.3 | 0.57129 | 0.52503 | 0.46863 | 0.4155 | 0.36689 | 0.32254 | 0.28222 | 0.26667 | 0.25556 | 0.24444 | 0.23333 | 0.22222 | 0.21111 | 0.2 | 0.18889 | 0.17778 | 0.16667 | 0.15903 | 0.19514 | 0.23964 | 0.28892 | 0.34247 | 0.40206 | 0.37902 | 0.29388 | 0.21353 | 0.14256 | 0.082344 | 0.033333 | 0.022222 | 0.011111 | 0.57129 | 0 | 0.71388 | Slope | 1 | 0.033585 |  | 0.83375 | 0 | 0.71388 | Slope | 2 | 1 | 0 | 20 | -20 | 8.1436e-05 | 0.00042488 | 0.0041038
47 | 0:08 | 3.3585 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.8826 | 0.028826 | 0.028826 | 3.3585 | 0.00023799 | [13 empty] | 0.98312 | 1 | 0.98499 | 0.94639 | 0.89227 | 0.82812 | 0.75788 | 0.68293 | 0.60578 | 0.52914 | 0.45684 | 0.38993 | 0.32807 | 0.27198 | 0.21171 | 0.14103 | 0.052343 | -0.05721 | -0.1861 | -0.33429 | -0.49861 | -0.66822 | -0.81374 | -0.91495 | -0.9629 | -0.95875 | -0.92657 | -0.8812 | -0.82612 | -0.76283 | -0.6966 | 0.0014413 | 0.0056097 | 0.00028049 | 0.00028049 | 0 | 0 | 0.0044559 | 0.05 | 0.42513 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.57515 | 0.43931 | 0.31324 | 0.20075 | 0.10101 | 0.013407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010495 | 0.15216 | 0.31899 | 0.50017 | 0.69414 | 0.90625 | 0.87032 | 0.64825 | 0.44051 | 0.26094 | 0.11363 | 0 | 0 | 0 | 0 | 0.90625 | 21 | Slope | 0.33333 | 0.52505 | 0.47977 | 0.42664 | 0.37803 | 0.33367 | 0.29336 | 0.27778 | 0.26667 | 0.25556 | 0.24444 | 0.23333 | 0.22222 | 0.21111 | 0.2 | 0.18889 | 0.17778 | 0.17016 | 0.20628 | 0.25077 | 0.30006 | 0.3536 | 0.41319 | 0.39011 | 0.30497 | 0.22462 | 0.15365 | 0.093433 | 0.044444 | 0.033333 | 0.022222 | 0.011111 | 0.52505 | 0 | 0.57515 | Slope | 1 | 0.028826 |  | 0.85731 | 0 | 0.57515 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00023799 | 0.00045003 | 0.0044559
48 | 0:08 | 2.8826 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.8488 | 0.018488 | 0.018488 | 2.8826 | 0.00051687 | [13 empty] | 0.98499 | 1 | 0.98671 | 0.95203 | 0.90277 | 0.84442 | 0.77934 | 0.70943 | 0.63688 | 0.56546 | 0.49741 | 0.4335 | 0.37463 | 0.31243 | 0.24093 | 0.15255 | 0.043684 | -0.084635 | -0.23378 | -0.40301 | -0.58481 | -0.75155 | -0.88009 | -0.95713 | -0.97735 | -0.96457 | -0.93617 | -0.89741 | -0.84827 | -0.79188 | -0.73124 | 0.00092441 | 0.0068704 | 0.00034352 | 0.00034352 | 0 | 0 | 0.0047679 | 0.05 | 0.56097 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.43937 | 0.3133 | 0.20081 | 0.10107 | 0.01347 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010558 | 0.15222 | 0.31905 | 0.50023 | 0.6942 | 0.90631 | 0.87026 | 0.64819 | 0.44045 | 0.26087 | 0.11357 | 0 | 0 | 0 | 0 | 0 | 0.90631 | 20 | Slope | 0.36667 | 0.47979 | 0.43777 | 0.38916 | 0.3448 | 0.30449 | 0.28889 | 0.27778 | 0.26667 | 0.25556 | 0.24444 | 0.23333 | 0.22222 | 0.21111 | 0.2 | 0.18889 | 0.1813 | 0.21741 | 0.26191 | 0.31119 | 0.36473 | 0.42433 | 0.4012 | 0.31606 | 0.23571 | 0.16474 | 0.10452 | 0.055556 | 0.044444 | 0.033333 | 0.022222 | 0.011111 | 0.47979 | 0 | 0.43937 | Slope | 1 | 0.018488 |  | 0.90848 | 0 | 0.43937 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00051687 | 0.00047233 | 0.0047679
49 | 0:08 | 1.8488 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.0056 | 0.010056 | 0.010056 | 1.8488 | 0.0004216 | [13 empty] | 0.98671 | 1 | 0.98797 | 0.95621 | 0.91108 | 0.85671 | 0.79562 | 0.72948 | 0.66134 | 0.59367 | 0.52834 | 0.46712 | 0.40309 | 0.33084 | 0.24295 | 0.13528 | 0.0078666 | -0.141 | -0.31195 | -0.49986 | -0.67996 | -0.82955 | -0.93182 | -0.97548 | -0.98146 | -0.96853 | -0.94445 | -0.91013 | -0.86644 | -0.81478 | -0.75929 | 0.00050282 | 0.0079954 | 0.00039977 | 0.00039977 | 0 | 0 | 0.0050453 | 0.05 | 0.68704 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.31336 | 0.20086 | 0.10113 | 0.013526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010614 | 0.15228 | 0.31911 | 0.50029 | 0.69426 | 0.90637 | 0.87021 | 0.64813 | 0.44039 | 0.26082 | 0.11351 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90637 | 19 | Slope | 0.4 | 0.43779 | 0.40029 | 0.35593 | 0.31562 | 0.3 | 0.28889 | 0.27778 | 0.26667 | 0.25556 | 0.24444 | 0.23333 | 0.22222 | 0.21111 | 0.2 | 0.19243 | 0.22854 | 0.27304 | 0.32232 | 0.37586 | 0.43546 | 0.41229 | 0.32715 | 0.2468 | 0.17583 | 0.11562 | 0.066667 | 0.055556 | 0.044444 | 0.033333 | 0.022222 | 0.011111 | 0.43779 | 0 | 0.31336 | Slope | 1 | 0.010056 |  | 0.95022 | 0 | 0.31336 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0004216 | 0.00049133 | 0.0050453
50 | 0:08 | 1.0056 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 0.31228 | 0.0031228 | 0.0031228 | 1.0056 | 0.00034667 | [13 empty] | 0.98797 | 1 | 0.98891 | 0.95968 | 0.91747 | 0.8662 | 0.80813 | 0.74567 | 0.6808 | 0.61557 | 0.55271 | 0.48722 | 0.41424 | 0.32682 | 0.22054 | 0.094658 | -0.053498 | -0.22488 | -0.4159 | -0.60385 | -0.76757 | -0.89007 | -0.95523 | -0.98019 | -0.98271 | -0.97223 | -0.95141 | -0.92126 | -0.88141 | -0.83409 | -0.78271 | 0.00015614 | 0.0089927 | 0.00044964 | 0.00044964 | 0 | 0 | 0.0052897 | 0.05 | 0.79954 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.20091 | 0.10118 | 0.013576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010664 | 0.15233 | 0.31916 | 0.50034 | 0.69431 | 0.90642 | 0.87016 | 0.64808 | 0.44034 | 0.26077 | 0.11346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90642 | 18 | Slope | 0.43333 | 0.4003 | 0.36706 | 0.32675 | 0.31111 | 0.3 | 0.28889 | 0.27778 | 0.26667 | 0.25556 | 0.24444 | 0.23333 | 0.22222 | 0.21111 | 0.20355 | 0.23967 | 0.28416 | 0.33345 | 0.38699 | 0.44658 | 0.42339 | 0.33825 | 0.25789 | 0.18692 | 0.12671 | 0.077778 | 0.066667 | 0.055556 | 0.044444 | 0.033333 | 0.022222 | 0.011111 | 0.44658 | 18 | 0.90642 | Slope | 0.43333 | 0.0031228 |  | 0.98454 | 0 | 0.90642 | Slope | 2 | 0.43333 | 0 | 20 | -20 | 0.00034667 | 0.00050676 | 0.0052897
51 | 0:08 | 0.31228 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -0.73354 | -0.0073354 | -0.0073354 | 0.31228 | 0.00052291 | [13 empty] | 0.98891 | 1 | 0.9898 | 0.9624 | 0.92248 | 0.87358 | 0.81853 | 0.75885 | 0.69615 | 0.6332 | 0.56689 | 0.49347 | 0.40648 | 0.30158 | 0.17753 | 0.030803 | -0.14054 | -0.33344 | -0.52643 | -0.69925 | -0.83601 | -0.91922 | -0.96218 | -0.98073 | -0.98395 | -0.97571 | -0.95803 | -0.93092 | -0.89463 | -0.85065 | -0.80353 | -0.00036677 | 0.0098687 | 0.00049344 | 0.00049344 | 0 | 0 | 0.0055028 | 0.05 | 0.89927 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.10122 | 0.01362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010708 | 0.15237 | 0.3192 | 0.50038 | 0.69435 | 0.90646 | 0.87011 | 0.64804 | 0.4403 | 0.26072 | 0.11342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90646 | 17 | Slope | 0.46667 | 0.36707 | 0.33787 | 0.32222 | 0.31111 | 0.3 | 0.28889 | 0.27778 | 0.26667 | 0.25556 | 0.24444 | 0.23333 | 0.22222 | 0.21468 | 0.25079 | 0.29529 | 0.34457 | 0.39812 | 0.45771 | 0.43448 | 0.34935 | 0.26899 | 0.19802 | 0.13781 | 0.088889 | 0.077778 | 0.066667 | 0.055556 | 0.044444 | 0.033333 | 0.022222 | 0.011111 | 0.45771 | 17 | 0.90646 | Slope | 0.46667 | 0.0073354 |  | 0.96369 | 0 | 0.90646 | Slope | 2 | 0.46667 | 0 | 20 | -20 | 0.00052291 | 0.00051814 | 0.0055028
52 | 0:09 | -0.73354 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -1.2552 | -0.012552 | -0.012552 | -0.73354 | 0.00026081 | [13 empty] | 0.9898 | 1 | 0.99035 | 0.96427 | 0.92598 | 0.8793 | 0.8264 | 0.76843 | 0.70758 | 0.64167 | 0.56815 | 0.48154 | 0.37759 | 0.25502 | 0.10986 | -0.06081 | -0.25519 | -0.45201 | -0.63116 | -0.7773 | -0.87294 | -0.93051 | -0.96384 | -0.98099 | -0.98521 | -0.97897 | -0.96349 | -0.93904 | -0.90521 | -0.8645 | -0.81837 | -0.00062758 | 0.010598 | 0.0005299 | 0.0005299 | 0 | 0 | 0.005683 | 0.05 | 0.98687 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.013656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010744 | 0.15241 | 0.31924 | 0.50042 | 0.69439 | 0.9065 | 0.87008 | 0.648 | 0.44026 | 0.26069 | 0.11338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9065 | 16 | Slope | 0.5 | 0.33789 | 0.33333 | 0.32222 | 0.31111 | 0.3 | 0.28889 | 0.27778 | 0.26667 | 0.25556 | 0.24444 | 0.23333 | 0.2258 | 0.26191 | 0.30641 | 0.35569 | 0.40924 | 0.46883 | 0.44558 | 0.36044 | 0.28009 | 0.20912 | 0.14891 | 0.1 | 0.088889 | 0.077778 | 0.066667 | 0.055556 | 0.044444 | 0.033333 | 0.022222 | 0.011111 | 0.46883 | 16 | 0.9065 | Slope | 0.5 | 0.012552 |  | 0.93787 | 0 | 0.9065 | Slope | 2 | 0.5 | 0 | 20 | -20 | 0.00026081 | 0.00052502 | 0.005683
53 | 0:09 | -1.2552 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -1.7291 | -0.017291 | -0.017291 | -1.2552 | 0.00023698 | [13 empty] | 0.99035 | 1 | 0.99079 | 0.9657 | 0.92906 | 0.88411 | 0.83262 | 0.77628 | 0.71313 | 0.6409 | 0.5552 | 0.45245 | 0.3313 | 0.18758 | 0.017862 | -0.17729 | -0.37759 | -0.56204 | -0.7154 | -0.82012 | -0.88825 | -0.93403 | -0.96434 | -0.98146 | -0.98682 | -0.98221 | -0.9688 | -0.94616 | -0.91477 | -0.8753 | -0.82905 | -0.00086456 | 0.01121 | 0.00056049 | 0.00056049 | 0 | 0 | 0.0058336 | 0.05 | 1.0598 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010775 | 0.15244 | 0.31927 | 0.50045 | 0.69442 | 0.90653 | 0.87004 | 0.64797 | 0.44023 | 0.26066 | 0.11335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90653 | 15 | Slope | 0.53333 | 0.33333 | 0.33333 | 0.32222 | 0.31111 | 0.3 | 0.28889 | 0.27778 | 0.26667 | 0.25556 | 0.24444 | 0.23692 | 0.27304 | 0.31753 | 0.36682 | 0.42036 | 0.47995 | 0.45668 | 0.37155 | 0.29119 | 0.22022 | 0.16001 | 0.11111 | 0.1 | 0.088889 | 0.077778 | 0.066667 | 0.055556 | 0.044444 | 0.033333 | 0.022222 | 0.011111 | 0.47995 | 15 | 0.90653 | Slope | 0.53333 | 0.017291 |  | 0.91441 | 0 | 0.90653 | Slope | 2 | 0.53333 | 0 | 20 | -20 | 0.00023698 | 0.00052715 | 0.0058336
54 | 0:09 | -1.7291 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.0775 | -0.020775 | -0.020775 | -1.7291 | 0.00017419 | [13 empty] | 0.99079 | 1 | 0.99111 | 0.96706 | 0.93175 | 0.88794 | 0.83787 | 0.7798 | 0.71115 | 0.62772 | 0.52668 | 0.4072 | 0.26485 | 0.095952 | -0.099741 | -0.30287 | -0.49227 | -0.65187 | -0.76385 | -0.83966 | -0.89423 | -0.93551 | -0.96479 | -0.98216 | -0.98859 | -0.98554 | -0.97341 | -0.95248 | -0.92248 | -0.88331 | -0.83594 | -0.0010388 | 0.011705 | 0.00058527 | 0.00058527 | 0 | 0 | 0.0059554 | 0.05 | 1.121 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010799 | 0.15247 | 0.31929 | 0.50047 | 0.69444 | 0.90655 | 0.87002 | 0.64794 | 0.44021 | 0.26063 | 0.11333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90655 | 14 | Slope | 0.56667 | 0.33333 | 0.33333 | 0.32222 | 0.31111 | 0.3 | 0.28889 | 0.27778 | 0.26667 | 0.25556 | 0.24804 | 0.28416 | 0.32865 | 0.37794 | 0.43148 | 0.49107 | 0.46778 | 0.38265 | 0.30229 | 0.23132 | 0.17111 | 0.12222 | 0.11111 | 0.1 | 0.088889 | 0.077778 | 0.066667 | 0.055556 | 0.044444 | 0.033333 | 0.022222 | 0.011111 | 0.49107 | 14 | 0.90655 | Slope | 0.56667 | 0.020775 |  | 0.89716 | 0 | 0.90655 | Slope | 2 | 0.56667 | 0 | 20 | -20 | 0.00017419 | 0.00052438 | 0.0059554
55 | 0:09 | -2.0775 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -3.0797 | -0.030797 | -0.030797 | -2.0775 | 0.00050111 | [13 empty] | 0.99111 | 1 | 0.99153 | 0.96843 | 0.93402 | 0.89146 | 0.84022 | 0.7775 | 0.69866 | 0.60075 | 0.48354 | 0.34287 | 0.17473 | -0.021681 | -0.22743 | -0.42116 | -0.58676 | -0.70534 | -0.78737 | -0.8482 | -0.8971 | -0.93646 | -0.96516 | -0.98305 | -0.99057 | -0.98839 | -0.9774 | -0.95798 | -0.92865 | -0.88887 | -0.84075 | -0.0015399 | 0.012091 | 0.00060455 | 0.00060455 | 0 | 0 | 0.0060499 | 0.05 | 1.1705 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010819 | 0.15249 | 0.31931 | 0.50049 | 0.69446 | 0.90657 | 0.87 | 0.64793 | 0.44019 | 0.26061 | 0.11331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90657 | 13 | Slope | 0.6 | 0.33333 | 0.33333 | 0.32222 | 0.31111 | 0.3 | 0.28889 | 0.27778 | 0.26667 | 0.25916 | 0.29527 | 0.33977 | 0.38905 | 0.4426 | 0.50219 | 0.47889 | 0.39375 | 0.3134 | 0.24243 | 0.18221 | 0.13333 | 0.12222 | 0.11111 | 0.1 | 0.088889 | 0.077778 | 0.066667 | 0.055556 | 0.044444 | 0.033333 | 0.022222 | 0.011111 | 0.50219 | 13 | 0.90657 | Slope | 0.6 | 0.030797 |  | 0.84755 | 0 | 0.90657 | Slope | 2 | 0.6 | 0 | 20 | -20 | 0.00050111 | 0.00051667 | 0.0060499
56 | 0:09 | -3.0797 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -3.8673 | -0.038673 | -0.038673 | -3.0797 | 0.00039381 | 1 = | Correl | 0 | 0% | [9 empty] | 0.99153 | 1 | 0.99181 | 0.96916 | 0.93552 | 0.89192 | 0.83643 | 0.76408 | 0.67111 | 0.55703 | 0.41825 | 0.25086 | 0.053377 | -0.1553 | -0.35315 | -0.52378 | -0.64775 | -0.73443 | -0.79943 | -0.85309 | -0.89904 | -0.93677 | -0.96525 | -0.98356 | -0.99149 | -0.98984 | -0.98031 | -0.96168 | -0.93198 | -0.89151 | -0.84196 | -0.0019337 | 0.012323 | 0.00061614 | 0.00061614 | 0 | 0 | 0.0061086 | 0.05 | 1.2091 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01083 | 0.1525 | 0.31932 | 0.5005 | 0.69447 | 0.90658 | 0.86999 | 0.64791 | 0.44018 | 0.2606 | 0.1133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.90658 | 12 | Slope | 0.63333 | 0.33333 | 0.33333 | 0.32222 | 0.31111 | 0.3 | 0.28889 | 0.27778 | 0.27028 | 0.30639 | 0.35089 | 0.40017 | 0.45371 | 0.51331 | 0.49 | 0.40486 | 0.3245 | 0.25353 | 0.19332 | 0.14444 | 0.13333 | 0.12222 | 0.11111 | 0.1 | 0.088889 | 0.077778 | 0.066667 | 0.055556 | 0.044444 | 0.033333 | 0.022222 | 0.011111 | 0.51331 | 12 | 0.90658 | Slope | 0.63333 | 0.038673 |  | 0.80857 | 0 | 0.90658 | Slope | 2 | 0.63333 | 0 | 20 | -20 | 0.00039381 | 0.00050405 | 0.0061086
57 | 0:09 | -3.8673 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.2722 | -0.042722 | -0.042722 | -3.8673 | 0.00020245 | 2 = | Slope | 360 | 100% | [9 empty] | 0.99181 | 1 | 0.99191 | 0.96963 | 0.9351 | 0.88768 | 0.82317 | 0.73717 | 0.6282 | 0.49227 | 0.32585 | 0.12727 | -0.084723 | -0.28704 | -0.46261 | -0.59131 | -0.68178 | -0.7497 | -0.80627 | -0.85615 | -0.89964 | -0.93654 | -0.96487 | -0.98324 | -0.99123 | -0.99102 | -0.9824 | -0.96368 | -0.93345 | -0.89171 | -0.83995 | -0.0021361 | 0.012411 | 0.00062054 | 0.00062054 | 0 | 0 | 0.0061315 | 0.05 | 1.2323 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.010835 | 0.1525 | 0.31933 | 0.50051 | 0.69448 | 0.90659 | 0.86998 | 0.64791 | 0.44017 | 0.2606 | 0.11329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00079357 | 0.90659 | 11 | Slope | 0.66667 | 0.33333 | 0.33333 | 0.32222 | 0.31111 | 0.3 | 0.28889 | 0.28139 | 0.3175 | 0.362 | 0.41128 | 0.46483 | 0.52442 | 0.50111 | 0.41597 | 0.33561 | 0.26464 | 0.20443 | 0.15556 | 0.14444 | 0.13333 | 0.12222 | 0.11111 | 0.1 | 0.088889 | 0.077778 | 0.066667 | 0.055556 | 0.044444 | 0.033333 | 0.022222 | 0.011376 | 0.52442 | 11 | 0.90659 | Slope | 0.66667 | 0.042722 |  | 0.78852 | 0 | 0.90659 | Slope | 2 | 0.66667 | 0 | 20 | -20 | 0.00020245 | 0.00048673 | 0.0061315
58 | 0:10 | -4.2722 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.0327 | -0.050327 | -0.050327 | -4.2722 | 0.00038021 |  |  | 360 | [10 empty] | 0.99191 | 1 | 0.99206 | 0.96918 | 0.93141 | 0.87575 | 0.79833 | 0.69685 | 0.56604 | 0.40174 | 0.20235 | -0.013009 | -0.22021 | -0.40124 | -0.53506 | -0.62918 | -0.69955 | -0.75804 | -0.8102 | -0.85698 | -0.8992 | -0.93555 | -0.96372 | -0.98184 | -0.99128 | -0.99217 | -0.98379 | -0.96483 | -0.93369 | -0.89014 | -0.83665 | -0.0025163 | 0.012376 | 0.00061882 | 0.00061882 | 0 | 0 | 0.0061224 | 0.05 | 1.2411 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0 | 0 | 0 | 0 | 0.010833 | 0.1525 | 0.31933 | 0.50051 | 0.69448 | 0.90658 | 0.86999 | 0.64791 | 0.44017 | 0.2606 | 0.11329 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00079529 | 0.10539 | 0.90658 | 10 | Slope | 0.7 | 0.33333 | 0.33333 | 0.32222 | 0.31111 | 0.3 | 0.2925 | 0.32861 | 0.37311 | 0.42239 | 0.47594 | 0.53553 | 0.51222 | 0.42708 | 0.34672 | 0.27575 | 0.21554 | 0.16667 | 0.15556 | 0.14444 | 0.13333 | 0.12222 | 0.11111 | 0.1 | 0.088889 | 0.077778 | 0.066667 | 0.055556 | 0.044444 | 0.033333 | 0.022487 | 0.046243 | 0.53553 | 10 | 0.90658 | Slope | 0.7 | 0.050327 |  | 0.75088 | 0 | 0.90658 | Slope | 2 | 0.7 | 0 | 20 | -20 | 0.00038021 | 0.00046498 | 0.0061224
59 | 0:10 | -5.0327 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.9641 | -0.059641 | -0.059641 | -5.0327 | 0.00046572 | [13 empty] | 0.99206 | 1 | 0.99153 | 0.96576 | 0.92028 | 0.8521 | 0.75939 | 0.63597 | 0.47595 | 0.27662 | 0.057928 | -0.15438 | -0.34121 | -0.48011 | -0.57768 | -0.64995 | -0.70967 | -0.763 | -0.81131 | -0.85634 | -0.89755 | -0.93357 | -0.96122 | -0.98074 | -0.99137 | -0.99267 | -0.98419 | -0.96453 | -0.93186 | -0.88672 | -0.82659 | -0.0029821 | 0.012195 | 0.00060976 | 0.00060976 | 0 | 0 | 0.0060728 | 0.05 | 1.2376 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0 | 0 | 0 | 0.010824 | 0.15249 | 0.31932 | 0.5005 | 0.69447 | 0.90658 | 0.87 | 0.64792 | 0.44018 | 0.26061 | 0.1133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00080436 | 0.1054 | 0.23152 | 0.90658 | 9 | Slope | 0.73333 | 0.33333 | 0.33333 | 0.32222 | 0.31111 | 0.30361 | 0.33972 | 0.38422 | 0.4335 | 0.48704 | 0.54664 | 0.52333 | 0.4382 | 0.35784 | 0.28687 | 0.22666 | 0.17778 | 0.16667 | 0.15556 | 0.14444 | 0.13333 | 0.12222 | 0.11111 | 0.1 | 0.088889 | 0.077778 | 0.066667 | 0.055556 | 0.044444 | 0.033601 | 0.057357 | 0.088286 | 0.54664 | 9 | 0.90658 | Slope | 0.73333 | 0.059641 |  | 0.70478 | 0 | 0.90658 | Slope | 2 | 0.73333 | 0 | 20 | -20 | 0.00046572 | 0.00043921 | 0.0060728
60 | 0:10 | -5.9641 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -6.6535 | -0.066535 | -0.066535 | -5.9641 | 0.00034472 | [13 empty] | 0.99153 | 1 | 0.99028 | 0.9589 | 0.90275 | 0.82054 | 0.70694 | 0.55483 | 0.35936 | 0.13882 | -0.079305 | -0.27331 | -0.41813 | -0.51983 | -0.59462 | -0.65596 | -0.71071 | -0.76016 | -0.8069 | -0.85096 | -0.89197 | -0.9273 | -0.95711 | -0.9788 | -0.99095 | -0.99286 | -0.9844 | -0.964 | -0.93021 | -0.87997 | -0.81189 | -0.0033268 | 0.01174 | 0.00058698 | 0.00058698 | 0 | 0 | 0.0059511 | 0.05 | 1.2195 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0 | 0 | 0.010801 | 0.15247 | 0.3193 | 0.50047 | 0.69444 | 0.90655 | 0.87002 | 0.64794 | 0.44021 | 0.26063 | 0.11333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00082713 | 0.10543 | 0.23155 | 0.37654 | 0.90655 | 8 | Slope | 0.76667 | 0.33333 | 0.33333 | 0.32222 | 0.31471 | 0.35082 | 0.39532 | 0.4446 | 0.49815 | 0.55774 | 0.53445 | 0.44931 | 0.36896 | 0.29799 | 0.23778 | 0.18889 | 0.17778 | 0.16667 | 0.15556 | 0.14444 | 0.13333 | 0.12222 | 0.11111 | 0.1 | 0.088889 | 0.077778 | 0.066667 | 0.055556 | 0.04472 | 0.068476 | 0.099404 | 0.13662 | 0.55774 | 8 | 0.90655 | Slope | 0.76667 | 0.066535 |  | 0.67065 | 0 | 0.90655 | Slope | 2 | 0.76667 | 0 | 20 | -20 | 0.00034472 | 0.00041017 | 0.0059511
61 | 0:10 | -6.6535 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.2489 | -0.072489 | -0.072489 | -6.6535 | 0.00029769 | [13 empty] | 0.99028 | 1 | 0.98795 | 0.94905 | 0.88125 | 0.78024 | 0.63962 | 0.45286 | 0.2348 | 0.012177 | -0.19022 | -0.34288 | -0.44997 | -0.52829 | -0.59218 | -0.64902 | -0.70006 | -0.74831 | -0.79426 | -0.83835 | -0.87854 | -0.91714 | -0.95061 | -0.97549 | -0.98944 | -0.99252 | -0.98454 | -0.96397 | -0.9276 | -0.87184 | -0.79688 | -0.0036245 | 0.010985 | 0.00054926 | 0.00054926 | 0 | 0 | 0.0057606 | 0.05 | 1.174 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0 | 0.010763 | 0.15243 | 0.31926 | 0.50044 | 0.69441 | 0.90651 | 0.87006 | 0.64798 | 0.44024 | 0.26067 | 0.11336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00086485 | 0.10546 | 0.23158 | 0.37658 | 0.53484 | 0.90651 | 7 | Slope | 0.8 | 0.33333 | 0.33333 | 0.32581 | 0.36192 | 0.40642 | 0.4557 | 0.50925 | 0.56884 | 0.54557 | 0.46044 | 0.38008 | 0.30911 | 0.2489 | 0.2 | 0.18889 | 0.17778 | 0.16667 | 0.15556 | 0.14444 | 0.13333 | 0.12222 | 0.11111 | 0.1 | 0.088889 | 0.077778 | 0.066667 | 0.055844 | 0.079599 | 0.11053 | 0.14775 | 0.18939 | 0.56884 | 7 | 0.90651 | Slope | 0.8 | 0.072489 |  | 0.64118 | 0 | 0.90651 | Slope | 2 | 0.8 | 0 | 20 | -20 | 0.00029769 | 0.00037935 | 0.0057606
62 | 0:10 | -7.2489 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -8.0368 | -0.080368 | -0.080368 | -7.2489 | 0.00039396 | [13 empty] | 0.98795 | 1 | 0.98521 | 0.93864 | 0.85573 | 0.73099 | 0.55831 | 0.34871 | 0.12615 | -0.083649 | -0.24574 | -0.3603 | -0.44351 | -0.5111 | -0.57116 | -0.62458 | -0.67492 | -0.72261 | -0.76881 | -0.81185 | -0.85669 | -0.90083 | -0.93975 | -0.96819 | -0.98501 | -0.99028 | -0.98346 | -0.96379 | -0.92563 | -0.86636 | -0.77752 | -0.0040184 | 0.0098979 | 0.00049489 | 0.00049489 | 0 | 0 | 0.0055112 | 0.05 | 1.0985 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0.010709 | 0.15238 | 0.3192 | 0.50038 | 0.69435 | 0.90646 | 0.87011 | 0.64804 | 0.4403 | 0.26072 | 0.11342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00091922 | 0.10552 | 0.23164 | 0.37663 | 0.53489 | 0.69295 | 0.90646 | 6 | Slope | 0.83333 | 0.33333 | 0.3369 | 0.37301 | 0.41751 | 0.46679 | 0.52034 | 0.57993 | 0.5567 | 0.47157 | 0.39121 | 0.32024 | 0.26003 | 0.21111 | 0.2 | 0.18889 | 0.17778 | 0.16667 | 0.15556 | 0.14444 | 0.13333 | 0.12222 | 0.11111 | 0.1 | 0.088889 | 0.077778 | 0.066973 | 0.090728 | 0.12166 | 0.15888 | 0.20052 | 0.24209 | 0.57993 | 6 | 0.90646 | Slope | 0.83333 | 0.080368 |  | 0.60218 | 0 | 0.90646 | Slope | 2 | 0.83333 | 0 | 20 | -20 | 0.00039396 | 0.00034868 | 0.0055112
63 | 0:10 | -8.0368 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -8.6145 | -0.086145 | -0.086145 | -8.0368 | 0.00028883 | [13 empty] | 0.98521 | 1 | 0.98252 | 0.92585 | 0.82376 | 0.67056 | 0.47553 | 0.25944 | 0.047014 | -0.12335 | -0.24641 | -0.3359 | -0.40801 | -0.47208 | -0.52867 | -0.58166 | -0.63146 | -0.67949 | -0.72427 | -0.77312 | -0.82519 | -0.87696 | -0.92132 | -0.95455 | -0.97546 | -0.98321 | -0.98077 | -0.96333 | -0.92558 | -0.85729 | -0.74847 | -0.0043072 | 0.0084812 | 0.00042406 | 0.00042406 | 0 | 0 | 0.0052142 | 0.05 | 0.98979 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.010638 | 0.1523 | 0.31913 | 0.50031 | 0.69428 | 0.90639 | 0.87018 | 0.64811 | 0.44037 | 0.26079 | 0.11349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00099006 | 0.10559 | 0.23171 | 0.3767 | 0.53497 | 0.69302 | 0.84241 | 0.90639 | 5 | Slope | 0.86667 | 0.33688 | 0.3841 | 0.4286 | 0.47788 | 0.53143 | 0.59102 | 0.56784 | 0.4827 | 0.40234 | 0.33138 | 0.27116 | 0.22222 | 0.21111 | 0.2 | 0.18889 | 0.17778 | 0.16667 | 0.15556 | 0.14444 | 0.13333 | 0.12222 | 0.11111 | 0.1 | 0.088889 | 0.078108 | 0.10186 | 0.13279 | 0.17001 | 0.21166 | 0.25323 | 0.29192 | 0.59102 | 5 | 0.90639 | Slope | 0.86667 | 0.086145 |  | 0.57358 | 0 | 0.90639 | Slope | 2 | 0.86667 | 0 | 20 | -20 | 0.00028883 | 0.00032057 | 0.0052142
64 | 0:11 | -8.6145 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.8764 | -0.078764 | -0.078764 | -8.6145 | 0.00036906 | 0 | [12 empty] | 0.98252 | 1 | 0.97852 | 0.90828 | 0.78183 | 0.60702 | 0.40399 | 0.19574 | 0.021663 | -0.1085 | -0.2047 | -0.28206 | -0.35037 | -0.41046 | -0.46651 | -0.51869 | -0.56882 | -0.61506 | -0.66629 | -0.72342 | -0.78467 | -0.84343 | -0.89442 | -0.93368 | -0.95846 | -0.97361 | -0.9769 | -0.96374 | -0.92282 | -0.84011 | -0.70385 | -0.0039382 | 0.0068129 | 0.00034065 | 0.00034065 | 0 | 0 | 0.0048833 | 0.05 | 0.84812 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.15222 | 0.31905 | 0.50023 | 0.6942 | 0.90631 | 0.87026 | 0.64819 | 0.44045 | 0.26088 | 0.11357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0010735 | 0.10567 | 0.23179 | 0.37679 | 0.53505 | 0.6931 | 0.8425 | 0.97994 | 0.97994 | 30 | Slope | 0.033333 | 0.38407 | 0.43968 | 0.48896 | 0.54251 | 0.6021 | 0.57898 | 0.49384 | 0.41348 | 0.34251 | 0.2823 | 0.23333 | 0.22222 | 0.21111 | 0.2 | 0.18889 | 0.17778 | 0.16667 | 0.15556 | 0.14444 | 0.13333 | 0.12222 | 0.11111 | 0.1 | 0.089247 | 0.113 | 0.14393 | 0.18115 | 0.22279 | 0.26437 | 0.30305 | 0.33776 | 0.6021 | 4 | 0.90631 | Slope | 0.9 | 0.078764 |  | 0.61012 | 0 | 0.90631 | Slope | 2 | 0.9 | 0 | 20 | -20 | 0.00036906 | 0.00029755 | 0.0048833
65 | 0:11 | -7.8764 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -6.7231 | -0.067231 | -0.067231 | -7.8764 | 0.00057665 | [9 empty] | Correl | Slope | Acc Score |  | 0.97852 | 1 | 0.97328 | 0.88576 | 0.74084 | 0.55841 | 0.362 | 0.19004 | 0.05631 | -0.045743 | -0.12881 | -0.20187 | -0.26559 | -0.32481 | -0.3796 | -0.4318 | -0.47952 | -0.53246 | -0.59252 | -0.65975 | -0.72895 | -0.7959 | -0.85504 | -0.90018 | -0.93622 | -0.96144 | -0.97402 | -0.9654 | -0.91863 | -0.81589 | -0.65681 | -0.0033615 | 0.0050011 | 0.00025006 | 0.00025006 | 0 | 0 | 0.0045736 | 0.05 | 0.68129 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.31896 | 0.50014 | 0.69411 | 0.90622 | 0.87036 | 0.64828 | 0.44054 | 0.26097 | 0.11366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011641 | 0.10576 | 0.23188 | 0.37688 | 0.53514 | 0.6932 | 0.84259 | 0.98003 | 0.90599 | 0.98003 | 29 | Slope | 0.066667 | 0.43965 | 0.50005 | 0.55359 | 0.61318 | 0.59012 | 0.50498 | 0.42463 | 0.35366 | 0.29344 | 0.24444 | 0.23333 | 0.22222 | 0.21111 | 0.2 | 0.18889 | 0.17778 | 0.16667 | 0.15556 | 0.14444 | 0.13333 | 0.12222 | 0.11111 | 0.10039 | 0.12414 | 0.15507 | 0.19229 | 0.23394 | 0.27551 | 0.3142 | 0.3489 | 0.31311 | 0.61318 | 3 | 0.90622 | Slope | 0.93333 | 0.067231 |  | 0.66721 | 0 | 0.90622 | Slope | 2 | 0.93333 | 0 | 20 | -20 | 0.00057665 | 0.000282 | 0.0045736
66 | 0:11 | -6.7231 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.6484 | -0.056484 | -0.056484 | -6.7231 | 0.00053736 |  | Limit | Correl | Slope | Acc Score | Limit per Minute | Per 5 Minute |  |  | 0% | 100% | 0.88446 |  | 0.97328 | 1 | 0.96661 | 0.86684 | 0.71672 | 0.54095 | 0.37888 | 0.24729 | 0.14305 | 0.05552 | -0.022321 | -0.08981 | -0.15193 | -0.20903 | -0.26306 | -0.31175 | -0.36609 | -0.42799 | -0.49848 | -0.57375 | -0.65167 | -0.72808 | -0.79469 | -0.85522 | -0.90619 | -0.94585 | -0.97123 | -0.96716 | -0.91144 | -0.79015 | -0.61902 | -0.0028242 | 0.0030614 | 0.00015307 | 0.00015307 | 0 | 0 | 0.0043286 | 0.05 | 0.50011 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.50004 | 0.69401 | 0.90612 | 0.87045 | 0.64838 | 0.44064 | 0.26106 | 0.11376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001261 | 0.10586 | 0.23198 | 0.37697 | 0.53524 | 0.69329 | 0.84268 | 0.98013 | 0.9059 | 0.80112 | 0.98013 | 28 | Slope | 0.1 | 0.50001 | 0.56467 | 0.62426 | 0.60126 | 0.51613 | 0.43577 | 0.3648 | 0.30459 | 0.25556 | 0.24444 | 0.23333 | 0.22222 | 0.21111 | 0.2 | 0.18889 | 0.17778 | 0.16667 | 0.15556 | 0.14444 | 0.13333 | 0.12222 | 0.11153 | 0.13529 | 0.16622 | 0.20344 | 0.24508 | 0.28665 | 0.32534 | 0.36004 | 0.32419 | 0.27815 | 0.62426 | 2 | 0.90612 | Slope | 0.96667 | 0.056484 |  | 0.72041 | 0 | 0.90612 | Slope | 2 | 0.96667 | 0 | 20 | -20 | 0.00053736 | 0.00027534 | 0.0043286
67 | 0:11 | -5.6484 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.566 | -0.04566 | -0.04566 | -5.6484 | 0.00054117 |  | 0.0001 | 96.07% | 3.927% | 0.79015 | 0.06% | 0.3% |  | 0.0001 | 0.96073 | 0.039275 | 0.79015 |  | 0.96661 | 1 | 0.96355 | 0.86287 | 0.7208 | 0.57825 | 0.45694 | 0.35676 | 0.26914 | 0.18856 | 0.11804 | 0.053601 | -0.0047958 | -0.059502 | -0.10802 | -0.16279 | -0.22575 | -0.29779 | -0.37529 | -0.45832 | -0.54517 | -0.62867 | -0.71379 | -0.79346 | -0.8632 | -0.92339 | -0.96363 | -0.96436 | -0.89689 | -0.77148 | -0.60682 | -0.002283 | 0.00094034 | 4.7017e-05 | 4.7017e-05 | 0 | 0 | 0.0042034 | 0.05 | 0.30614 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.6939 | 0.90601 | 0.87056 | 0.64848 | 0.44075 | 0.26117 | 0.11387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013671 | 0.10597 | 0.23209 | 0.37708 | 0.53534 | 0.6934 | 0.84279 | 0.98024 | 0.90579 | 0.80102 | 0.70399 | 0.98024 | 27 | Slope | 0.13333 | 0.56463 | 0.63534 | 0.61241 | 0.52727 | 0.44692 | 0.37595 | 0.31573 | 0.26667 | 0.25556 | 0.24444 | 0.23333 | 0.22222 | 0.21111 | 0.2 | 0.18889 | 0.17778 | 0.16667 | 0.15556 | 0.14444 | 0.13333 | 0.12268 | 0.14643 | 0.17736 | 0.21458 | 0.25623 | 0.2978 | 0.33649 | 0.37119 | 0.33526 | 0.28923 | 0.24578 | 0.63534 | 1 | 0.90601 | Slope | 1 | 0.04566 |  | 0.77398 | 0 | 0.90601 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00054117 | 0.00027779 | 0.0042034
68 | 0:11 | -4.566 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -3.4432 | -0.034432 | -0.034432 | -4.566 | 0.00056143 |  | 0.0002 | 96.07% | 3.927% | 0.79015 | 0.12% | 0.6% |  | 0.0002 | 0.96073 | 0.039275 | 0.79015 |  | 0.96355 | 1 | 0.96448 | 0.87138 | 0.75902 | 0.65594 | 0.56725 | 0.48603 | 0.40789 | 0.33708 | 0.27178 | 0.21315 | 0.15906 | 0.11182 | 0.058687 | -0.0032239 | -0.074766 | -0.15172 | -0.23466 | -0.32423 | -0.41556 | -0.5172 | -0.62217 | -0.72163 | -0.81652 | -0.89855 | -0.95422 | -0.94904 | -0.88407 | -0.76781 | -0.63351 | -0.0017216 | -0.0012939 | -6.4697e-05 | -6.4697e-05 | 0 | 0 | 0.0042062 | 0.05 | 0.094034 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.9059 | 0.87067 | 0.64859 | 0.44086 | 0.26128 | 0.11398 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0014788 | 0.10608 | 0.2322 | 0.37719 | 0.53545 | 0.69351 | 0.8429 | 0.98035 | 0.90568 | 0.80091 | 0.70388 | 0.61562 | 0.98035 | 26 | Slope | 0.16667 | 0.6353 | 0.62356 | 0.53842 | 0.45806 | 0.38709 | 0.32688 | 0.27778 | 0.26667 | 0.25556 | 0.24444 | 0.23333 | 0.22222 | 0.21111 | 0.2 | 0.18889 | 0.17778 | 0.16667 | 0.15556 | 0.14444 | 0.13383 | 0.15758 | 0.18851 | 0.22573 | 0.26737 | 0.30895 | 0.34763 | 0.38234 | 0.34634 | 0.3003 | 0.25685 | 0.21632 | 0.6353 | 0 | 0.9059 | Slope | 1 | 0.034432 |  | 0.82956 | 0 | 0.9059 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00056143 | 0.00028786 | 0.0042062
69 | 0:11 | -3.4432 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -1.1443 | -0.011443 | -0.011443 | -3.4432 | 0.0011494 |  | 0.0003 | 96.07% | 3.927% | 0.79015 | 0.18% | 0.9% |  | 0.0003 | 0.96073 | 0.039275 | 0.79015 |  | 0.96448 | 1 | 0.968 | 0.89692 | 0.8194 | 0.7479 | 0.67934 | 0.60958 | 0.54312 | 0.47946 | 0.42163 | 0.3685 | 0.32274 | 0.27276 | 0.2146 | 0.14634 | 0.072068 | -0.0079461 | -0.094767 | -0.18588 | -0.29246 | -0.41144 | -0.534 | -0.66005 | -0.78069 | -0.88481 | -0.93859 | -0.93845 | -0.88062 | -0.78745 | -0.6983 | -0.00057216 | -0.0035147 | -0.00017573 | -0.00017573 | 0 | 0 | 0.0042823 | 0.05 | -0.12939 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.87078 | 0.64871 | 0.44097 | 0.26139 | 0.11409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0015898 | 0.10619 | 0.23231 | 0.3773 | 0.53557 | 0.69362 | 0.84301 | 0.98046 | 0.90557 | 0.80079 | 0.70377 | 0.61551 | 0.54951 | 0.98046 | 25 | Slope | 0.2 | 0.62359 | 0.54957 | 0.46921 | 0.39824 | 0.33803 | 0.28889 | 0.27778 | 0.26667 | 0.25556 | 0.24444 | 0.23333 | 0.22222 | 0.21111 | 0.2 | 0.18889 | 0.17778 | 0.16667 | 0.15556 | 0.14497 | 0.16873 | 0.19966 | 0.23688 | 0.27852 | 0.3201 | 0.35878 | 0.39349 | 0.35741 | 0.31138 | 0.26792 | 0.22739 | 0.19428 | 0.62359 | 0 | 0.87078 | Slope | 1 | 0.011443 |  | 0.94336 | 0 | 0.87078 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0011494 | 0.00030294 | 0.0042823
70 | 0:12 | -1.1443 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.9465 | 0.039465 | 0.039465 | -1.1443 | 0.0025454 |  | 0.0004 | 95.47% | 4.532% | 0.78861 | 0.24% | 1.2% |  | 0.0004 | 0.95468 | 0.045317 | 0.78861 |  | 0.968 | 1 | 0.97791 | 0.93244 | 0.88199 | 0.82957 | 0.77298 | 0.71553 | 0.65737 | 0.60215 | 0.55056 | 0.50598 | 0.45929 | 0.40635 | 0.34404 | 0.27496 | 0.19966 | 0.11805 | 0.032095 | -0.070949 | -0.19142 | -0.32454 | -0.473 | -0.62647 | -0.77282 | -0.87638 | -0.93461 | -0.93649 | -0.89041 | -0.82975 | -0.77679 | 0.0019733 | -0.0055921 | -0.0002796 | -0.0002796 | 0 | 0 | 0.004432 | 0.05 | -0.35147 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.64881 | 0.44107 | 0.2615 | 0.11419 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016937 | 0.10629 | 0.23241 | 0.37741 | 0.53567 | 0.69373 | 0.84312 | 0.98056 | 0.90546 | 0.80069 | 0.70367 | 0.6154 | 0.54941 | 0.50374 | 0.98056 | 24 | Slope | 0.23333 | 0.5496 | 0.48036 | 0.40939 | 0.34918 | 0.3 | 0.28889 | 0.27778 | 0.26667 | 0.25556 | 0.24444 | 0.23333 | 0.22222 | 0.21111 | 0.2 | 0.18889 | 0.17778 | 0.16667 | 0.15612 | 0.17988 | 0.2108 | 0.24802 | 0.28967 | 0.33124 | 0.36993 | 0.40463 | 0.36849 | 0.32245 | 0.279 | 0.23847 | 0.20536 | 0.17903 | 0.5496 | 0 | 0.64881 | Slope | 1 | 0.039465 |  | 0.80465 | 0 | 0.64881 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0025454 | 0.00032038 | 0.004432
71 | 0:12 | 3.9465 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 8.8887 | 0.088887 | 0.088887 | 3.9465 | 0.0024711 |  | 0.0005 | 95.17% | 4.834% | 0.79051 | 0.3% | 1.5% |  | 0.0005 | 0.95166 | 0.048338 | 0.79051 |  | 0.97791 | 1 | 0.98627 | 0.95699 | 0.92023 | 0.87738 | 0.83112 | 0.78136 | 0.73126 | 0.68264 | 0.63952 | 0.59499 | 0.54633 | 0.49026 | 0.42793 | 0.3587 | 0.28272 | 0.20281 | 0.10623 | -0.0093024 | -0.14247 | -0.29981 | -0.47476 | -0.65284 | -0.79335 | -0.89554 | -0.9458 | -0.94244 | -0.90695 | -0.86878 | -0.82839 | 0.0044444 | -0.0073878 | -0.00036939 | -0.00036939 | 0 | 0 | 0.0047169 | 0.05 | -0.55921 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.44116 | 0.26159 | 0.11428 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0017835 | 0.10638 | 0.2325 | 0.3775 | 0.53576 | 0.69381 | 0.84321 | 0.98065 | 0.90537 | 0.8006 | 0.70358 | 0.61531 | 0.54932 | 0.50365 | 0.46731 | 0.98065 | 23 | Slope | 0.26667 | 0.48039 | 0.42053 | 0.36032 | 0.31111 | 0.3 | 0.28889 | 0.27778 | 0.26667 | 0.25556 | 0.24444 | 0.23333 | 0.22222 | 0.21111 | 0.2 | 0.18889 | 0.17778 | 0.16726 | 0.19102 | 0.22195 | 0.25917 | 0.30081 | 0.34238 | 0.38107 | 0.41577 | 0.37957 | 0.33353 | 0.29008 | 0.24955 | 0.21644 | 0.19011 | 0.16688 | 0.48039 | 0 | 0.44116 | Slope | 1 | 0.088887 |  | 0.56001 | 0 | 0.44116 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0024711 | 0.00033792 | 0.0047169
72 | 0:12 | 8.8887 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 12.7919 | 0.12792 | 0.12792 | 8.8887 | 0.0019516 |  | 0.0006 | 94.56% | 5.438% | 0.79446 | 0.36% | 1.8% |  | 0.0006 | 0.94562 | 0.054381 | 0.79446 |  | 0.98627 | 1 | 0.99079 | 0.9687 | 0.93792 | 0.90205 | 0.86139 | 0.81785 | 0.77334 | 0.73189 | 0.68896 | 0.64262 | 0.59084 | 0.53416 | 0.47099 | 0.40032 | 0.32494 | 0.23392 | 0.12409 | -0.0052433 | -0.16262 | -0.34664 | -0.54583 | -0.71487 | -0.84886 | -0.93378 | -0.9626 | -0.94862 | -0.92171 | -0.89111 | -0.85498 | 0.006396 | -0.0088609 | -0.00044304 | -0.00044304 | 0 | 0 | 0.0050486 | 0.05 | -0.73878 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.26166 | 0.11436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018572 | 0.10646 | 0.23258 | 0.37757 | 0.53583 | 0.69389 | 0.84328 | 0.98073 | 0.9053 | 0.80053 | 0.7035 | 0.61524 | 0.54925 | 0.50358 | 0.46724 | 0.43594 | 0.98073 | 22 | Slope | 0.3 | 0.42055 | 0.37145 | 0.32222 | 0.31111 | 0.3 | 0.28889 | 0.27778 | 0.26667 | 0.25556 | 0.24444 | 0.23333 | 0.22222 | 0.21111 | 0.2 | 0.18889 | 0.1784 | 0.20215 | 0.23308 | 0.2703 | 0.31194 | 0.35352 | 0.3922 | 0.42691 | 0.39066 | 0.34462 | 0.30117 | 0.26064 | 0.22753 | 0.20119 | 0.17797 | 0.15642 | 0.42691 | 22 | 0.98073 | Slope | 0.3 | 0.12792 |  | 0.3668 | 0 | 0.98073 | Slope | 2 | 0.3 | 0 | 20 | -20 | 0.0019516 | 0.00035377 | 0.0050486
73 | 0:12 | 12.7919 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 15.3078 | 0.15308 | 0.15308 | 12.7919 | 0.0012579 |  | 0.0007 | 94.26% | 5.74% | 0.79482 | 0.42% | 2.1% |  | 0.0007 | 0.9426 | 0.057402 | 0.79482 |  | 0.99079 | 1 | 0.99257 | 0.97331 | 0.94656 | 0.91421 | 0.87774 | 0.83832 | 0.7993 | 0.75787 | 0.71306 | 0.66341 | 0.61018 | 0.55162 | 0.48584 | 0.41419 | 0.32685 | 0.22132 | 0.095897 | -0.058619 | -0.24394 | -0.45339 | -0.64375 | -0.80415 | -0.91519 | -0.96735 | -0.97008 | -0.95392 | -0.9306 | -0.90255 | -0.87157 | 0.0076539 | -0.010035 | -0.00050177 | -0.00050177 | 0 | 0 | 0.0053603 | 0.05 | -0.88609 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.11441 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0019159 | 0.10652 | 0.23264 | 0.37763 | 0.53589 | 0.69395 | 0.84334 | 0.98079 | 0.90524 | 0.80047 | 0.70345 | 0.61518 | 0.54919 | 0.50352 | 0.46718 | 0.43588 | 0.41629 | 0.98079 | 21 | Slope | 0.33333 | 0.37147 | 0.33333 | 0.32222 | 0.31111 | 0.3 | 0.28889 | 0.27778 | 0.26667 | 0.25556 | 0.24444 | 0.23333 | 0.22222 | 0.21111 | 0.2 | 0.18953 | 0.21328 | 0.24421 | 0.28143 | 0.32307 | 0.36465 | 0.40334 | 0.43804 | 0.40175 | 0.35571 | 0.31226 | 0.27173 | 0.23862 | 0.21228 | 0.18906 | 0.16751 | 0.14988 | 0.43804 | 21 | 0.98079 | Slope | 0.33333 | 0.15308 |  | 0.24226 | 0 | 0.98079 | Slope | 2 | 0.33333 | 0 | 20 | -20 | 0.0012579 | 0.00036672 | 0.0053603
74 | 0:12 | 15.3078 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 16.8347 | 0.16835 | 0.16835 | 15.3078 | 0.00076346 |  | 0.0008 | 93.35% | 6.647% | 0.79771 | 0.48% | 2.4% |  | 0.0008 | 0.93353 | 0.066465 | 0.79771 |  | 0.99257 | 1 | 0.99328 | 0.97607 | 0.95148 | 0.92189 | 0.88826 | 0.85279 | 0.81376 | 0.77062 | 0.7226 | 0.67104 | 0.61532 | 0.55343 | 0.48558 | 0.40176 | 0.29937 | 0.17727 | 0.025953 | -0.15777 | -0.37031 | -0.57348 | -0.75576 | -0.89089 | -0.96256 | -0.97923 | -0.97306 | -0.95782 | -0.93602 | -0.91088 | -0.8782 | 0.0084174 | -0.010957 | -0.00054785 | -0.00054785 | 0 | 0 | 0.0056191 | 0.05 | -1.0035 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001962 | 0.10656 | 0.23268 | 0.37768 | 0.53594 | 0.69399 | 0.84339 | 0.98083 | 0.9052 | 0.80042 | 0.7034 | 0.61514 | 0.54914 | 0.50347 | 0.46714 | 0.43583 | 0.41625 | 0.41353 | 0.98083 | 20 | Slope | 0.36667 | 0.33333 | 0.33333 | 0.32222 | 0.31111 | 0.3 | 0.28889 | 0.27778 | 0.26667 | 0.25556 | 0.24444 | 0.23333 | 0.22222 | 0.21111 | 0.20065 | 0.22441 | 0.25534 | 0.29256 | 0.3342 | 0.37578 | 0.41446 | 0.44917 | 0.41284 | 0.36681 | 0.32336 | 0.28282 | 0.24971 | 0.22338 | 0.20016 | 0.17861 | 0.16097 | 0.14895 | 0.44917 | 20 | 0.98083 | Slope | 0.36667 | 0.16835 |  | 0.16668 | 0 | 0.98083 | Slope | 2 | 0.36667 | 0 | 20 | -20 | 0.00076346 | 0.00037597 | 0.0056191
75 | 0:12 | 16.8347 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 18.3616 | 0.18362 | 0.18362 | 16.8347 | 0.00076346 |  | 0.0009 | 93.05% | 6.949% | 0.7977 | 0.54% | 2.7% |  | 0.0009 | 0.93051 | 0.069486 | 0.7977 |  | 0.99328 | 1 | 0.99399 | 0.97807 | 0.95534 | 0.92769 | 0.89682 | 0.86147 | 0.82106 | 0.77506 | 0.72501 | 0.67076 | 0.61145 | 0.54697 | 0.46732 | 0.36865 | 0.24961 | 0.10148 | -0.079848 | -0.29251 | -0.5019 | -0.69886 | -0.85579 | -0.94791 | -0.97837 | -0.98194 | -0.97501 | -0.96059 | -0.94044 | -0.91416 | -0.86993 | 0.0091808 | -0.011669 | -0.00058343 | -0.00058343 | 0 | 0 | 0.005821 | 0.05 | -1.0957 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0019975 | 0.1066 | 0.23272 | 0.37771 | 0.53597 | 0.69403 | 0.84342 | 0.98087 | 0.90516 | 0.80039 | 0.70336 | 0.6151 | 0.54911 | 0.50344 | 0.4671 | 0.4358 | 0.41621 | 0.41349 | 0.43361 | 0.98087 | 19 | Slope | 0.4 | 0.33333 | 0.33333 | 0.32222 | 0.31111 | 0.3 | 0.28889 | 0.27778 | 0.26667 | 0.25556 | 0.24444 | 0.23333 | 0.22222 | 0.21178 | 0.23553 | 0.26646 | 0.30368 | 0.34532 | 0.3869 | 0.42558 | 0.46029 | 0.42394 | 0.37791 | 0.33445 | 0.29392 | 0.26081 | 0.23448 | 0.21126 | 0.18971 | 0.17207 | 0.16005 | 0.15565 | 0.46029 | 19 | 0.98087 | Slope | 0.4 | 0.18362 |  | 0.0911 | 0 | 0.98087 | Slope | 2 | 0.4 | 0 | 20 | -20 | 0.00076346 | 0.0003812 | 0.005821
76 | 0:13 | 18.3616 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 19.2637 | 0.19264 | 0.19264 | 18.3616 | 0.00045103 |  | 0.001 | 91.84% | 8.157% | 0.80117 | 0.6% | 3% |  | 0.001 | 0.91843 | 0.081571 | 0.80117 |  | 0.99399 | 1 | 0.99434 | 0.9794 | 0.95785 | 0.93197 | 0.9012 | 0.86459 | 0.82147 | 0.77321 | 0.72018 | 0.66198 | 0.59948 | 0.52327 | 0.42872 | 0.31313 | 0.16777 | -0.011145 | -0.22292 | -0.43481 | -0.63986 | -0.81211 | -0.92359 | -0.96919 | -0.98241 | -0.98353 | -0.9767 | -0.96253 | -0.94141 | -0.905 | -0.84455 | 0.0096318 | -0.012182 | -0.00060908 | -0.00060908 | 0 | 0 | 0.0059709 | 0.05 | -1.1669 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0020232 | 0.10662 | 0.23274 | 0.37774 | 0.536 | 0.69405 | 0.84345 | 0.98089 | 0.90513 | 0.80036 | 0.70334 | 0.61507 | 0.54908 | 0.50341 | 0.46707 | 0.43577 | 0.41619 | 0.41347 | 0.43359 | 0.47037 | 0.98089 | 18 | Slope | 0.43333 | 0.33333 | 0.33333 | 0.32222 | 0.31111 | 0.3 | 0.28889 | 0.27778 | 0.26667 | 0.25556 | 0.24444 | 0.23333 | 0.2229 | 0.24665 | 0.27758 | 0.3148 | 0.35644 | 0.39802 | 0.4367 | 0.47141 | 0.43504 | 0.38901 | 0.34556 | 0.30502 | 0.27192 | 0.24558 | 0.22236 | 0.20081 | 0.18317 | 0.17116 | 0.16675 | 0.1679 | 0.47141 | 18 | 0.98089 | Slope | 0.43333 | 0.19264 |  | 0.046448 | 0 | 0.98089 | Slope | 2 | 0.43333 | 0 | 20 | -20 | 0.00045103 | 0.00038248 | 0.0059709
77 | 0:13 | 19.2637 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 20 | 0.2 | 0.2 | 19.2637 | 0.00036816 |  | 0.002 | 88.52% | 11.48% | 0.81711 | 1.2% | 6% |  | 0.002 | 0.8852 | 0.1148 | 0.81711 |  | 0.99434 | 1 | 0.99466 | 0.98035 | 0.95985 | 0.93415 | 0.90234 | 0.86329 | 0.81788 | 0.76657 | 0.70948 | 0.64778 | 0.57386 | 0.48306 | 0.3719 | 0.23014 | 0.053525 | -0.15724 | -0.37061 | -0.5802 | -0.76195 | -0.8881 | -0.9496 | -0.97483 | -0.98436 | -0.98508 | -0.97751 | -0.96267 | -0.93285 | -0.88136 | -0.80833 | 0.01 | -0.012531 | -0.00062653 | -0.00062653 | 0 | 0 | 0.0060741 | 0.05 | -1.2182 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0020406 | 0.10664 | 0.23276 | 0.37775 | 0.53602 | 0.69407 | 0.84346 | 0.98091 | 0.90512 | 0.80034 | 0.70332 | 0.61506 | 0.54906 | 0.5034 | 0.46706 | 0.43575 | 0.41617 | 0.41345 | 0.43357 | 0.47035 | 0.5156 | 0.98091 | 17 | Slope | 0.46667 | 0.33333 | 0.33333 | 0.32222 | 0.31111 | 0.3 | 0.28889 | 0.27778 | 0.26667 | 0.25556 | 0.24444 | 0.23401 | 0.25777 | 0.2887 | 0.32592 | 0.36756 | 0.40914 | 0.44782 | 0.48253 | 0.44615 | 0.40011 | 0.35666 | 0.31613 | 0.28302 | 0.25669 | 0.23346 | 0.21192 | 0.19428 | 0.18226 | 0.17786 | 0.179 | 0.18298 | 0.48253 | 17 | 0.98091 | Slope | 0.46667 | 0.2 |  | 0.01 | 0 | 0.98091 | Slope | 2 | 0.46667 | 0 | 20 | -20 | 0.00036816 | 0.00037995 | 0.0060741
78 | 0:13 | 20 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 20 | 0.2 | 0.2 | 20 | 0 |  | 0.003 | 0.83988 | 0.16012 | 0.83528 | 1.8% | 9% |  | 0.003 | 0.83988 | 0.16012 | 0.83528 |  | 0.99466 | 1 | 0.99482 | 0.98097 | 0.96063 | 0.934 | 0.89988 | 0.85849 | 0.80993 | 0.75442 | 0.69353 | 0.62048 | 0.53205 | 0.42483 | 0.28774 | 0.11442 | -0.095468 | -0.30979 | -0.52284 | -0.71067 | -0.84643 | -0.91988 | -0.95792 | -0.97807 | -0.98665 | -0.98562 | -0.97732 | -0.95458 | -0.9104 | -0.84657 | -0.76036 | 0.01 | -0.012742 | -0.00063712 | -0.00063712 | 0 | 0 | 0.0061382 | 0.05 | -1.2531 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0020512 | 0.10665 | 0.23277 | 0.37776 | 0.53603 | 0.69408 | 0.84347 | 0.98092 | 0.90511 | 0.80033 | 0.70331 | 0.61505 | 0.54905 | 0.50339 | 0.46705 | 0.43574 | 0.41616 | 0.41344 | 0.43356 | 0.47034 | 0.51559 | 0.56946 | 0.98092 | 16 | Slope | 0.5 | 0.33333 | 0.33333 | 0.32222 | 0.31111 | 0.3 | 0.28889 | 0.27778 | 0.26667 | 0.25556 | 0.24513 | 0.26888 | 0.29981 | 0.33703 | 0.37868 | 0.42025 | 0.45894 | 0.49364 | 0.45726 | 0.41122 | 0.36777 | 0.32724 | 0.29413 | 0.2678 | 0.24457 | 0.22303 | 0.20539 | 0.19337 | 0.18896 | 0.19011 | 0.19409 | 0.20093 | 0.49364 | 16 | 0.98092 | Slope | 0.5 | 0.2 |  | 0.01 | 0 | 0.98092 | Slope | 2 | 0.5 | 0 | 20 | -20 | 0 | 0.00037382 | 0.0061382
79 | 0:13 | 20 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 20 | 0.2 | 0.2 | 20 | 0 |  | 0.004 | 0.81873 | 0.18127 | 0.84059 | 2.4% | 12% |  | 0.004 | 0.81873 | 0.18127 | 0.84059 |  | 0.99482 | 1 | 0.99495 | 0.98121 | 0.96 | 0.93117 | 0.89481 | 0.85038 | 0.79775 | 0.73854 | 0.66656 | 0.5793 | 0.47514 | 0.34258 | 0.1742 | -0.033716 | -0.24885 | -0.46497 | -0.65819 | -0.80122 | -0.88313 | -0.93108 | -0.96281 | -0.98136 | -0.98743 | -0.98538 | -0.96934 | -0.93249 | -0.87606 | -0.79898 | -0.6997 | 0.01 | -0.012894 | -0.0006447 | -0.0006447 | 0 | 0 | 0.0061852 | 0.05 | -1.2742 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0020588 | 0.10666 | 0.23278 | 0.37777 | 0.53603 | 0.69409 | 0.84348 | 0.98093 | 0.9051 | 0.80033 | 0.7033 | 0.61504 | 0.54905 | 0.50338 | 0.46704 | 0.43574 | 0.41615 | 0.41343 | 0.43355 | 0.47033 | 0.51558 | 0.56945 | 0.6303 | 0.98093 | 15 | Slope | 0.53333 | 0.33333 | 0.33333 | 0.32222 | 0.31111 | 0.3 | 0.28889 | 0.27778 | 0.26667 | 0.25624 | 0.28 | 0.31093 | 0.34815 | 0.38979 | 0.43136 | 0.47005 | 0.50475 | 0.46837 | 0.42233 | 0.37888 | 0.33835 | 0.30524 | 0.2789 | 0.25568 | 0.23413 | 0.21649 | 0.20448 | 0.20007 | 0.20122 | 0.20519 | 0.21204 | 0.22121 | 0.50475 | 15 | 0.98093 | Slope | 0.53333 | 0.2 |  | 0.01 | 0 | 0.98093 | Slope | 2 | 0.53333 | 0 | 20 | -20 | 0 | 0.00036432 | 0.0061852
80 | 0:13 | 20 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 20 | 0.2 | 0.2 | 20 | 0 |  | 0.005 | 0.79456 | 0.20544 | 0.84452 | 3% | 15% |  | 0.005 | 0.79456 | 0.20544 | 0.84452 |  | 0.99495 | 1 | 0.99473 | 0.9799 | 0.95633 | 0.92517 | 0.88574 | 0.83726 | 0.78099 | 0.71066 | 0.62445 | 0.52175 | 0.39249 | 0.2288 | 0.024631 | -0.18963 | -0.40863 | -0.6068 | -0.75647 | -0.84434 | -0.89854 | -0.93881 | -0.96804 | -0.98297 | -0.98715 | -0.97662 | -0.94602 | -0.89669 | -0.82669 | -0.7362 | -0.62622 | 0.01 | -0.013017 | -0.00065084 | -0.00065084 | 0 | 0 | 0.0062248 | 0.05 | -1.2894 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.002065 | 0.10666 | 0.23278 | 0.37778 | 0.53604 | 0.6941 | 0.84349 | 0.98093 | 0.90509 | 0.80032 | 0.7033 | 0.61503 | 0.54904 | 0.50337 | 0.46703 | 0.43573 | 0.41615 | 0.41343 | 0.43355 | 0.47032 | 0.51558 | 0.56944 | 0.6303 | 0.69763 | 0.98093 | 14 | Slope | 0.56667 | 0.33333 | 0.33333 | 0.32222 | 0.31111 | 0.3 | 0.28889 | 0.27778 | 0.26735 | 0.29111 | 0.32204 | 0.35926 | 0.4009 | 0.44248 | 0.48116 | 0.51587 | 0.47948 | 0.43344 | 0.38999 | 0.34946 | 0.31635 | 0.29001 | 0.26679 | 0.24524 | 0.2276 | 0.21559 | 0.21118 | 0.21233 | 0.2163 | 0.22315 | 0.23232 | 0.24365 | 0.51587 | 14 | 0.98093 | Slope | 0.56667 | 0.2 |  | 0.01 | 0 | 0.98093 | Slope | 2 | 0.56667 | 0 | 20 | -20 | 0 | 0.00035152 | 0.0062248
81 | 0:13 | 20 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 20 | 0.2 | 0.2 | 20 | 0 |  | 0.006 | 0.7855 | 0.2145 | 0.84537 | 3.6% | 18% |  | 0.006 | 0.7855 | 0.2145 | 0.84537 |  | 0.99473 | 1 | 0.99429 | 0.97783 | 0.95235 | 0.91855 | 0.87552 | 0.82364 | 0.75731 | 0.6737 | 0.57285 | 0.4456 | 0.28539 | 0.085329 | -0.12772 | -0.34795 | -0.55112 | -0.70694 | -0.80119 | -0.86043 | -0.90666 | -0.94445 | -0.96965 | -0.9835 | -0.98137 | -0.95827 | -0.91625 | -0.854 | -0.77088 | -0.66948 | -0.54374 | 0.01 | -0.012972 | -0.00064861 | -0.00064861 | 0 | 0 | 0.0062108 | 0.05 | -1.3017 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0 | 0 | 0 | 0 | 0 | 0.0020627 | 0.10666 | 0.23278 | 0.37778 | 0.53604 | 0.69409 | 0.84349 | 0.98093 | 0.9051 | 0.80032 | 0.7033 | 0.61504 | 0.54904 | 0.50337 | 0.46704 | 0.43573 | 0.41615 | 0.41343 | 0.43355 | 0.47033 | 0.51558 | 0.56945 | 0.6303 | 0.69763 | 0.77594 | 0.98093 | 13 | Slope | 0.6 | 0.33333 | 0.33333 | 0.32222 | 0.31111 | 0.3 | 0.28889 | 0.27847 | 0.30222 | 0.33315 | 0.37037 | 0.41201 | 0.45359 | 0.49227 | 0.52698 | 0.49059 | 0.44455 | 0.4011 | 0.36057 | 0.32746 | 0.30112 | 0.2779 | 0.25635 | 0.23872 | 0.2267 | 0.22229 | 0.22344 | 0.22741 | 0.23426 | 0.24343 | 0.25476 | 0.26976 | 0.52698 | 13 | 0.98093 | Slope | 0.6 | 0.2 |  | 0.01 | 0 | 0.98093 | Slope | 2 | 0.6 | 0 | 20 | -20 | 0 | 0.00033542 | 0.0062108
82 | 0:14 | 20 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 20 | 0.2 | 0.2 | 20 | 0 |  | 0.007 | 0.76737 | 0.23263 | 0.84725 | 4.2% | 21% |  | 0.007 | 0.76737 | 0.23263 | 0.84725 |  | 0.99429 | 1 | 0.99367 | 0.97593 | 0.94838 | 0.9116 | 0.86556 | 0.80501 | 0.7268 | 0.62971 | 0.50513 | 0.34706 | 0.14993 | -0.061672 | -0.28274 | -0.48926 | -0.65135 | -0.75165 | -0.81642 | -0.86758 | -0.91161 | -0.94512 | -0.97029 | -0.98057 | -0.96845 | -0.93538 | -0.88143 | -0.80665 | -0.71252 | -0.5953 | -0.44925 | 0.01 | -0.012732 | -0.00063658 | -0.00063658 | 0 | 0 | 0.0061381 | 0.05 | -1.2972 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0 | 0 | 0 | 0 | 0.0020507 | 0.10665 | 0.23277 | 0.37776 | 0.53603 | 0.69408 | 0.84347 | 0.98092 | 0.90511 | 0.80033 | 0.70331 | 0.61505 | 0.54905 | 0.50339 | 0.46705 | 0.43574 | 0.41616 | 0.41344 | 0.43356 | 0.47034 | 0.51559 | 0.56946 | 0.63031 | 0.69764 | 0.77595 | 0.86835 | 0.98092 | 12 | Slope | 0.63333 | 0.33333 | 0.33333 | 0.32222 | 0.31111 | 0.3 | 0.28957 | 0.31333 | 0.34426 | 0.38148 | 0.42312 | 0.46469 | 0.50338 | 0.53808 | 0.5017 | 0.45567 | 0.41221 | 0.37168 | 0.33857 | 0.31224 | 0.28902 | 0.26747 | 0.24983 | 0.23781 | 0.23341 | 0.23456 | 0.23853 | 0.24537 | 0.25455 | 0.26588 | 0.28087 | 0.30056 | 0.53808 | 12 | 0.98092 | Slope | 0.63333 | 0.2 |  | 0.01 | 0 | 0.98092 | Slope | 2 | 0.63333 | 0 | 20 | -20 | 0 | 0.00031658 | 0.0061381
83 | 0:14 | 20 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 20 | 0.2 | 0.2 | 20 | 0 |  | 0.008 | 0.73716 | 0.26284 | 0.84553 | 4.8% | 24% |  | 0.008 | 0.73716 | 0.26284 | 0.84553 |  | 0.99367 | 1 | 0.99326 | 0.97423 | 0.94443 | 0.90515 | 0.85207 | 0.78134 | 0.69131 | 0.57178 | 0.41673 | 0.22106 | 0.0095729 | -0.21203 | -0.42152 | -0.58831 | -0.69474 | -0.76463 | -0.82119 | -0.87053 | -0.91006 | -0.94467 | -0.96922 | -0.97255 | -0.95236 | -0.90866 | -0.843 | -0.75731 | -0.64738 | -0.50999 | -0.34244 | 0.01 | -0.012285 | -0.00061423 | -0.00061423 | 0 | 0 | 0.0060084 | 0.05 | -1.2732 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0 | 0 | 0 | 0.0020283 | 0.10663 | 0.23275 | 0.37774 | 0.536 | 0.69406 | 0.84345 | 0.9809 | 0.90513 | 0.80036 | 0.70333 | 0.61507 | 0.54908 | 0.50341 | 0.46707 | 0.43577 | 0.41618 | 0.41346 | 0.43358 | 0.47036 | 0.51561 | 0.56948 | 0.63033 | 0.69766 | 0.77597 | 0.86837 | 0.96225 | 0.9809 | 11 | Slope | 0.66667 | 0.33333 | 0.33333 | 0.32222 | 0.31111 | 0.30068 | 0.32443 | 0.35536 | 0.39258 | 0.43422 | 0.4758 | 0.51448 | 0.54919 | 0.51282 | 0.46679 | 0.42333 | 0.3828 | 0.34969 | 0.32336 | 0.30013 | 0.27859 | 0.26095 | 0.24893 | 0.24453 | 0.24568 | 0.24965 | 0.25649 | 0.26567 | 0.277 | 0.29199 | 0.31168 | 0.33186 | 0.54919 | 11 | 0.9809 | Slope | 0.66667 | 0.2 |  | 0.01 | 0 | 0.9809 | Slope | 2 | 0.66667 | 0 | 20 | -20 | 0 | 0.00029576 | 0.0060084
84 | 0:14 | 20 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 20 | 0.2 | 0.2 | 20 | 0 | [13 empty] | 0.99326 | 1 | 0.99276 | 0.97217 | 0.94033 | 0.89527 | 0.83347 | 0.75253 | 0.64161 | 0.49221 | 0.29853 | 0.085809 | -0.13802 | -0.35033 | -0.52164 | -0.63225 | -0.70676 | -0.76795 | -0.82283 | -0.8671 | -0.90809 | -0.94384 | -0.96387 | -0.96099 | -0.93141 | -0.87676 | -0.80029 | -0.69872 | -0.56845 | -0.40934 | -0.22763 | 0.01 | -0.011676 | -0.00058378 | -0.00058378 | 0 | 0 | 0.0058334 | 0.05 | -1.2285 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0 | 0 | 0.0019979 | 0.1066 | 0.23272 | 0.37771 | 0.53597 | 0.69403 | 0.84342 | 0.98087 | 0.90516 | 0.80039 | 0.70336 | 0.6151 | 0.54911 | 0.50344 | 0.4671 | 0.4358 | 0.41621 | 0.41349 | 0.43361 | 0.47039 | 0.51564 | 0.56951 | 0.63036 | 0.69769 | 0.776 | 0.8684 | 0.96228 | 0.94532 | 0.98087 | 10 | Slope | 0.7 | 0.33333 | 0.33333 | 0.32222 | 0.31178 | 0.33553 | 0.36646 | 0.40368 | 0.44532 | 0.4869 | 0.52558 | 0.56029 | 0.52394 | 0.47791 | 0.43445 | 0.39392 | 0.36081 | 0.33448 | 0.31126 | 0.28971 | 0.27207 | 0.26005 | 0.25565 | 0.2568 | 0.26077 | 0.26761 | 0.27679 | 0.28812 | 0.30311 | 0.3228 | 0.34298 | 0.32622 | 0.56029 | 10 | 0.98087 | Slope | 0.7 | 0.2 |  | 0.01 | 0 | 0.98087 | Slope | 2 | 0.7 | 0 | 20 | -20 | 0 | 0.00027395 | 0.0058334
85 | 0:14 | 20 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 20 | 0.2 | 0.2 | 20 | 0 | [13 empty] | 0.99276 | 1 | 0.99215 | 0.97011 | 0.93374 | 0.88135 | 0.81098 | 0.71103 | 0.57147 | 0.38275 | 0.16926 | -0.058539 | -0.27561 | -0.45131 | -0.56573 | -0.64273 | -0.70801 | -0.76768 | -0.81683 | -0.86277 | -0.90648 | -0.94011 | -0.95614 | -0.9456 | -0.9062 | -0.841 | -0.74855 | -0.62637 | -0.47413 | -0.30001 | -0.12341 | 0.01 | -0.010909 | -0.00054543 | -0.00054543 | 0 | 0 | 0.0056136 | 0.05 | -1.1676 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0 | 0.0019595 | 0.10656 | 0.23268 | 0.37767 | 0.53594 | 0.69399 | 0.84338 | 0.98083 | 0.9052 | 0.80043 | 0.7034 | 0.61514 | 0.54914 | 0.50348 | 0.46714 | 0.43583 | 0.41625 | 0.41353 | 0.43365 | 0.47043 | 0.51568 | 0.56955 | 0.6304 | 0.69773 | 0.77604 | 0.86844 | 0.96232 | 0.94528 | 0.86028 | 0.98083 | 9 | Slope | 0.73333 | 0.33333 | 0.33333 | 0.32288 | 0.34663 | 0.37756 | 0.41478 | 0.45642 | 0.498 | 0.53668 | 0.57139 | 0.53507 | 0.48903 | 0.44558 | 0.40505 | 0.37194 | 0.3456 | 0.32238 | 0.30083 | 0.28319 | 0.27118 | 0.26677 | 0.26792 | 0.27189 | 0.27874 | 0.28791 | 0.29924 | 0.31424 | 0.33392 | 0.35411 | 0.33732 | 0.29787 | 0.57139 | 9 | 0.98083 | Slope | 0.73333 | 0.2 |  | 0.01 | 0 | 0.98083 | Slope | 2 | 0.73333 | 0 | 20 | -20 | 0 | 0.00025206 | 0.0056136
86 | 0:14 | 20 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 20 | 0.2 | 0.2 | 20 | 0 | [13 empty] | 0.99215 | 1 | 0.9916 | 0.96648 | 0.92413 | 0.86465 | 0.77737 | 0.65049 | 0.47174 | 0.2607 | 0.029112 | -0.19489 | -0.37707 | -0.49493 | -0.57377 | -0.64097 | -0.70496 | -0.75815 | -0.80911 | -0.8593 | -0.90329 | -0.93531 | -0.94587 | -0.92728 | -0.87799 | -0.79678 | -0.68324 | -0.53897 | -0.37097 | -0.20084 | -0.035536 | 0.01 | -0.0099859 | -0.00049929 | -0.00049929 | 0 | 0 | 0.0053479 | 0.05 | -1.0909 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0 | 0.0019134 | 0.10651 | 0.23263 | 0.37763 | 0.53589 | 0.69394 | 0.84334 | 0.98078 | 0.90524 | 0.80047 | 0.70345 | 0.61518 | 0.54919 | 0.50352 | 0.46718 | 0.43588 | 0.4163 | 0.41358 | 0.4337 | 0.47048 | 0.51573 | 0.56959 | 0.63045 | 0.69778 | 0.77609 | 0.86848 | 0.96237 | 0.94524 | 0.86023 | 0.78681 | 0.98078 | 8 | Slope | 0.76667 | 0.33333 | 0.33397 | 0.35773 | 0.38866 | 0.42588 | 0.46752 | 0.50909 | 0.54778 | 0.58248 | 0.54619 | 0.50016 | 0.4567 | 0.41617 | 0.38306 | 0.35673 | 0.33351 | 0.31196 | 0.29432 | 0.2823 | 0.2779 | 0.27905 | 0.28302 | 0.28986 | 0.29904 | 0.31037 | 0.32536 | 0.34505 | 0.36523 | 0.34841 | 0.30897 | 0.27338 | 0.58248 | 8 | 0.98078 | Slope | 0.76667 | 0.2 |  | 0.01 | 0 | 0.98078 | Slope | 2 | 0.76667 | 0 | 20 | -20 | 0 | 0.00023106 | 0.0053479
87 | 0:14 | 20 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 20 | 0.2 | 0.2 | 20 | 0 | [13 empty] | 0.9916 | 1 | 0.98996 | 0.95999 | 0.91145 | 0.83674 | 0.7243 | 0.55868 | 0.35603 | 0.12366 | -0.10778 | -0.29917 | -0.4221 | -0.50183 | -0.57006 | -0.63608 | -0.69253 | -0.7471 | -0.80305 | -0.85536 | -0.89986 | -0.92844 | -0.93301 | -0.90562 | -0.84035 | -0.73712 | -0.60115 | -0.44028 | -0.27521 | -0.11545 | 0.039721 | 0.01 | -0.0089399 | -0.00044699 | -0.00044699 | 0 | 0 | 0.0050361 | 0.05 | -0.99859 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.0018611 | 0.10646 | 0.23258 | 0.37757 | 0.53584 | 0.69389 | 0.84328 | 0.98073 | 0.9053 | 0.80052 | 0.7035 | 0.61524 | 0.54924 | 0.50358 | 0.46724 | 0.43593 | 0.41635 | 0.41363 | 0.43375 | 0.47053 | 0.51578 | 0.56965 | 0.6305 | 0.69783 | 0.77614 | 0.86854 | 0.96242 | 0.94519 | 0.86018 | 0.78676 | 0.7273 | 0.98073 | 7 | Slope | 0.8 | 0.33395 | 0.36882 | 0.39975 | 0.43697 | 0.47861 | 0.52019 | 0.55887 | 0.59358 | 0.55732 | 0.51129 | 0.46783 | 0.4273 | 0.39419 | 0.36786 | 0.34463 | 0.32309 | 0.30545 | 0.29343 | 0.28903 | 0.29018 | 0.29415 | 0.30099 | 0.31017 | 0.3215 | 0.33649 | 0.35618 | 0.37636 | 0.35951 | 0.32006 | 0.28448 | 0.25354 | 0.59358 | 7 | 0.98073 | Slope | 0.8 | 0.2 |  | 0.01 | 0 | 0.98073 | Slope | 2 | 0.8 | 0 | 20 | -20 | 0 | 0.000212 | 0.0050361
88 | 0:15 | 20 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 20 | 0.2 | 0.2 | 20 | 0 | [13 empty] | 0.98996 | 1 | 0.98811 | 0.95401 | 0.8931 | 0.79613 | 0.64783 | 0.45712 | 0.23159 | -0.0036598 | -0.20429 | -0.33527 | -0.41793 | -0.48676 | -0.55458 | -0.61246 | -0.6715 | -0.73471 | -0.79743 | -0.8542 | -0.89887 | -0.92504 | -0.9233 | -0.88148 | -0.79423 | -0.6697 | -0.51766 | -0.35907 | -0.20183 | -0.049332 | 0.10025 | 0.01 | -0.0076787 | -0.00038393 | -0.00038393 | 0 | 0 | 0.0046687 | 0.05 | -0.89399 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.1064 | 0.23252 | 0.37751 | 0.53577 | 0.69383 | 0.84322 | 0.98067 | 0.90536 | 0.80059 | 0.70356 | 0.6153 | 0.54931 | 0.50364 | 0.4673 | 0.436 | 0.41641 | 0.41369 | 0.43381 | 0.47059 | 0.51584 | 0.56971 | 0.63056 | 0.69789 | 0.7762 | 0.8686 | 0.96248 | 0.94512 | 0.86012 | 0.7867 | 0.72723 | 0.68156 | 0.98067 | 6 | Slope | 0.83333 | 0.3688 | 0.41084 | 0.44806 | 0.4897 | 0.53128 | 0.56996 | 0.60467 | 0.56845 | 0.52242 | 0.47897 | 0.43843 | 0.40532 | 0.37899 | 0.35577 | 0.33422 | 0.31658 | 0.30456 | 0.30016 | 0.30131 | 0.30528 | 0.31213 | 0.3213 | 0.33263 | 0.34762 | 0.36731 | 0.38749 | 0.3706 | 0.33115 | 0.29557 | 0.26463 | 0.2383 | 0.60467 | 6 | 0.98067 | Slope | 0.83333 | 0.2 |  | 0.01 | 0 | 0.98067 | Slope | 2 | 0.83333 | 0 | 20 | -20 | 0 | 0.00019596 | 0.0046687
89 | 0:15 | 20 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 20 | 0.2 | 0.2 | 20 | 0 | [13 empty] | 0.98811 | 1 | 0.98666 | 0.94371 | 0.86379 | 0.73463 | 0.56139 | 0.34679 | 0.11578 | -0.090866 | -0.2296 | -0.3175 | -0.38879 | -0.45802 | -0.51674 | -0.57798 | -0.64927 | -0.7244 | -0.79637 | -0.8575 | -0.90384 | -0.92664 | -0.91268 | -0.84945 | -0.74296 | -0.60335 | -0.45327 | -0.30009 | -0.14703 | 0.0029323 | 0.15888 | 0.01 | -0.0062287 | -0.00031144 | -0.00031144 | 0 | 0 | 0.0042459 | 0.05 | -0.76787 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.23245 | 0.37744 | 0.5357 | 0.69376 | 0.84315 | 0.9806 | 0.90543 | 0.80066 | 0.70364 | 0.61537 | 0.54938 | 0.50371 | 0.46737 | 0.43607 | 0.41648 | 0.41377 | 0.43388 | 0.47066 | 0.51591 | 0.56978 | 0.63064 | 0.69796 | 0.77628 | 0.86867 | 0.96256 | 0.94505 | 0.86005 | 0.78663 | 0.72716 | 0.68149 | 0.64273 | 0.9806 | 5 | Slope | 0.86667 | 0.41082 | 0.45915 | 0.50079 | 0.54236 | 0.58105 | 0.61575 | 0.57959 | 0.53355 | 0.4901 | 0.44957 | 0.41646 | 0.39013 | 0.3669 | 0.34536 | 0.32772 | 0.3157 | 0.31129 | 0.31244 | 0.31642 | 0.32326 | 0.33243 | 0.34377 | 0.35876 | 0.37845 | 0.39863 | 0.38168 | 0.34224 | 0.30665 | 0.27572 | 0.24939 | 0.22535 | 0.61575 | 5 | 0.9806 | Slope | 0.86667 | 0.2 |  | 0.01 | 0 | 0.9806 | Slope | 2 | 0.86667 | 0 | 20 | -20 | 0 | 0.00018406 | 0.0042459
90 | 0:15 | 20 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 18.1289 | 0.18129 | 0.18129 | 20 | 0.00093555 | [13 empty] | 0.98666 | 1 | 0.98232 | 0.92427 | 0.81616 | 0.66323 | 0.46547 | 0.24225 | 0.03722 | -0.10538 | -0.19724 | -0.27323 | -0.34601 | -0.40462 | -0.46664 | -0.54268 | -0.63122 | -0.72148 | -0.80312 | -0.8709 | -0.91734 | -0.93002 | -0.89482 | -0.81563 | -0.69571 | -0.55804 | -0.41117 | -0.25919 | -0.1051 | 0.055375 | 0.19019 | 0.0090644 | -0.0046461 | -0.00023231 | -0.00023231 | 0 | 0 | 0.0037553 | 0.05 | -0.62287 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.37736 | 0.53562 | 0.69368 | 0.84307 | 0.98052 | 0.90551 | 0.80074 | 0.70371 | 0.61545 | 0.54946 | 0.50379 | 0.46745 | 0.43615 | 0.41656 | 0.41385 | 0.43396 | 0.47074 | 0.51599 | 0.56986 | 0.63071 | 0.69804 | 0.77635 | 0.86875 | 0.96264 | 0.94497 | 0.85997 | 0.78655 | 0.72708 | 0.68141 | 0.64265 | 0.62379 | 0.98052 | 4 | Slope | 0.9 | 0.45912 | 0.51187 | 0.55345 | 0.59213 | 0.62684 | 0.59073 | 0.54469 | 0.50124 | 0.46071 | 0.4276 | 0.40126 | 0.37804 | 0.35649 | 0.33885 | 0.32684 | 0.32243 | 0.32358 | 0.32755 | 0.3344 | 0.34357 | 0.3549 | 0.3699 | 0.38958 | 0.40977 | 0.39277 | 0.35332 | 0.31774 | 0.28681 | 0.26047 | 0.23644 | 0.21904 | 0.62684 | 4 | 0.98052 | Slope | 0.9 | 0.18129 |  | 0.10262 | 0 | 0.98052 | Slope | 2 | 0.9 | 0 | 20 | -20 | 0.00093555 | 0.00017696 | 0.0037553
91 | 0:15 | 18.1289 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 15.5293 | 0.15529 | 0.15529 | 18.1289 | 0.0012998 | [13 empty] | 0.98232 | 1 | 0.97591 | 0.89716 | 0.76824 | 0.59283 | 0.38576 | 0.18606 | 0.04518 | -0.048458 | -0.12798 | -0.20628 | -0.26752 | -0.32929 | -0.40838 | -0.50626 | -0.61575 | -0.72174 | -0.81613 | -0.88876 | -0.92938 | -0.92465 | -0.87999 | -0.79223 | -0.67577 | -0.54063 | -0.39315 | -0.23754 | -0.069722 | 0.071627 | 0.18872 | 0.0077646 | -0.0030655 | -0.00015328 | -0.00015328 | 0 | 0 | 0.0032754 | 0.05 | -0.46461 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.53554 | 0.6936 | 0.84299 | 0.98044 | 0.90559 | 0.80082 | 0.70379 | 0.61553 | 0.54954 | 0.50387 | 0.46753 | 0.43623 | 0.41664 | 0.41392 | 0.43404 | 0.47082 | 0.51607 | 0.56994 | 0.63079 | 0.69812 | 0.77643 | 0.86883 | 0.96271 | 0.94489 | 0.85989 | 0.78647 | 0.727 | 0.68133 | 0.64257 | 0.62371 | 0.6207 | 0.98044 | 3 | Slope | 0.93333 | 0.51185 | 0.56453 | 0.60322 | 0.63792 | 0.60186 | 0.55583 | 0.51238 | 0.47184 | 0.43873 | 0.4124 | 0.38918 | 0.36763 | 0.34999 | 0.33797 | 0.33357 | 0.33472 | 0.33869 | 0.34554 | 0.35471 | 0.36604 | 0.38103 | 0.40072 | 0.4209 | 0.40385 | 0.36441 | 0.32882 | 0.29789 | 0.27156 | 0.24752 | 0.23012 | 0.21801 | 0.63792 | 3 | 0.98044 | Slope | 0.93333 | 0.15529 |  | 0.2313 | 0 | 0.98044 | Slope | 2 | 0.93333 | 0 | 20 | -20 | 0.0012998 | 0.00017467 | 0.0032754
92 | 0:15 | 15.5293 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 12.1375 | 0.12138 | 0.12138 | 15.5293 | 0.0016959 | [13 empty] | 0.97591 | 1 | 0.96737 | 0.87376 | 0.72613 | 0.54238 | 0.35694 | 0.22033 | 0.13026 | 0.049991 | -0.031794 | -0.097628 | -0.16142 | -0.24106 | -0.34502 | -0.46791 | -0.59861 | -0.72362 | -0.82842 | -0.90054 | -0.92928 | -0.92306 | -0.87686 | -0.79634 | -0.68398 | -0.54846 | -0.39648 | -0.2258 | -0.074784 | 0.049993 | 0.15881 | 0.0060688 | -0.0015716 | -7.8581e-05 | -7.8581e-05 | 0 | 0 | 0.002848 | 0.05 | -0.30655 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.69352 | 0.84292 | 0.98036 | 0.90567 | 0.80089 | 0.70387 | 0.61561 | 0.54961 | 0.50394 | 0.46761 | 0.4363 | 0.41672 | 0.414 | 0.43412 | 0.4709 | 0.51615 | 0.57002 | 0.63087 | 0.6982 | 0.77651 | 0.8689 | 0.96279 | 0.94482 | 0.85981 | 0.78639 | 0.72693 | 0.68126 | 0.64249 | 0.62363 | 0.62062 | 0.62203 | 0.98036 | 2 | Slope | 0.96667 | 0.56451 | 0.61431 | 0.64901 | 0.613 | 0.56696 | 0.52351 | 0.48298 | 0.44987 | 0.42354 | 0.40031 | 0.37877 | 0.36113 | 0.34911 | 0.34471 | 0.34585 | 0.34983 | 0.35667 | 0.36585 | 0.37718 | 0.39217 | 0.41186 | 0.43204 | 0.41494 | 0.37549 | 0.33991 | 0.30898 | 0.28264 | 0.25861 | 0.24121 | 0.2291 | 0.21845 | 0.64901 | 2 | 0.98036 | Slope | 0.96667 | 0.12138 |  | 0.39919 | 0 | 0.98036 | Slope | 2 | 0.96667 | 0 | 20 | -20 | 0.0016959 | 0.00017607 | 0.002848
93 | 0:15 | 12.1375 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 8.8263 | 0.088263 | 0.088263 | 12.1375 | 0.0016556 | [13 empty] | 0.96737 | 1 | 0.96219 | 0.85815 | 0.70635 | 0.54419 | 0.41878 | 0.33288 | 0.25812 | 0.17751 | 0.10956 | 0.041568 | -0.041391 | -0.14752 | -0.27744 | -0.42326 | -0.5763 | -0.71541 | -0.82539 | -0.89342 | -0.92953 | -0.92974 | -0.89522 | -0.82204 | -0.7116 | -0.57317 | -0.40909 | -0.25366 | -0.11807 | -0.0035999 | 0.1035 | 0.0044131 | -0.00019716 | -9.8581e-06 | -9.8581e-06 | 0 | 0 | 0.0025428 | 0.05 | -0.15716 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.84285 | 0.98029 | 0.90573 | 0.80096 | 0.70394 | 0.61567 | 0.54968 | 0.50401 | 0.46767 | 0.43637 | 0.41679 | 0.41407 | 0.43419 | 0.47096 | 0.51622 | 0.57008 | 0.63094 | 0.69827 | 0.77658 | 0.86897 | 0.96286 | 0.94475 | 0.85975 | 0.78632 | 0.72686 | 0.68119 | 0.64243 | 0.62356 | 0.62055 | 0.62196 | 0.63123 | 0.98029 | 1 | Slope | 1 | 0.61428 | 0.6601 | 0.62413 | 0.5781 | 0.53465 | 0.49411 | 0.461 | 0.43467 | 0.41145 | 0.3899 | 0.37226 | 0.36024 | 0.35584 | 0.35699 | 0.36096 | 0.36781 | 0.37698 | 0.38831 | 0.4033 | 0.42299 | 0.44317 | 0.42603 | 0.38658 | 0.351 | 0.32006 | 0.29373 | 0.2697 | 0.2523 | 0.24018 | 0.22954 | 0.22152 | 0.6601 | 1 | 0.98029 | Slope | 1 | 0.088263 |  | 0.5631 | 0 | 0.98029 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0016556 | 0.00017971 | 0.0025428
94 | 0:16 | 8.8263 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 6.4067 | 0.064067 | 0.064067 | 8.8263 | 0.0012098 | [13 empty] | 0.96219 | 1 | 0.95749 | 0.84939 | 0.71279 | 0.60318 | 0.52653 | 0.45776 | 0.38577 | 0.32105 | 0.25501 | 0.17279 | 0.067029 | -0.061647 | -0.21169 | -0.37798 | -0.54517 | -0.69191 | -0.80332 | -0.88336 | -0.92857 | -0.9408 | -0.91689 | -0.85026 | -0.74129 | -0.59576 | -0.4471 | -0.30711 | -0.18222 | -0.070865 | 0.038389 | 0.0032034 | 0.00094256 | 4.7128e-05 | 4.7128e-05 | 0 | 0 | 0.0023368 | 0.05 | -0.019716 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.98024 | 0.90579 | 0.80102 | 0.70399 | 0.61573 | 0.54974 | 0.50407 | 0.46773 | 0.43643 | 0.41684 | 0.41412 | 0.43424 | 0.47102 | 0.51627 | 0.57014 | 0.63099 | 0.69832 | 0.77663 | 0.86903 | 0.96292 | 0.94469 | 0.85969 | 0.78627 | 0.7268 | 0.68113 | 0.64237 | 0.62351 | 0.6205 | 0.6219 | 0.63117 | 0.64338 | 0.98024 | 0 | Slope | 1 | 0.66008 | 0.63526 | 0.58923 | 0.54578 | 0.50524 | 0.47213 | 0.4458 | 0.42258 | 0.40103 | 0.38339 | 0.37137 | 0.36697 | 0.36812 | 0.37209 | 0.37894 | 0.38811 | 0.39944 | 0.41443 | 0.43412 | 0.45431 | 0.43712 | 0.39767 | 0.36209 | 0.33116 | 0.30482 | 0.28079 | 0.26339 | 0.25128 | 0.24063 | 0.23261 | 0.22557 | 0.66008 | 0 | 0.98024 | Slope | 1 | 0.064067 |  | 0.68287 | 0 | 0.98024 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0012098 | 0.00018424 | 0.0023368
95 | 0:16 | 6.4067 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 4.248 | 0.04248 | 0.04248 | 6.4067 | 0.0010794 | [13 empty] | 0.95749 | 1 | 0.95693 | 0.86084 | 0.76927 | 0.70538 | 0.64694 | 0.58323 | 0.52873 | 0.46792 | 0.38885 | 0.28455 | 0.15829 | 0.012151 | -0.15546 | -0.33287 | -0.50734 | -0.6578 | -0.78605 | -0.87877 | -0.93527 | -0.95632 | -0.93874 | -0.87509 | -0.76344 | -0.6326 | -0.49988 | -0.3737 | -0.25356 | -0.14313 | -0.052908 | 0.002124 | 0.0019903 | 9.9515e-05 | 9.9515e-05 | 0 | 0 | 0.0022274 | 0.05 | 0.094256 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.90584 | 0.80107 | 0.70405 | 0.61578 | 0.54979 | 0.50412 | 0.46778 | 0.43648 | 0.4169 | 0.41418 | 0.4343 | 0.47107 | 0.51633 | 0.57019 | 0.63105 | 0.69838 | 0.77669 | 0.86908 | 0.96297 | 0.94464 | 0.85964 | 0.78621 | 0.72675 | 0.68108 | 0.64232 | 0.62345 | 0.62044 | 0.62185 | 0.63112 | 0.64333 | 0.65681 | 0.96297 | 18 | Slope | 0.43333 | 0.63528 | 0.60036 | 0.5569 | 0.51637 | 0.48326 | 0.45693 | 0.43371 | 0.41216 | 0.39452 | 0.3825 | 0.3781 | 0.37925 | 0.38322 | 0.39006 | 0.39924 | 0.41057 | 0.42556 | 0.44525 | 0.46543 | 0.44821 | 0.40877 | 0.37318 | 0.34225 | 0.31592 | 0.29188 | 0.27448 | 0.26237 | 0.25173 | 0.24371 | 0.23667 | 0.23005 | 0.63528 | 0 | 0.90584 | Slope | 1 | 0.04248 |  | 0.78972 | 0 | 0.90584 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0010794 | 0.0001887 | 0.0022274
96 | 0:16 | 4.248 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.7114 | 0.017114 | 0.017114 | 4.248 | 0.0012683 | [13 empty] | 0.95693 | 1 | 0.96307 | 0.90088 | 0.84917 | 0.80305 | 0.75118 | 0.70514 | 0.65575 | 0.58293 | 0.48289 | 0.36059 | 0.21981 | 0.059976 | -0.1141 | -0.29546 | -0.47235 | -0.64064 | -0.78203 | -0.88182 | -0.9412 | -0.96394 | -0.94699 | -0.88282 | -0.78311 | -0.66756 | -0.55178 | -0.4327 | -0.31679 | -0.22841 | -0.12688 | 0.0008557 | 0.0029605 | 0.00014803 | 0.00014803 | 0 | 0 | 0.0022089 | 0.05 | 0.19903 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.80112 | 0.7041 | 0.61583 | 0.54984 | 0.50417 | 0.46783 | 0.43653 | 0.41694 | 0.41423 | 0.43434 | 0.47112 | 0.51637 | 0.57024 | 0.6311 | 0.69842 | 0.77674 | 0.86913 | 0.96302 | 0.94459 | 0.85959 | 0.78617 | 0.7267 | 0.68103 | 0.64227 | 0.6234 | 0.6204 | 0.6218 | 0.63107 | 0.64328 | 0.65676 | 0.66499 | 0.96302 | 17 | Slope | 0.46667 | 0.60037 | 0.56803 | 0.5275 | 0.49439 | 0.46806 | 0.44483 | 0.42329 | 0.40565 | 0.39363 | 0.38923 | 0.39037 | 0.39435 | 0.40119 | 0.41037 | 0.4217 | 0.43669 | 0.45638 | 0.47656 | 0.45931 | 0.41986 | 0.38428 | 0.35334 | 0.32701 | 0.30298 | 0.28558 | 0.27347 | 0.26282 | 0.2548 | 0.24776 | 0.24114 | 0.23277 | 0.60037 | 0 | 0.80112 | Slope | 1 | 0.017114 |  | 0.91529 | 0 | 0.80112 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0012683 | 0.00019218 | 0.0022089
97 | 0:16 | 1.7114 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -1.8716 | -0.018716 | -0.018716 | 1.7114 | 0.0017915 | [13 empty] | 0.96307 | 1 | 0.9778 | 0.94358 | 0.90662 | 0.86693 | 0.83024 | 0.78805 | 0.72569 | 0.6324 | 0.51703 | 0.38308 | 0.23242 | 0.070628 | -0.10425 | -0.28603 | -0.4775 | -0.65428 | -0.79294 | -0.88447 | -0.93585 | -0.95175 | -0.93207 | -0.87154 | -0.78253 | -0.68512 | -0.57769 | -0.46637 | -0.37467 | -0.28178 | -0.17559 | -0.00093578 | 0.0038432 | 0.00019216 | 0.00019216 | 0 | 0 | 0.0022904 | 0.05 | 0.29605 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.70414 | 0.61588 | 0.54988 | 0.50421 | 0.46788 | 0.43657 | 0.41699 | 0.41427 | 0.43439 | 0.47117 | 0.51642 | 0.57029 | 0.63114 | 0.69847 | 0.77678 | 0.86918 | 0.96306 | 0.94455 | 0.85954 | 0.78612 | 0.72666 | 0.68099 | 0.64222 | 0.62336 | 0.62035 | 0.62176 | 0.63103 | 0.64324 | 0.65671 | 0.66494 | 0.6853 | 0.96306 | 16 | Slope | 0.5 | 0.56805 | 0.53863 | 0.50552 | 0.47918 | 0.45596 | 0.43441 | 0.41677 | 0.40476 | 0.40035 | 0.4015 | 0.40547 | 0.41232 | 0.42149 | 0.43282 | 0.44782 | 0.4675 | 0.48769 | 0.4704 | 0.43096 | 0.39537 | 0.36444 | 0.33811 | 0.31407 | 0.29668 | 0.28456 | 0.27392 | 0.2659 | 0.25886 | 0.25224 | 0.24387 | 0.23954 | 0.56805 | 0 | 0.70414 | Slope | 1 | 0.018716 |  | 0.90736 | 0 | 0.70414 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0017915 | 0.0001939 | 0.0022904
98 | 0:16 | -1.8716 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.646 | -0.04646 | -0.04646 | -1.8716 | 0.0013872 | [13 empty] | 0.9778 | 1 | 0.98605 | 0.95994 | 0.92758 | 0.89725 | 0.86193 | 0.80671 | 0.72515 | 0.61856 | 0.49262 | 0.35013 | 0.19762 | 0.032671 | -0.14734 | -0.34051 | -0.53366 | -0.69586 | -0.81553 | -0.88986 | -0.92655 | -0.93538 | -0.90571 | -0.84496 | -0.7686 | -0.67605 | -0.57563 | -0.48445 | -0.3941 | -0.29438 | -0.16953 | -0.002323 | 0.0045031 | 0.00022516 | 0.00022516 | 0 | 0 | 0.002422 | 0.05 | 0.38432 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.61591 | 0.54992 | 0.50425 | 0.46791 | 0.43661 | 0.41702 | 0.4143 | 0.43442 | 0.4712 | 0.51645 | 0.57032 | 0.63117 | 0.6985 | 0.77681 | 0.86921 | 0.96309 | 0.94451 | 0.85951 | 0.78609 | 0.72662 | 0.68095 | 0.64219 | 0.62333 | 0.62032 | 0.62173 | 0.63099 | 0.6432 | 0.65668 | 0.66491 | 0.68526 | 0.72329 | 0.96309 | 15 | Slope | 0.53333 | 0.53864 | 0.51664 | 0.4903 | 0.46708 | 0.44554 | 0.4279 | 0.41588 | 0.41147 | 0.41262 | 0.41659 | 0.42344 | 0.43261 | 0.44394 | 0.45894 | 0.47863 | 0.49881 | 0.4815 | 0.44206 | 0.40647 | 0.37554 | 0.34921 | 0.32517 | 0.30778 | 0.29566 | 0.28502 | 0.277 | 0.26996 | 0.26334 | 0.25497 | 0.25064 | 0.25221 | 0.53864 | 0 | 0.61591 | Slope | 1 | 0.04646 |  | 0.77002 | 0 | 0.61591 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0013872 | 0.00019334 | 0.002422
99 | 0:16 | -4.646 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.6252 | -0.056252 | -0.056252 | -4.646 | 0.00048957 | [13 empty] | 0.98605 | 1 | 0.98798 | 0.96419 | 0.93634 | 0.90542 | 0.85727 | 0.78354 | 0.6887 | 0.57044 | 0.43458 | 0.2874 | 0.12696 | -0.050024 | -0.24218 | -0.43552 | -0.60919 | -0.74784 | -0.84562 | -0.90091 | -0.92792 | -0.91685 | -0.87768 | -0.82289 | -0.74654 | -0.65793 | -0.5716 | -0.484 | -0.38411 | -0.26263 | -0.11634 | -0.0028126 | 0.0049598 | 0.00024799 | 0.00024799 | 0 | 0 | 0.0025433 | 0.05 | 0.45031 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.54994 | 0.50427 | 0.46793 | 0.43663 | 0.41704 | 0.41433 | 0.43444 | 0.47122 | 0.51647 | 0.57034 | 0.6312 | 0.69852 | 0.77684 | 0.86923 | 0.96312 | 0.94449 | 0.85949 | 0.78607 | 0.7266 | 0.68093 | 0.64217 | 0.62331 | 0.6203 | 0.6217 | 0.63097 | 0.64318 | 0.65666 | 0.66489 | 0.68524 | 0.72326 | 0.77984 | 0.96312 | 14 | Slope | 0.56667 | 0.51665 | 0.50142 | 0.4782 | 0.45665 | 0.43901 | 0.427 | 0.42259 | 0.42374 | 0.42771 | 0.43456 | 0.44373 | 0.45506 | 0.47006 | 0.48974 | 0.50993 | 0.49261 | 0.45316 | 0.41758 | 0.38664 | 0.36031 | 0.33628 | 0.31888 | 0.30677 | 0.29612 | 0.2881 | 0.28106 | 0.27444 | 0.26607 | 0.26175 | 0.26331 | 0.27106 | 0.51665 | 0 | 0.54994 | Slope | 1 | 0.056252 |  | 0.72155 | 0 | 0.54994 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00048957 | 0.00019051 | 0.0025433
100 | 0:17 | -5.6252 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.8523 | -0.058523 | -0.058523 | -5.6252 | 0.00011359 | [13 empty] | 0.98798 | 1 | 0.9888 | 0.96748 | 0.93897 | 0.89631 | 0.83044 | 0.74342 | 0.63614 | 0.5069 | 0.36468 | 0.20742 | 0.032426 | -0.15832 | -0.35213 | -0.52662 | -0.67628 | -0.79203 | -0.8694 | -0.91413 | -0.91777 | -0.89363 | -0.85711 | -0.79987 | -0.72552 | -0.64773 | -0.56487 | -0.46693 | -0.34468 | -0.19995 | -0.031491 | -0.0029262 | 0.0053232 | 0.00026616 | 0.00026616 | 0 | 0 | 0.0026463 | 0.05 | 0.49598 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.50429 | 0.46795 | 0.43665 | 0.41706 | 0.41434 | 0.43446 | 0.47124 | 0.51649 | 0.57036 | 0.63121 | 0.69854 | 0.77685 | 0.86925 | 0.96313 | 0.94447 | 0.85947 | 0.78605 | 0.72658 | 0.68091 | 0.64215 | 0.62329 | 0.62028 | 0.62168 | 0.63095 | 0.64316 | 0.65664 | 0.66487 | 0.68522 | 0.72325 | 0.77982 | 0.84799 | 0.96313 | 13 | Slope | 0.6 | 0.50143 | 0.48932 | 0.46777 | 0.45013 | 0.43811 | 0.43371 | 0.43486 | 0.43883 | 0.44568 | 0.45485 | 0.46618 | 0.48117 | 0.50086 | 0.52104 | 0.50371 | 0.46427 | 0.42868 | 0.39775 | 0.37142 | 0.34738 | 0.32998 | 0.31787 | 0.30723 | 0.29921 | 0.29217 | 0.28555 | 0.27718 | 0.27285 | 0.27442 | 0.28216 | 0.29377 | 0.52104 | 13 | 0.96313 | Slope | 0.6 | 0.058523 |  | 0.71031 | 0 | 0.96313 | Slope | 2 | 0.6 | 0 | 20 | -20 | 0.00011359 | 0.00018574 | 0.0026463
101 | 0:17 | -5.8523 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -6.9403 | -0.069403 | -0.069403 | -5.8523 | 0.00054398 | [13 empty] | 0.9888 | 1 | 0.9902 | 0.96869 | 0.93007 | 0.87079 | 0.79188 | 0.6923 | 0.57355 | 0.4372 | 0.28427 | 0.11225 | -0.077887 | -0.27235 | -0.44912 | -0.60052 | -0.72758 | -0.82289 | -0.88934 | -0.90965 | -0.89895 | -0.87587 | -0.83582 | -0.77941 | -0.71402 | -0.63901 | -0.546 | -0.4263 | -0.28099 | -0.11363 | 0.077961 | -0.0034702 | 0.0056362 | 0.00028181 | 0.00028181 | 0 | 0 | 0.0027348 | 0.05 | 0.53232 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.46797 | 0.43666 | 0.41708 | 0.41436 | 0.43448 | 0.47126 | 0.51651 | 0.57038 | 0.63123 | 0.69856 | 0.77687 | 0.86927 | 0.96315 | 0.94446 | 0.85945 | 0.78603 | 0.72657 | 0.6809 | 0.64213 | 0.62327 | 0.62026 | 0.62167 | 0.63094 | 0.64315 | 0.65662 | 0.66485 | 0.68521 | 0.72323 | 0.77981 | 0.84797 | 0.92681 | 0.96315 | 12 | Slope | 0.63333 | 0.48932 | 0.47889 | 0.46125 | 0.44923 | 0.44483 | 0.44597 | 0.44995 | 0.45679 | 0.46597 | 0.4773 | 0.49229 | 0.51198 | 0.53216 | 0.51482 | 0.47537 | 0.43979 | 0.40886 | 0.38252 | 0.35849 | 0.34109 | 0.32898 | 0.31833 | 0.31031 | 0.30327 | 0.29665 | 0.28828 | 0.28396 | 0.28552 | 0.29327 | 0.30488 | 0.32005 | 0.53216 | 12 | 0.96315 | Slope | 0.63333 | 0.069403 |  | 0.65645 | 0 | 0.96315 | Slope | 2 | 0.63333 | 0 | 20 | -20 | 0.00054398 | 0.00017939 | 0.0027348
102 | 0:17 | -6.9403 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.6022 | -0.076022 | -0.076022 | -6.9403 | 0.00033093 | [13 empty] | 0.9902 | 1 | 0.98937 | 0.95867 | 0.90433 | 0.83214 | 0.74007 | 0.62803 | 0.50036 | 0.3508 | 0.17992 | -0.0089551 | -0.20418 | -0.38216 | -0.5364 | -0.66563 | -0.77218 | -0.85653 | -0.89562 | -0.89852 | -0.88625 | -0.85777 | -0.81696 | -0.76621 | -0.70358 | -0.6173 | -0.50158 | -0.35663 | -0.18678 | 0.0058381 | 0.21282 | -0.0038011 | 0.005832 | 0.0002916 | 0.0002916 | 0 | 0 | 0.0027937 | 0.05 | 0.56362 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.43667 | 0.41709 | 0.41437 | 0.43449 | 0.47127 | 0.51652 | 0.57039 | 0.63124 | 0.69857 | 0.77688 | 0.86928 | 0.96316 | 0.94445 | 0.85944 | 0.78602 | 0.72656 | 0.68089 | 0.64212 | 0.62326 | 0.62025 | 0.62166 | 0.63093 | 0.64314 | 0.65661 | 0.66484 | 0.6852 | 0.72322 | 0.7798 | 0.84796 | 0.9268 | 0.98552 | 0.98552 | 30 | Slope | 0.033333 | 0.47889 | 0.47236 | 0.46035 | 0.45594 | 0.45709 | 0.46106 | 0.46791 | 0.47708 | 0.48841 | 0.5034 | 0.52309 | 0.54328 | 0.52593 | 0.48648 | 0.4509 | 0.41996 | 0.39363 | 0.3696 | 0.3522 | 0.34008 | 0.32944 | 0.32142 | 0.31438 | 0.30776 | 0.29939 | 0.29507 | 0.29663 | 0.30438 | 0.31599 | 0.33116 | 0.33962 | 0.54328 | 11 | 0.96316 | Slope | 0.66667 | 0.076022 |  | 0.62369 | 0 | 0.96316 | Slope | 2 | 0.66667 | 0 | 20 | -20 | 0.00033093 | 0.00017187 | 0.0027937
103 | 0:17 | -7.6022 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.928 | -0.07928 | -0.07928 | -7.6022 | 0.0001629 | [13 empty] | 0.98937 | 1 | 0.9848 | 0.94224 | 0.87663 | 0.79203 | 0.6875 | 0.56527 | 0.4229 | 0.25335 | 0.064231 | -0.13119 | -0.31208 | -0.4714 | -0.60748 | -0.71979 | -0.81775 | -0.87561 | -0.89681 | -0.89592 | -0.87764 | -0.84728 | -0.80828 | -0.75973 | -0.68653 | -0.57953 | -0.43906 | -0.26943 | -0.073905 | 0.1358 | 0.34654 | -0.003964 | 0.0058592 | 0.00029296 | 0.00029296 | 0 | 0 | 0.0028014 | 0.05 | 0.5832 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.41709 | 0.41437 | 0.43449 | 0.47127 | 0.51652 | 0.57039 | 0.63124 | 0.69857 | 0.77688 | 0.86928 | 0.96316 | 0.94445 | 0.85944 | 0.78602 | 0.72656 | 0.68089 | 0.64212 | 0.62326 | 0.62025 | 0.62166 | 0.63093 | 0.64314 | 0.65661 | 0.66484 | 0.6852 | 0.72322 | 0.7798 | 0.84796 | 0.9268 | 0.98552 | 0.89633 | 0.98552 | 29 | Slope | 0.066667 | 0.47236 | 0.47146 | 0.46705 | 0.4682 | 0.47217 | 0.47902 | 0.48819 | 0.49952 | 0.51452 | 0.5342 | 0.55439 | 0.53704 | 0.49759 | 0.46201 | 0.43107 | 0.40474 | 0.38071 | 0.36331 | 0.35119 | 0.34055 | 0.33253 | 0.32549 | 0.31887 | 0.3105 | 0.30618 | 0.30774 | 0.31549 | 0.3271 | 0.34227 | 0.35073 | 0.30989 | 0.55439 | 10 | 0.96316 | Slope | 0.7 | 0.07928 |  | 0.60757 | 0 | 0.96316 | Slope | 2 | 0.7 | 0 | 20 | -20 | 0.0001629 | 0.00016378 | 0.0028014
104 | 0:17 | -7.928 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.8153 | -0.078153 | -0.078153 | -7.928 | 5.6333e-05 | [13 empty] | 0.9848 | 1 | 0.9808 | 0.9311 | 0.85595 | 0.76073 | 0.64618 | 0.50967 | 0.34783 | 0.16014 | -0.03602 | -0.2198 | -0.38821 | -0.53629 | -0.66183 | -0.76965 | -0.84536 | -0.88751 | -0.90316 | -0.89702 | -0.87638 | -0.84346 | -0.80613 | -0.75039 | -0.66259 | -0.53528 | -0.37317 | -0.18043 | 0.031805 | 0.24895 | 0.46799 | -0.0039077 | 0.005658 | 0.0002829 | 0.0002829 | 0 | 0 | 0.0027551 | 0.05 | 0.58592 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.41436 | 0.43448 | 0.47126 | 0.51651 | 0.57038 | 0.63123 | 0.69856 | 0.77687 | 0.86927 | 0.96315 | 0.94446 | 0.85945 | 0.78603 | 0.72657 | 0.6809 | 0.64213 | 0.62327 | 0.62026 | 0.62167 | 0.63094 | 0.64315 | 0.65662 | 0.66485 | 0.68521 | 0.72323 | 0.77981 | 0.84797 | 0.92681 | 0.98551 | 0.89632 | 0.81498 | 0.98551 | 28 | Slope | 0.1 | 0.47145 | 0.47816 | 0.47931 | 0.48328 | 0.49013 | 0.4993 | 0.51063 | 0.52562 | 0.54531 | 0.56549 | 0.54815 | 0.50871 | 0.47312 | 0.44219 | 0.41585 | 0.39182 | 0.37442 | 0.36231 | 0.35167 | 0.34365 | 0.3366 | 0.32999 | 0.32162 | 0.31729 | 0.31885 | 0.3266 | 0.33821 | 0.35338 | 0.36184 | 0.321 | 0.28277 | 0.56549 | 9 | 0.96315 | Slope | 0.73333 | 0.078153 |  | 0.61314 | 0 | 0.96315 | Slope | 2 | 0.73333 | 0 | 20 | -20 | 5.6333e-05 | 0.00015576 | 0.0027551
105 | 0:17 | -7.8153 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.5096 | -0.075096 | -0.075096 | -7.8153 | 0.00015285 | [13 empty] | 0.9808 | 1 | 0.9786 | 0.92326 | 0.84032 | 0.73685 | 0.61055 | 0.45793 | 0.27969 | 0.084947 | -0.10174 | -0.2772 | -0.43932 | -0.58171 | -0.70574 | -0.79532 | -0.85792 | -0.89377 | -0.90564 | -0.89741 | -0.87142 | -0.8399 | -0.79942 | -0.73612 | -0.63459 | -0.49061 | -0.3094 | -0.10189 | 0.11888 | 0.34873 | 0.56866 | -0.0037548 | 0.0052903 | 0.00026451 | 0.00026451 | 0 | 0 | 0.0026901 | 0.05 | 0.5658 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.43446 | 0.47124 | 0.51649 | 0.57036 | 0.63121 | 0.69854 | 0.77685 | 0.86925 | 0.96313 | 0.94447 | 0.85947 | 0.78605 | 0.72659 | 0.68091 | 0.64215 | 0.62329 | 0.62028 | 0.62169 | 0.63096 | 0.64317 | 0.65664 | 0.66487 | 0.68522 | 0.72325 | 0.77982 | 0.84799 | 0.92683 | 0.98549 | 0.8963 | 0.81496 | 0.75396 | 0.98549 | 27 | Slope | 0.13333 | 0.47815 | 0.49041 | 0.49439 | 0.50123 | 0.5104 | 0.52174 | 0.53673 | 0.55642 | 0.5766 | 0.55927 | 0.51982 | 0.48424 | 0.45331 | 0.42697 | 0.40294 | 0.38554 | 0.37343 | 0.36278 | 0.35476 | 0.34772 | 0.3411 | 0.33273 | 0.32841 | 0.32997 | 0.33772 | 0.34933 | 0.3645 | 0.37294 | 0.3321 | 0.29388 | 0.26243 | 0.5766 | 8 | 0.96313 | Slope | 0.76667 | 0.075096 |  | 0.62827 | 0 | 0.96313 | Slope | 2 | 0.76667 | 0 | 20 | -20 | 0.00015285 | 0.00014854 | 0.0026901
106 | 0:18 | -7.5096 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.48 | -0.0748 | -0.0748 | -7.5096 | 1.4787e-05 | [13 empty] | 0.9786 | 1 | 0.97658 | 0.91623 | 0.82704 | 0.71472 | 0.57667 | 0.409 | 0.22303 | 0.035432 | -0.14479 | -0.31617 | -0.47507 | -0.6175 | -0.72595 | -0.80404 | -0.86012 | -0.89343 | -0.90384 | -0.8891 | -0.86448 | -0.8326 | -0.78958 | -0.71815 | -0.60469 | -0.44487 | -0.25044 | -0.034931 | 0.19881 | 0.4342 | 0.62241 | -0.00374 | 0.0048377 | 0.00024189 | 0.00024189 | 0 | 0 | 0.0026256 | 0.05 | 0.52903 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.47122 | 0.51647 | 0.57034 | 0.63119 | 0.69852 | 0.77683 | 0.86923 | 0.96311 | 0.9445 | 0.85949 | 0.78607 | 0.72661 | 0.68094 | 0.64217 | 0.62331 | 0.6203 | 0.62171 | 0.63098 | 0.64319 | 0.65666 | 0.66489 | 0.68525 | 0.72327 | 0.77985 | 0.84801 | 0.92685 | 0.98547 | 0.89628 | 0.81494 | 0.75394 | 0.71288 | 0.98547 | 26 | Slope | 0.16667 | 0.49041 | 0.50549 | 0.51233 | 0.52151 | 0.53284 | 0.54783 | 0.56752 | 0.5877 | 0.57039 | 0.53094 | 0.49536 | 0.46442 | 0.43809 | 0.41406 | 0.39666 | 0.38455 | 0.3739 | 0.36588 | 0.35884 | 0.35222 | 0.34385 | 0.33953 | 0.34109 | 0.34884 | 0.36045 | 0.37562 | 0.38405 | 0.3432 | 0.30498 | 0.27354 | 0.24874 | 0.5877 | 7 | 0.96311 | Slope | 0.8 | 0.0748 |  | 0.62974 | 0 | 0.96311 | Slope | 2 | 0.8 | 0 | 20 | -20 | 1.4787e-05 | 0.00014273 | 0.0026256
107 | 0:18 | -7.48 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.4505 | -0.074505 | -0.074505 | -7.48 | 1.4787e-05 | [13 empty] | 0.97658 | 1 | 0.97473 | 0.91034 | 0.81483 | 0.69458 | 0.54302 | 0.36695 | 0.18619 | 0.003854 | -0.1737 | -0.34353 | -0.50366 | -0.63229 | -0.73017 | -0.80109 | -0.85538 | -0.88775 | -0.89045 | -0.87754 | -0.85478 | -0.82423 | -0.77732 | -0.69842 | -0.57269 | -0.40118 | -0.19948 | 0.028261 | 0.27073 | 0.47903 | 0.63388 | -0.0037252 | 0.0042991 | 0.00021495 | 0.00021495 | 0 | 0 | 0.0025624 | 0.05 | 0.48377 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.51644 | 0.57031 | 0.63116 | 0.69849 | 0.7768 | 0.8692 | 0.96308 | 0.94452 | 0.85952 | 0.7861 | 0.72663 | 0.68096 | 0.6422 | 0.62334 | 0.62033 | 0.62174 | 0.631 | 0.64322 | 0.65669 | 0.66492 | 0.68527 | 0.7233 | 0.77987 | 0.84804 | 0.92688 | 0.98544 | 0.89625 | 0.81491 | 0.75391 | 0.71285 | 0.68408 | 0.98544 | 25 | Slope | 0.2 | 0.50548 | 0.52344 | 0.53261 | 0.54394 | 0.55893 | 0.57862 | 0.59881 | 0.58151 | 0.54206 | 0.50648 | 0.47554 | 0.44921 | 0.42518 | 0.40778 | 0.39567 | 0.38502 | 0.377 | 0.36996 | 0.36334 | 0.35497 | 0.35065 | 0.35221 | 0.35996 | 0.37157 | 0.38674 | 0.39515 | 0.35431 | 0.31608 | 0.28464 | 0.25984 | 0.23914 | 0.59881 | 6 | 0.96308 | Slope | 0.83333 | 0.074505 |  | 0.6312 | 0 | 0.96308 | Slope | 2 | 0.83333 | 0 | 20 | -20 | 1.4787e-05 | 0.00013858 | 0.0025624
108 | 0:18 | -7.4505 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.7507 | -0.077507 | -0.077507 | -7.4505 | 0.00015014 | [13 empty] | 0.97473 | 1 | 0.97337 | 0.90559 | 0.80603 | 0.67399 | 0.51349 | 0.34072 | 0.16458 | -0.015833 | -0.19285 | -0.36456 | -0.51227 | -0.63091 | -0.721 | -0.79047 | -0.84421 | -0.86788 | -0.87318 | -0.86415 | -0.84605 | -0.81491 | -0.76438 | -0.67695 | -0.54158 | -0.36407 | -0.15198 | 0.086156 | 0.3061 | 0.48225 | 0.62486 | -0.0038754 | 0.0036905 | 0.00018453 | 0.00018453 | 0 | 0 | 0.0025038 | 0.05 | 0.42991 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.57028 | 0.63113 | 0.69846 | 0.77677 | 0.86917 | 0.96305 | 0.94455 | 0.85955 | 0.78613 | 0.72667 | 0.68099 | 0.64223 | 0.62337 | 0.62036 | 0.62177 | 0.63104 | 0.64325 | 0.65672 | 0.66495 | 0.6853 | 0.72333 | 0.7799 | 0.84807 | 0.92691 | 0.98541 | 0.89622 | 0.81488 | 0.75388 | 0.71282 | 0.68405 | 0.66556 | 0.98541 | 24 | Slope | 0.23333 | 0.52343 | 0.54371 | 0.55504 | 0.57004 | 0.58972 | 0.60991 | 0.59263 | 0.55318 | 0.5176 | 0.48667 | 0.46033 | 0.4363 | 0.4189 | 0.40679 | 0.39614 | 0.38812 | 0.38108 | 0.37446 | 0.36609 | 0.36177 | 0.36333 | 0.37108 | 0.38269 | 0.39786 | 0.40625 | 0.36541 | 0.32718 | 0.29574 | 0.27094 | 0.25024 | 0.23297 | 0.60991 | 5 | 0.96305 | Slope | 0.86667 | 0.077507 |  | 0.61634 | 0 | 0.96305 | Slope | 2 | 0.86667 | 0 | 20 | -20 | 0.00015014 | 0.00013616 | 0.0025038
109 | 0:18 | -7.7507 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -8.6071 | -0.086071 | -0.086071 | -7.7507 | 0.0004282 | [13 empty] | 0.97337 | 1 | 0.97221 | 0.90298 | 0.79278 | 0.65102 | 0.49212 | 0.32377 | 0.14956 | -0.030691 | -0.21017 | -0.36965 | -0.50703 | -0.61728 | -0.70591 | -0.77494 | -0.81888 | -0.84663 | -0.85683 | -0.85424 | -0.83683 | -0.80399 | -0.74726 | -0.65144 | -0.51092 | -0.32508 | -0.1025 | 0.11645 | 0.30513 | 0.4686 | 0.6064 | -0.0043036 | 0.0030172 | 0.00015086 | 0.00015086 | 0 | 0 | 0.0024411 | 0.05 | 0.36905 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.6311 | 0.69843 | 0.77674 | 0.86913 | 0.96302 | 0.94459 | 0.85958 | 0.78616 | 0.7267 | 0.68103 | 0.64227 | 0.6234 | 0.62039 | 0.6218 | 0.63107 | 0.64328 | 0.65676 | 0.66498 | 0.68534 | 0.72336 | 0.77994 | 0.8481 | 0.92694 | 0.98538 | 0.89619 | 0.81485 | 0.75385 | 0.71278 | 0.68401 | 0.66553 | 0.65869 | 0.98538 | 23 | Slope | 0.26667 | 0.5437 | 0.56614 | 0.58113 | 0.60082 | 0.62101 | 0.60375 | 0.56431 | 0.52872 | 0.49779 | 0.47145 | 0.44742 | 0.43002 | 0.41791 | 0.40727 | 0.39925 | 0.3922 | 0.38559 | 0.37722 | 0.37289 | 0.37445 | 0.3822 | 0.39381 | 0.40898 | 0.41735 | 0.37651 | 0.33828 | 0.30684 | 0.28204 | 0.26134 | 0.24407 | 0.23067 | 0.62101 | 4 | 0.96302 | Slope | 0.9 | 0.086071 |  | 0.57395 | 0 | 0.96302 | Slope | 2 | 0.9 | 0 | 20 | -20 | 0.0004282 | 0.00013536 | 0.0024411
110 | 0:18 | -8.6071 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -10.0375 | -0.10037 | -0.10037 | -8.6071 | 0.00071517 | [13 empty] | 0.97221 | 1 | 0.97206 | 0.89467 | 0.7754 | 0.63489 | 0.48017 | 0.3134 | 0.13875 | -0.045193 | -0.21195 | -0.36001 | -0.48804 | -0.59672 | -0.68527 | -0.7423 | -0.79298 | -0.82641 | -0.8447 | -0.84318 | -0.82574 | -0.78901 | -0.72532 | -0.62473 | -0.4767 | -0.28017 | -0.075684 | 0.11106 | 0.28608 | 0.44377 | 0.58004 | -0.0050187 | 0.0022341 | 0.00011171 | 0.00011171 | 0 | 0 | 0.0023621 | 0.05 | 0.30172 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.69839 | 0.7767 | 0.8691 | 0.96298 | 0.94463 | 0.85962 | 0.7862 | 0.72674 | 0.68107 | 0.6423 | 0.62344 | 0.62043 | 0.62184 | 0.63111 | 0.64332 | 0.65679 | 0.66502 | 0.68538 | 0.7234 | 0.77998 | 0.84814 | 0.92698 | 0.98534 | 0.89615 | 0.81481 | 0.75381 | 0.71275 | 0.68397 | 0.66549 | 0.65865 | 0.66213 | 0.98534 | 22 | Slope | 0.3 | 0.56613 | 0.59223 | 0.61192 | 0.6321 | 0.61488 | 0.57543 | 0.53985 | 0.50891 | 0.48258 | 0.45855 | 0.44115 | 0.42903 | 0.41839 | 0.41037 | 0.40333 | 0.39671 | 0.38834 | 0.38401 | 0.38558 | 0.39333 | 0.40494 | 0.4201 | 0.42845 | 0.38761 | 0.34938 | 0.31794 | 0.29314 | 0.27244 | 0.25516 | 0.24177 | 0.23182 | 0.6321 | 3 | 0.96298 | Slope | 0.93333 | 0.10037 |  | 0.50315 | 0 | 0.96298 | Slope | 2 | 0.93333 | 0 | 20 | -20 | 0.00071517 | 0.00013598 | 0.0023621
111 | 0:18 | -10.0375 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -9.2688 | -0.092688 | -0.092688 | -10.0375 | 0.00038433 | [13 empty] | 0.97206 | 1 | 0.96833 | 0.88466 | 0.76773 | 0.63111 | 0.47726 | 0.30878 | 0.12792 | -0.042389 | -0.19631 | -0.33445 | -0.46139 | -0.5714 | -0.6458 | -0.71402 | -0.77092 | -0.81363 | -0.83199 | -0.8316 | -0.81233 | -0.76951 | -0.70057 | -0.59175 | -0.43349 | -0.25696 | -0.087586 | 0.084356 | 0.25277 | 0.40868 | 0.54722 | -0.0046344 | 0.0013102 | 6.5508e-05 | 6.5508e-05 | 0 | 0 | 0.0022415 | 0.05 | 0.22341 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.77665 | 0.86905 | 0.96293 | 0.94467 | 0.85967 | 0.78625 | 0.72678 | 0.68111 | 0.64235 | 0.62349 | 0.62048 | 0.62188 | 0.63115 | 0.64336 | 0.65684 | 0.66507 | 0.68542 | 0.72345 | 0.78002 | 0.84819 | 0.92703 | 0.98529 | 0.8961 | 0.81476 | 0.75376 | 0.7127 | 0.68393 | 0.66545 | 0.6586 | 0.66208 | 0.67203 | 0.98529 | 21 | Slope | 0.33333 | 0.59222 | 0.62302 | 0.6432 | 0.626 | 0.58656 | 0.55097 | 0.52004 | 0.4937 | 0.46967 | 0.45227 | 0.44016 | 0.42952 | 0.4215 | 0.41445 | 0.40784 | 0.39947 | 0.39514 | 0.3967 | 0.40445 | 0.41606 | 0.43123 | 0.43954 | 0.3987 | 0.36048 | 0.32903 | 0.30423 | 0.28353 | 0.26626 | 0.25287 | 0.24292 | 0.23512 | 0.6432 | 2 | 0.96293 | Slope | 0.96667 | 0.092688 |  | 0.54119 | 0 | 0.96293 | Slope | 2 | 0.96667 | 0 | 20 | -20 | 0.00038433 | 0.00013775 | 0.0022415
112 | 0:19 | -9.2688 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.9818 | -0.079818 | -0.079818 | -9.2688 | 0.00064352 | [13 empty] | 0.96833 | 1 | 0.9665 | 0.88589 | 0.77326 | 0.638 | 0.48298 | 0.30984 | 0.14205 | -0.015002 | -0.15674 | -0.29278 | -0.42024 | -0.51435 | -0.60002 | -0.67635 | -0.74703 | -0.79486 | -0.81942 | -0.82253 | -0.80144 | -0.75566 | -0.68045 | -0.56187 | -0.4222 | -0.28108 | -0.12817 | 0.03548 | 0.20075 | 0.35803 | 0.49519 | -0.0039909 | 0.00037132 | 1.8566e-05 | 1.8566e-05 | 0 | 0 | 0.0021569 | 0.05 | 0.13102 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.869 | 0.96289 | 0.94472 | 0.85972 | 0.7863 | 0.72683 | 0.68116 | 0.6424 | 0.62353 | 0.62053 | 0.62193 | 0.6312 | 0.64341 | 0.65689 | 0.66512 | 0.68547 | 0.72349 | 0.78007 | 0.84823 | 0.92707 | 0.98525 | 0.89606 | 0.81472 | 0.75372 | 0.71265 | 0.68388 | 0.6654 | 0.65856 | 0.66204 | 0.67198 | 0.68911 | 0.98525 | 20 | Slope | 0.36667 | 0.623 | 0.6543 | 0.63713 | 0.59768 | 0.5621 | 0.53117 | 0.50483 | 0.4808 | 0.4634 | 0.45129 | 0.44064 | 0.43262 | 0.42558 | 0.41896 | 0.41059 | 0.40627 | 0.40783 | 0.41558 | 0.42719 | 0.44236 | 0.45064 | 0.4098 | 0.37157 | 0.34013 | 0.31533 | 0.29463 | 0.27736 | 0.26396 | 0.25401 | 0.24622 | 0.24081 | 0.6543 | 1 | 0.96289 | Slope | 1 | 0.079818 |  | 0.6049 | 0 | 0.96289 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00064352 | 0.00014028 | 0.0021569
113 | 0:19 | -7.9818 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -6.4345 | -0.064345 | -0.064345 | -7.9818 | 0.00077365 | [13 empty] | 0.9665 | 1 | 0.96875 | 0.89186 | 0.78067 | 0.64496 | 0.48833 | 0.32716 | 0.17311 | 0.031533 | -0.10576 | -0.2393 | -0.34784 | -0.45055 | -0.54535 | -0.63915 | -0.72032 | -0.77979 | -0.81357 | -0.81949 | -0.79778 | -0.74688 | -0.66009 | -0.55566 | -0.44937 | -0.32559 | -0.18285 | -0.025033 | 0.13843 | 0.29182 | 0.42685 | -0.0032172 | -0.00055261 | -2.7631e-05 | -2.7631e-05 | 0 | 0 | 0.0021352 | 0.05 | 0.037132 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.96284 | 0.94477 | 0.85976 | 0.78634 | 0.72688 | 0.68121 | 0.64244 | 0.62358 | 0.62057 | 0.62198 | 0.63125 | 0.64346 | 0.65693 | 0.66516 | 0.68552 | 0.72354 | 0.78012 | 0.84828 | 0.92712 | 0.9852 | 0.89601 | 0.81467 | 0.75367 | 0.71261 | 0.68383 | 0.66535 | 0.65851 | 0.66199 | 0.67194 | 0.68906 | 0.71227 | 0.9852 | 19 | Slope | 0.4 | 0.65428 | 0.64826 | 0.60881 | 0.57323 | 0.54229 | 0.51596 | 0.49193 | 0.47453 | 0.46241 | 0.45177 | 0.44375 | 0.43671 | 0.43009 | 0.42172 | 0.41739 | 0.41896 | 0.42671 | 0.43832 | 0.45348 | 0.46173 | 0.42089 | 0.38267 | 0.35122 | 0.32642 | 0.30572 | 0.28845 | 0.27506 | 0.26511 | 0.25731 | 0.25191 | 0.24853 | 0.65428 | 0 | 0.96284 | Slope | 1 | 0.064345 |  | 0.68149 | 0 | 0.96284 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00077365 | 0.00014279 | 0.0021352
114 | 0:19 | -6.4345 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.521 | -0.05521 | -0.05521 | -6.4345 | 0.00045672 | [13 empty] | 0.96875 | 1 | 0.96964 | 0.89298 | 0.78113 | 0.64575 | 0.49843 | 0.34996 | 0.21275 | 0.07725 | -0.055033 | -0.1682 | -0.28166 | -0.39295 | -0.50619 | -0.6132 | -0.70852 | -0.7798 | -0.81828 | -0.82459 | -0.79924 | -0.73469 | -0.65379 | -0.57578 | -0.48451 | -0.37055 | -0.23493 | -0.081606 | 0.075527 | 0.2246 | 0.37195 | -0.0027605 | -0.0014026 | -7.0132e-05 | -7.0132e-05 | 0 | 0 | 0.002166 | 0.05 | -0.055261 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.94481 | 0.85981 | 0.78638 | 0.72692 | 0.68125 | 0.64249 | 0.62362 | 0.62061 | 0.62202 | 0.63129 | 0.6435 | 0.65698 | 0.66521 | 0.68556 | 0.72358 | 0.78016 | 0.84832 | 0.92716 | 0.98516 | 0.89597 | 0.81463 | 0.75363 | 0.71256 | 0.68379 | 0.66531 | 0.65847 | 0.66195 | 0.67189 | 0.68902 | 0.71222 | 0.74877 | 0.98516 | 18 | Slope | 0.43333 | 0.64827 | 0.61994 | 0.58435 | 0.55342 | 0.52708 | 0.50305 | 0.48565 | 0.47354 | 0.4629 | 0.45487 | 0.44783 | 0.44121 | 0.43285 | 0.42852 | 0.43008 | 0.43783 | 0.44944 | 0.46461 | 0.47283 | 0.43199 | 0.39376 | 0.36232 | 0.33752 | 0.31682 | 0.29955 | 0.28616 | 0.2762 | 0.26841 | 0.26301 | 0.25963 | 0.2607 | 0.64827 | 0 | 0.94481 | Slope | 1 | 0.05521 |  | 0.72671 | 0 | 0.94481 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00045672 | 0.00014456 | 0.002166
115 | 0:19 | -5.521 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.6076 | -0.046076 | -0.046076 | -5.521 | 0.00045672 | [13 empty] | 0.96964 | 1 | 0.96953 | 0.89218 | 0.78047 | 0.652 | 0.5155 | 0.3816 | 0.25013 | 0.11912 | 0.004667 | -0.11333 | -0.2336 | -0.36078 | -0.48599 | -0.60644 | -0.71261 | -0.78731 | -0.8261 | -0.83177 | -0.79523 | -0.73046 | -0.66845 | -0.60254 | -0.52002 | -0.413 | -0.28193 | -0.13513 | 0.017333 | 0.17603 | 0.33729 | -0.0023038 | -0.0021369 | -0.00010684 | -0.00010684 | 0 | 0 | 0.0021934 | 0.05 | -0.14026 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.85984 | 0.78642 | 0.72696 | 0.68129 | 0.64252 | 0.62366 | 0.62065 | 0.62206 | 0.63133 | 0.64354 | 0.65701 | 0.66524 | 0.6856 | 0.72362 | 0.78019 | 0.84836 | 0.9272 | 0.98512 | 0.89593 | 0.81459 | 0.75359 | 0.71253 | 0.68376 | 0.66527 | 0.65843 | 0.66191 | 0.67186 | 0.68898 | 0.71219 | 0.74873 | 0.7998 | 0.98512 | 17 | Slope | 0.46667 | 0.61995 | 0.59547 | 0.56454 | 0.53821 | 0.51417 | 0.49678 | 0.48466 | 0.47402 | 0.466 | 0.45896 | 0.45234 | 0.44397 | 0.43964 | 0.44121 | 0.44895 | 0.46056 | 0.47573 | 0.48393 | 0.44309 | 0.40486 | 0.37342 | 0.34862 | 0.32792 | 0.31065 | 0.29725 | 0.2873 | 0.27951 | 0.2741 | 0.27073 | 0.2718 | 0.27771 | 0.61995 | 0 | 0.85984 | Slope | 1 | 0.046076 |  | 0.77193 | 0 | 0.85984 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00045672 | 0.0001452 | 0.0021934
116 | 0:19 | -4.6076 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -3.6729 | -0.036729 | -0.036729 | -4.6076 | 0.00046732 | [13 empty] | 0.96953 | 1 | 0.9693 | 0.89191 | 0.78521 | 0.66577 | 0.54093 | 0.41224 | 0.28432 | 0.16776 | 0.048055 | -0.074749 | -0.20756 | -0.34465 | -0.48197 | -0.61192 | -0.72031 | -0.79546 | -0.83713 | -0.83561 | -0.79378 | -0.74063 | -0.68833 | -0.63049 | -0.55479 | -0.45219 | -0.32755 | -0.18552 | -0.02677 | 0.14232 | 0.31564 | -0.0018365 | -0.0027315 | -0.00013658 | -0.00013658 | 0 | 0 | 0.0022093 | 0.05 | -0.21369 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.78645 | 0.72699 | 0.68132 | 0.64255 | 0.62369 | 0.62068 | 0.62209 | 0.63136 | 0.64357 | 0.65704 | 0.66527 | 0.68563 | 0.72365 | 0.78022 | 0.84839 | 0.92723 | 0.98509 | 0.8959 | 0.81456 | 0.75356 | 0.7125 | 0.68373 | 0.66524 | 0.6584 | 0.66188 | 0.67183 | 0.68895 | 0.71216 | 0.7487 | 0.79977 | 0.85721 | 0.98509 | 16 | Slope | 0.5 | 0.59548 | 0.57566 | 0.54933 | 0.5253 | 0.5079 | 0.49578 | 0.48514 | 0.47712 | 0.47008 | 0.46346 | 0.45509 | 0.45076 | 0.45233 | 0.46007 | 0.47169 | 0.48685 | 0.49503 | 0.45419 | 0.41596 | 0.38452 | 0.35972 | 0.33902 | 0.32175 | 0.30836 | 0.2984 | 0.29061 | 0.28521 | 0.28183 | 0.2829 | 0.28881 | 0.29685 | 0.59548 | 0 | 0.78645 | Slope | 1 | 0.036729 |  | 0.81819 | 0 | 0.78645 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00046732 | 0.00014459 | 0.0022093
117 | 0:19 | -3.6729 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -3.2139 | -0.032139 | -0.032139 | -3.6729 | 0.00022952 | [13 empty] | 0.9693 | 1 | 0.96933 | 0.89535 | 0.79615 | 0.68582 | 0.56586 | 0.44003 | 0.32351 | 0.20149 | 0.078999 | -0.052981 | -0.19342 | -0.34123 | -0.48703 | -0.61863 | -0.72777 | -0.8087 | -0.84714 | -0.83633 | -0.79948 | -0.75398 | -0.70933 | -0.65832 | -0.58711 | -0.49106 | -0.37164 | -0.22702 | -0.061999 | 0.11707 | 0.3104 | -0.0016069 | -0.0031882 | -0.00015941 | -0.00015941 | 0 | 0 | 0.0022174 | 0.05 | -0.27315 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.72701 | 0.68134 | 0.64258 | 0.62371 | 0.6207 | 0.62211 | 0.63138 | 0.64359 | 0.65707 | 0.66529 | 0.68565 | 0.72367 | 0.78025 | 0.84841 | 0.92725 | 0.98507 | 0.89588 | 0.81454 | 0.75354 | 0.71247 | 0.6837 | 0.66522 | 0.65838 | 0.66186 | 0.6718 | 0.68893 | 0.71214 | 0.74868 | 0.79975 | 0.85719 | 0.91487 | 0.98507 | 15 | Slope | 0.53333 | 0.57567 | 0.56045 | 0.53641 | 0.51902 | 0.5069 | 0.49626 | 0.48824 | 0.4812 | 0.47458 | 0.46621 | 0.46188 | 0.46345 | 0.47119 | 0.4828 | 0.49797 | 0.50613 | 0.46529 | 0.42707 | 0.39562 | 0.37082 | 0.35012 | 0.33285 | 0.31946 | 0.30951 | 0.30171 | 0.29631 | 0.29293 | 0.294 | 0.29992 | 0.30795 | 0.31607 | 0.57567 | 0 | 0.72701 | Slope | 1 | 0.032139 |  | 0.84091 | 0 | 0.72701 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00022952 | 0.00014279 | 0.0022174
118 | 0:20 | -3.2139 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -1.2034 | -0.012034 | -0.012034 | -3.2139 | 0.0010053 | [13 empty] | 0.96933 | 1 | 0.9719 | 0.90475 | 0.81354 | 0.70827 | 0.59106 | 0.47547 | 0.35306 | 0.22994 | 0.10066 | -0.036833 | -0.18729 | -0.34418 | -0.49247 | -0.62492 | -0.74037 | -0.82048 | -0.84865 | -0.83947 | -0.80913 | -0.77128 | -0.73373 | -0.68755 | -0.62357 | -0.53393 | -0.41554 | -0.26933 | -0.097882 | 0.10359 | 0.31345 | -0.00060168 | -0.0035758 | -0.00017879 | -0.00017879 | 0 | 0 | 0.0022225 | 0.05 | -0.31882 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.68136 | 0.6426 | 0.62373 | 0.62072 | 0.62213 | 0.6314 | 0.64361 | 0.65708 | 0.66531 | 0.68567 | 0.72369 | 0.78027 | 0.84843 | 0.92727 | 0.98505 | 0.89586 | 0.81452 | 0.75352 | 0.71245 | 0.68368 | 0.6652 | 0.65836 | 0.66184 | 0.67179 | 0.68891 | 0.71212 | 0.74866 | 0.79973 | 0.85717 | 0.91485 | 0.97181 | 0.98505 | 14 | Slope | 0.56667 | 0.56045 | 0.54753 | 0.53013 | 0.51802 | 0.50738 | 0.49936 | 0.49231 | 0.48569 | 0.47733 | 0.473 | 0.47456 | 0.48231 | 0.49392 | 0.50909 | 0.51724 | 0.4764 | 0.43817 | 0.40673 | 0.38193 | 0.36123 | 0.34396 | 0.33056 | 0.32061 | 0.31282 | 0.30741 | 0.30404 | 0.30511 | 0.31102 | 0.31906 | 0.32717 | 0.33505 | 0.56045 | 0 | 0.68136 | Slope | 1 | 0.012034 |  | 0.94043 | 0 | 0.68136 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0010053 | 0.00013999 | 0.0022225
119 | 0:20 | -1.2034 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 0.50344 | 0.0050344 | 0.0050344 | -1.2034 | 0.0008534 | [13 empty] | 0.9719 | 1 | 0.97413 | 0.91116 | 0.82346 | 0.72004 | 0.60896 | 0.48927 | 0.36645 | 0.23808 | 0.10299 | -0.043769 | -0.20264 | -0.3621 | -0.51147 | -0.65153 | -0.76693 | -0.8291 | -0.8484 | -0.8406 | -0.81479 | -0.7818 | -0.7477 | -0.70684 | -0.64803 | -0.56068 | -0.44242 | -0.29152 | -0.099195 | 0.11835 | 0.3246 | 0.00025172 | -0.0037645 | -0.00018822 | -0.00018822 | 0 | 0 | 0.0022301 | 0.05 | -0.35758 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.6426 | 0.62374 | 0.62073 | 0.62214 | 0.63141 | 0.64362 | 0.65709 | 0.66532 | 0.68568 | 0.7237 | 0.78028 | 0.84844 | 0.92728 | 0.98504 | 0.89585 | 0.81451 | 0.75351 | 0.71245 | 0.68367 | 0.66519 | 0.65835 | 0.66183 | 0.67178 | 0.6889 | 0.71211 | 0.74865 | 0.79972 | 0.85716 | 0.91484 | 0.9718 | 0.96996 | 0.98504 | 13 | Slope | 0.6 | 0.54753 | 0.54125 | 0.52913 | 0.51849 | 0.51047 | 0.50343 | 0.49681 | 0.48844 | 0.48411 | 0.48568 | 0.49343 | 0.50504 | 0.5202 | 0.52835 | 0.48751 | 0.44928 | 0.41784 | 0.39304 | 0.37234 | 0.35506 | 0.34167 | 0.33172 | 0.32393 | 0.31852 | 0.31515 | 0.31622 | 0.32213 | 0.33017 | 0.33828 | 0.34616 | 0.33443 | 0.54753 | 0 | 0.6426 | Slope | 1 | 0.0050344 |  | 0.97508 | 0 | 0.6426 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0008534 | 0.0001364 | 0.0022301
120 | 0:20 | 0.50344 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.3975 | 0.013975 | 0.013975 | 0.50344 | 0.00044701 | [13 empty] | 0.97413 | 1 | 0.97489 | 0.91363 | 0.82664 | 0.72574 | 0.61177 | 0.4915 | 0.36365 | 0.22811 | 0.083278 | -0.072517 | -0.23525 | -0.39653 | -0.55413 | -0.69409 | -0.78572 | -0.83067 | -0.84669 | -0.84012 | -0.81675 | -0.78566 | -0.75469 | -0.7173 | -0.66079 | -0.57399 | -0.4523 | -0.28159 | -0.072042 | 0.14365 | 0.33109 | 0.00069873 | -0.0037946 | -0.00018973 | -0.00018973 | 0 | 0 | 0.0022321 | 0.05 | -0.37645 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.62374 | 0.62073 | 0.62214 | 0.63141 | 0.64362 | 0.6571 | 0.66532 | 0.68568 | 0.7237 | 0.78028 | 0.84844 | 0.92728 | 0.98504 | 0.89585 | 0.81451 | 0.75351 | 0.71244 | 0.68367 | 0.66519 | 0.65835 | 0.66183 | 0.67177 | 0.6889 | 0.7121 | 0.74865 | 0.79972 | 0.85716 | 0.91484 | 0.9718 | 0.96997 | 0.90765 | 0.98504 | 12 | Slope | 0.63333 | 0.54125 | 0.54024 | 0.5296 | 0.52158 | 0.51454 | 0.50792 | 0.49955 | 0.49523 | 0.49679 | 0.50454 | 0.51615 | 0.53132 | 0.53946 | 0.49862 | 0.46039 | 0.42895 | 0.40415 | 0.38345 | 0.36617 | 0.35278 | 0.34283 | 0.33504 | 0.32963 | 0.32626 | 0.32733 | 0.33324 | 0.34128 | 0.34939 | 0.35727 | 0.34554 | 0.31366 | 0.54125 | 0 | 0.62374 | Slope | 1 | 0.013975 |  | 0.93083 | 0 | 0.62374 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00044701 | 0.00013266 | 0.0022321
121 | 0:20 | 1.3975 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.119 | 0.02119 | 0.02119 | 1.3975 | 0.00036077 | [13 empty] | 0.97489 | 1 | 0.97521 | 0.91414 | 0.8288 | 0.72565 | 0.60998 | 0.4828 | 0.34531 | 0.19757 | 0.040372 | -0.12245 | -0.28758 | -0.45492 | -0.60946 | -0.72292 | -0.79373 | -0.83221 | -0.84646 | -0.84 | -0.81714 | -0.7875 | -0.75869 | -0.72194 | -0.66504 | -0.57601 | -0.43375 | -0.24089 | -0.025526 | 0.17602 | 0.33624 | 0.0010595 | -0.0037805 | -0.00018902 | -0.00018902 | 0 | 0 | 0.0022306 | 0.05 | -0.37946 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.62073 | 0.62214 | 0.63141 | 0.64362 | 0.6571 | 0.66532 | 0.68568 | 0.7237 | 0.78028 | 0.84844 | 0.92728 | 0.98504 | 0.89585 | 0.81451 | 0.75351 | 0.71244 | 0.68367 | 0.66519 | 0.65835 | 0.66183 | 0.67177 | 0.6889 | 0.71211 | 0.74865 | 0.79972 | 0.85716 | 0.91484 | 0.9718 | 0.96997 | 0.90765 | 0.84543 | 0.98504 | 11 | Slope | 0.66667 | 0.54024 | 0.54071 | 0.53269 | 0.52565 | 0.51903 | 0.51066 | 0.50634 | 0.5079 | 0.51565 | 0.52726 | 0.54243 | 0.55057 | 0.50973 | 0.4715 | 0.44006 | 0.41526 | 0.39456 | 0.37729 | 0.36389 | 0.35394 | 0.34615 | 0.34074 | 0.33737 | 0.33844 | 0.34435 | 0.35239 | 0.3605 | 0.36838 | 0.35666 | 0.32477 | 0.29292 | 0.55057 | 11 | 0.98504 | Slope | 0.66667 | 0.02119 |  | 0.89511 | 0 | 0.98504 | Slope | 2 | 0.66667 | 0 | 20 | -20 | 0.00036077 | 0.0001294 | 0.0022306
122 | 0:20 | 2.119 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.3922 | 0.023922 | 0.023922 | 2.119 | 0.0001366 | [13 empty] | 0.97521 | 1 | 0.97506 | 0.91399 | 0.82669 | 0.72201 | 0.59982 | 0.46263 | 0.31215 | 0.15059 | -0.015335 | -0.18136 | -0.3524 | -0.51703 | -0.64436 | -0.7343 | -0.79658 | -0.83166 | -0.84485 | -0.83825 | -0.81582 | -0.78729 | -0.75887 | -0.7221 | -0.66473 | -0.55676 | -0.39049 | -0.18672 | 0.01849 | 0.19305 | 0.33261 | 0.0011961 | -0.0036878 | -0.00018439 | -0.00018439 | 0 | 0 | 0.0022194 | 0.05 | -0.37805 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.62213 | 0.6314 | 0.64361 | 0.65709 | 0.66532 | 0.68567 | 0.7237 | 0.78027 | 0.84844 | 0.92728 | 0.98504 | 0.89585 | 0.81451 | 0.75351 | 0.71245 | 0.68368 | 0.6652 | 0.65835 | 0.66183 | 0.67178 | 0.6889 | 0.71211 | 0.74865 | 0.79973 | 0.85717 | 0.91484 | 0.97181 | 0.96996 | 0.90764 | 0.84542 | 0.78621 | 0.98504 | 10 | Slope | 0.7 | 0.54071 | 0.5438 | 0.53676 | 0.53014 | 0.52177 | 0.51745 | 0.51901 | 0.52676 | 0.53837 | 0.55354 | 0.56168 | 0.52084 | 0.48262 | 0.45117 | 0.42637 | 0.40567 | 0.3884 | 0.37501 | 0.36506 | 0.35726 | 0.35186 | 0.34848 | 0.34955 | 0.35546 | 0.3635 | 0.37161 | 0.37949 | 0.36776 | 0.33588 | 0.30403 | 0.27318 | 0.56168 | 10 | 0.98504 | Slope | 0.7 | 0.023922 |  | 0.88159 | 0 | 0.98504 | Slope | 2 | 0.7 | 0 | 20 | -20 | 0.0001366 | 0.00012711 | 0.0022194
123 | 0:20 | 2.3922 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.1593 | 0.031593 | 0.031593 | 2.3922 | 0.00038353 | [13 empty] | 0.97506 | 1 | 0.97492 | 0.91225 | 0.82376 | 0.71286 | 0.58076 | 0.42971 | 0.26334 | 0.090942 | -0.078609 | -0.24912 | -0.41672 | -0.55511 | -0.65854 | -0.73883 | -0.79652 | -0.8297 | -0.84242 | -0.8359 | -0.81424 | -0.78557 | -0.75697 | -0.72105 | -0.64609 | -0.51208 | -0.32876 | -0.12966 | 0.051207 | 0.2024 | 0.33233 | 0.0015796 | -0.0035657 | -0.00017828 | -0.00017828 | 0 | 0 | 0.0022033 | 0.05 | -0.36878 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.6314 | 0.64361 | 0.65708 | 0.66531 | 0.68567 | 0.72369 | 0.78027 | 0.84843 | 0.92727 | 0.98505 | 0.89586 | 0.81452 | 0.75352 | 0.71246 | 0.68368 | 0.6652 | 0.65836 | 0.66184 | 0.67179 | 0.68891 | 0.71212 | 0.74866 | 0.79973 | 0.85717 | 0.91485 | 0.97181 | 0.96995 | 0.90764 | 0.84542 | 0.7862 | 0.72438 | 0.98505 | 9 | Slope | 0.73333 | 0.5438 | 0.54787 | 0.54125 | 0.53288 | 0.52856 | 0.53012 | 0.53787 | 0.54948 | 0.56465 | 0.57279 | 0.53195 | 0.49373 | 0.46228 | 0.43749 | 0.41678 | 0.39951 | 0.38612 | 0.37617 | 0.36837 | 0.36297 | 0.35959 | 0.36066 | 0.36658 | 0.37461 | 0.38273 | 0.3906 | 0.37887 | 0.34699 | 0.31514 | 0.28429 | 0.25257 | 0.57279 | 9 | 0.98505 | Slope | 0.73333 | 0.031593 |  | 0.84362 | 0 | 0.98505 | Slope | 2 | 0.73333 | 0 | 20 | -20 | 0.00038353 | 0.00012629 | 0.0022033
124 | 0:21 | 3.1593 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.2116 | 0.022116 | 0.022116 | 3.1593 | 0.00047383 | [13 empty] | 0.97492 | 1 | 0.97494 | 0.90896 | 0.81074 | 0.68597 | 0.53608 | 0.36389 | 0.18193 | 0.0046701 | -0.16677 | -0.32892 | -0.46752 | -0.57983 | -0.67064 | -0.74275 | -0.79555 | -0.8266 | -0.83752 | -0.83022 | -0.80456 | -0.77062 | -0.74027 | -0.68639 | -0.58387 | -0.42748 | -0.24302 | -0.065968 | 0.088005 | 0.22716 | 0.34412 | 0.0011058 | -0.0034309 | -0.00017155 | -0.00017155 | 0 | 0 | 0.0021785 | 0.05 | -0.35657 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.6436 | 0.65708 | 0.66531 | 0.68566 | 0.72368 | 0.78026 | 0.84843 | 0.92726 | 0.98506 | 0.89587 | 0.81453 | 0.75353 | 0.71246 | 0.68369 | 0.66521 | 0.65837 | 0.66185 | 0.67179 | 0.68892 | 0.71212 | 0.74867 | 0.79974 | 0.85718 | 0.91485 | 0.97182 | 0.96995 | 0.90763 | 0.84541 | 0.7862 | 0.72437 | 0.66483 | 0.98506 | 8 | Slope | 0.76667 | 0.54787 | 0.55236 | 0.54399 | 0.53966 | 0.54123 | 0.54898 | 0.56059 | 0.57575 | 0.58391 | 0.54307 | 0.50484 | 0.4734 | 0.4486 | 0.4279 | 0.41063 | 0.39723 | 0.38728 | 0.37949 | 0.37408 | 0.37071 | 0.37178 | 0.37769 | 0.38573 | 0.39384 | 0.40172 | 0.38998 | 0.3581 | 0.32625 | 0.2954 | 0.26368 | 0.23272 | 0.58391 | 8 | 0.98506 | Slope | 0.76667 | 0.022116 |  | 0.89053 | 0 | 0.98506 | Slope | 2 | 0.76667 | 0 | 20 | -20 | 0.00047383 | 0.00012723 | 0.0021785
125 | 0:21 | 2.2116 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.8306 | 0.028306 | 0.028306 | 2.2116 | 0.00030952 | [13 empty] | 0.97494 | 1 | 0.97386 | 0.90086 | 0.79259 | 0.65158 | 0.48006 | 0.2917 | 0.10606 | -0.070112 | -0.233 | -0.37146 | -0.48847 | -0.58955 | -0.67297 | -0.74093 | -0.79233 | -0.82292 | -0.83473 | -0.82579 | -0.79766 | -0.76373 | -0.71486 | -0.63102 | -0.50057 | -0.3375 | -0.16931 | -0.018611 | 0.12103 | 0.24568 | 0.35471 | 0.0014153 | -0.0033487 | -0.00016743 | -0.00016743 | 0 | 0 | 0.002165 | 0.05 | -0.34309 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.65707 | 0.6653 | 0.68566 | 0.72368 | 0.78026 | 0.84842 | 0.92726 | 0.98506 | 0.89587 | 0.81453 | 0.75353 | 0.71247 | 0.68369 | 0.66521 | 0.65837 | 0.66185 | 0.6718 | 0.68892 | 0.71213 | 0.74867 | 0.79974 | 0.85718 | 0.91486 | 0.97182 | 0.96994 | 0.90763 | 0.84541 | 0.78619 | 0.72437 | 0.66483 | 0.60752 | 0.98506 | 7 | Slope | 0.8 | 0.55236 | 0.5551 | 0.55077 | 0.55234 | 0.56009 | 0.5717 | 0.58686 | 0.59502 | 0.55418 | 0.51595 | 0.48451 | 0.45971 | 0.43901 | 0.42174 | 0.40835 | 0.39839 | 0.3906 | 0.3852 | 0.38182 | 0.38289 | 0.3888 | 0.39684 | 0.40495 | 0.41283 | 0.40109 | 0.36921 | 0.33736 | 0.30651 | 0.27479 | 0.24383 | 0.21362 | 0.59502 | 7 | 0.98506 | Slope | 0.8 | 0.028306 |  | 0.85988 | 0 | 0.98506 | Slope | 2 | 0.8 | 0 | 20 | -20 | 0.00030952 | 0.0001299 | 0.002165
126 | 0:21 | 2.8306 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.6135 | 0.036135 | 0.036135 | 2.8306 | 0.00039143 | [13 empty] | 0.97386 | 1 | 0.97044 | 0.88975 | 0.76705 | 0.6052 | 0.41684 | 0.22321 | 0.03605 | -0.13562 | -0.2756 | -0.39042 | -0.49557 | -0.58914 | -0.66841 | -0.73519 | -0.78586 | -0.81707 | -0.82912 | -0.81971 | -0.79203 | -0.74211 | -0.66791 | -0.5603 | -0.42325 | -0.2756 | -0.13324 | 0.0046313 | 0.13003 | 0.24718 | 0.36133 | 0.0018068 | -0.0031451 | -0.00015726 | -0.00015726 | 0 | 0 | 0.0021335 | 0.05 | -0.33487 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.66529 | 0.68565 | 0.72367 | 0.78025 | 0.84841 | 0.92725 | 0.98507 | 0.89588 | 0.81454 | 0.75354 | 0.71248 | 0.6837 | 0.66522 | 0.65838 | 0.66186 | 0.67181 | 0.68893 | 0.71214 | 0.74868 | 0.79975 | 0.85719 | 0.91487 | 0.97183 | 0.96993 | 0.90762 | 0.84539 | 0.78618 | 0.72436 | 0.66482 | 0.60751 | 0.55653 | 0.98507 | 6 | Slope | 0.83333 | 0.5551 | 0.56188 | 0.56345 | 0.57119 | 0.5828 | 0.59797 | 0.60613 | 0.56529 | 0.52707 | 0.49562 | 0.47083 | 0.45012 | 0.43285 | 0.41946 | 0.40951 | 0.40171 | 0.39631 | 0.39293 | 0.394 | 0.39992 | 0.40795 | 0.41607 | 0.42394 | 0.4122 | 0.38032 | 0.34846 | 0.31762 | 0.2859 | 0.25494 | 0.22472 | 0.19662 | 0.60613 | 6 | 0.98507 | Slope | 0.83333 | 0.036135 |  | 0.82113 | 0 | 0.98507 | Slope | 2 | 0.83333 | 0 | 20 | -20 | 0.00039143 | 0.00013385 | 0.0021335
127 | 0:21 | 3.6135 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 4.8286 | 0.048286 | 0.048286 | 3.6135 | 0.00060753 | [13 empty] | 0.97044 | 1 | 0.96816 | 0.87789 | 0.73839 | 0.56123 | 0.36627 | 0.16681 | -0.023068 | -0.17298 | -0.28583 | -0.38816 | -0.48631 | -0.57644 | -0.65515 | -0.72109 | -0.77229 | -0.8073 | -0.82289 | -0.81626 | -0.77825 | -0.71051 | -0.62087 | -0.51009 | -0.38961 | -0.26636 | -0.13434 | -0.0099103 | 0.1096 | 0.23696 | 0.36021 | 0.0024143 | -0.0027649 | -0.00013824 | -0.00013824 | 0 | 0 | 0.0020852 | 0.05 | -0.31451 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.68563 | 0.72365 | 0.78023 | 0.84839 | 0.92723 | 0.98509 | 0.8959 | 0.81456 | 0.75356 | 0.7125 | 0.68372 | 0.66524 | 0.6584 | 0.66188 | 0.67183 | 0.68895 | 0.71216 | 0.7487 | 0.79977 | 0.85721 | 0.91489 | 0.97185 | 0.96991 | 0.9076 | 0.84538 | 0.78616 | 0.72434 | 0.6648 | 0.60749 | 0.55652 | 0.51725 | 0.98509 | 5 | Slope | 0.86667 | 0.56188 | 0.57455 | 0.5823 | 0.59391 | 0.60908 | 0.61725 | 0.57641 | 0.53819 | 0.50674 | 0.48194 | 0.46124 | 0.44397 | 0.43058 | 0.42063 | 0.41283 | 0.40743 | 0.40405 | 0.40512 | 0.41104 | 0.41907 | 0.42718 | 0.43506 | 0.4233 | 0.39142 | 0.35957 | 0.32872 | 0.297 | 0.26604 | 0.23583 | 0.20773 | 0.18353 | 0.61725 | 5 | 0.98509 | Slope | 0.86667 | 0.048286 |  | 0.76099 | 0 | 0.98509 | Slope | 2 | 0.86667 | 0 | 20 | -20 | 0.00060753 | 0.00013867 | 0.0020852
128 | 0:21 | 4.8286 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 5.1764 | 0.051764 | 0.051764 | 4.8286 | 0.00017392 | [13 empty] | 0.96816 | 1 | 0.96406 | 0.8612 | 0.70755 | 0.52218 | 0.31745 | 0.10928 | -0.058415 | -0.17592 | -0.27417 | -0.36849 | -0.46261 | -0.55218 | -0.62894 | -0.69427 | -0.75108 | -0.79136 | -0.81099 | -0.80161 | -0.75507 | -0.68121 | -0.59293 | -0.50178 | -0.40532 | -0.28939 | -0.1705 | -0.050711 | 0.083906 | 0.22506 | 0.35067 | 0.0025882 | -0.0021991 | -0.00010996 | -0.00010996 | 0 | 0 | 0.0020166 | 0.05 | -0.27649 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.72362 | 0.7802 | 0.84836 | 0.9272 | 0.98512 | 0.89593 | 0.81459 | 0.75359 | 0.71252 | 0.68375 | 0.66527 | 0.65843 | 0.66191 | 0.67185 | 0.68898 | 0.71218 | 0.74873 | 0.7998 | 0.85724 | 0.91492 | 0.97188 | 0.96989 | 0.90757 | 0.84535 | 0.78613 | 0.72431 | 0.66477 | 0.60746 | 0.55649 | 0.51722 | 0.49667 | 0.98512 | 4 | Slope | 0.9 | 0.57454 | 0.5934 | 0.60501 | 0.62018 | 0.62837 | 0.58753 | 0.54931 | 0.51786 | 0.49306 | 0.47236 | 0.45509 | 0.4417 | 0.43175 | 0.42395 | 0.41855 | 0.41517 | 0.41624 | 0.42216 | 0.43019 | 0.43831 | 0.44618 | 0.43441 | 0.40252 | 0.37067 | 0.33982 | 0.3081 | 0.27715 | 0.24693 | 0.21883 | 0.19463 | 0.17667 | 0.62837 | 4 | 0.98512 | Slope | 0.9 | 0.051764 |  | 0.74377 | 0 | 0.98512 | Slope | 2 | 0.9 | 0 | 20 | -20 | 0.00017392 | 0.00014386 | 0.0020166
129 | 0:21 | 5.1764 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 5.245 | 0.05245 | 0.05245 | 5.1764 | 3.428e-05 | [13 empty] | 0.96406 | 1 | 0.95908 | 0.84626 | 0.68586 | 0.4905 | 0.27271 | 0.084023 | -0.04923 | -0.15119 | -0.24105 | -0.33089 | -0.42418 | -0.51106 | -0.58634 | -0.6595 | -0.72466 | -0.77151 | -0.7964 | -0.78774 | -0.7424 | -0.67335 | -0.60621 | -0.53814 | -0.44727 | -0.34443 | -0.23023 | -0.093717 | 0.056889 | 0.20246 | 0.32394 | 0.0026225 | -0.0015175 | -7.5873e-05 | -7.5873e-05 | 0 | 0 | 0.0019529 | 0.05 | -0.21991 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.78016 | 0.84833 | 0.92717 | 0.98515 | 0.89596 | 0.81462 | 0.75362 | 0.71256 | 0.68379 | 0.6653 | 0.65846 | 0.66194 | 0.67189 | 0.68901 | 0.71222 | 0.74876 | 0.79984 | 0.85727 | 0.91495 | 0.97191 | 0.96985 | 0.90754 | 0.84531 | 0.7861 | 0.72427 | 0.66474 | 0.60743 | 0.55645 | 0.51719 | 0.49664 | 0.49822 | 0.98515 | 3 | Slope | 0.93333 | 0.59339 | 0.61611 | 0.63128 | 0.63949 | 0.59865 | 0.56043 | 0.52899 | 0.50419 | 0.48348 | 0.46621 | 0.45282 | 0.44287 | 0.43507 | 0.42967 | 0.4263 | 0.42737 | 0.43328 | 0.44131 | 0.44943 | 0.4573 | 0.44551 | 0.41362 | 0.38177 | 0.35092 | 0.3192 | 0.28825 | 0.25803 | 0.22993 | 0.20573 | 0.18777 | 0.17718 | 0.63949 | 3 | 0.98515 | Slope | 0.93333 | 0.05245 |  | 0.74037 | 0 | 0.98515 | Slope | 2 | 0.93333 | 0 | 20 | -20 | 3.428e-05 | 0.00014881 | 0.0019529
130 | 0:22 | 5.245 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 5.4065 | 0.054065 | 0.054065 | 5.245 | 8.0748e-05 | [13 empty] | 0.95908 | 1 | 0.95625 | 0.84029 | 0.67187 | 0.46073 | 0.25967 | 0.10725 | -0.0094793 | -0.10292 | -0.18787 | -0.27585 | -0.36494 | -0.44894 | -0.53414 | -0.61857 | -0.69257 | -0.75308 | -0.78914 | -0.79009 | -0.7531 | -0.70653 | -0.66131 | -0.59737 | -0.51932 | -0.42154 | -0.29027 | -0.13695 | 0.019184 | 0.16159 | 0.29278 | 0.0027032 | -0.00072909 | -3.6454e-05 | -3.6454e-05 | 0 | 0 | 0.0019164 | 0.05 | -0.15175 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.84829 | 0.92713 | 0.98519 | 0.896 | 0.81466 | 0.75366 | 0.7126 | 0.68383 | 0.66534 | 0.6585 | 0.66198 | 0.67193 | 0.68905 | 0.71226 | 0.7488 | 0.79987 | 0.85731 | 0.91499 | 0.97195 | 0.96981 | 0.9075 | 0.84527 | 0.78606 | 0.72424 | 0.6647 | 0.60739 | 0.55641 | 0.51715 | 0.4966 | 0.49818 | 0.52554 | 0.98519 | 2 | Slope | 0.96667 | 0.6161 | 0.64238 | 0.65062 | 0.60978 | 0.57155 | 0.54011 | 0.51531 | 0.49461 | 0.47734 | 0.46394 | 0.45399 | 0.4462 | 0.44079 | 0.43742 | 0.43849 | 0.4444 | 0.45244 | 0.46055 | 0.46843 | 0.4566 | 0.42472 | 0.39287 | 0.36202 | 0.3303 | 0.29934 | 0.26913 | 0.24103 | 0.21683 | 0.19887 | 0.18828 | 0.18629 | 0.65062 | 2 | 0.98519 | Slope | 0.96667 | 0.054065 |  | 0.73238 | 0 | 0.98519 | Slope | 2 | 0.96667 | 0 | 20 | -20 | 8.0748e-05 | 0.00015298 | 0.0019164
131 | 0:22 | 5.4065 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 5.5518 | 0.055518 | 0.055518 | 5.4065 | 7.268e-05 | [13 empty] | 0.95625 | 1 | 0.95579 | 0.83413 | 0.64933 | 0.45295 | 0.28981 | 0.15565 | 0.048427 | -0.03919 | -0.12098 | -0.20263 | -0.28654 | -0.3807 | -0.47752 | -0.57061 | -0.66541 | -0.74674 | -0.79997 | -0.81093 | -0.79583 | -0.76999 | -0.72755 | -0.67567 | -0.60257 | -0.48827 | -0.34093 | -0.18266 | -0.030598 | 0.12329 | 0.26154 | 0.0027759 | 0.00014773 | 7.3865e-06 | 7.3865e-06 | 0 | 0 | 0.0019071 | 0.05 | -0.072909 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.92708 | 0.98523 | 0.89604 | 0.81471 | 0.75371 | 0.71264 | 0.68387 | 0.66539 | 0.65855 | 0.66203 | 0.67197 | 0.68909 | 0.7123 | 0.74885 | 0.79992 | 0.85736 | 0.91503 | 0.972 | 0.96977 | 0.90745 | 0.84523 | 0.78602 | 0.72419 | 0.66465 | 0.60734 | 0.55637 | 0.51711 | 0.49655 | 0.49813 | 0.52549 | 0.57284 | 0.98523 | 1 | Slope | 1 | 0.64236 | 0.66174 | 0.6209 | 0.58268 | 0.55124 | 0.52644 | 0.50573 | 0.48846 | 0.47507 | 0.46512 | 0.45732 | 0.45192 | 0.44855 | 0.44962 | 0.45553 | 0.46356 | 0.47168 | 0.47955 | 0.4677 | 0.43582 | 0.40397 | 0.37312 | 0.3414 | 0.31044 | 0.28023 | 0.25212 | 0.22792 | 0.20996 | 0.19938 | 0.19739 | 0.20206 | 0.66174 | 1 | 0.98523 | Slope | 1 | 0.055518 |  | 0.72518 | 0 | 0.98523 | Slope | 2 | 1 | 0 | 20 | -20 | 7.268e-05 | 0.00015607 | 0.0019071
132 | 0:22 | 5.5518 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 5.5349 | 0.055349 | 0.055349 | 5.5518 | 8.4558e-06 | [13 empty] | 0.95579 | 1 | 0.95274 | 0.81681 | 0.64344 | 0.48273 | 0.33836 | 0.21506 | 0.11493 | 0.031365 | -0.042564 | -0.11718 | -0.20874 | -0.31166 | -0.41513 | -0.53364 | -0.65663 | -0.75985 | -0.82193 | -0.85095 | -0.85447 | -0.83061 | -0.79973 | -0.75263 | -0.66539 | -0.53757 | -0.38728 | -0.235 | -0.072901 | 0.087587 | 0.21696 | 0.0027675 | 0.0010396 | 5.1982e-05 | 5.1982e-05 | 0 | 0 | 0.0018953 | 0.05 | 0.014773 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.98528 | 0.89609 | 0.81475 | 0.75375 | 0.71269 | 0.68391 | 0.66543 | 0.65859 | 0.66207 | 0.67202 | 0.68914 | 0.71235 | 0.74889 | 0.79996 | 0.8574 | 0.91508 | 0.97204 | 0.96972 | 0.90741 | 0.84519 | 0.78597 | 0.72415 | 0.66461 | 0.6073 | 0.55633 | 0.51706 | 0.49651 | 0.49809 | 0.52545 | 0.57279 | 0.63401 | 0.98528 | 0 | Slope | 1 | 0.66176 | 0.63203 | 0.59381 | 0.56236 | 0.53756 | 0.51686 | 0.49959 | 0.4862 | 0.47625 | 0.46845 | 0.46305 | 0.45967 | 0.46074 | 0.46665 | 0.47469 | 0.4828 | 0.49068 | 0.4788 | 0.44691 | 0.41506 | 0.38421 | 0.35249 | 0.32154 | 0.29132 | 0.26322 | 0.23902 | 0.22106 | 0.21047 | 0.20848 | 0.21315 | 0.22245 | 0.66176 | 0 | 0.98528 | Slope | 1 | 0.055349 |  | 0.72602 | 0 | 0.98528 | Slope | 2 | 1 | 0 | 20 | -20 | 8.4558e-06 | 0.00015776 | 0.0018953
133 | 0:22 | 5.5349 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 4.2841 | 0.042841 | 0.042841 | 5.5349 | 0.00062539 | [13 empty] | 0.95274 | 1 | 0.94645 | 0.81899 | 0.67512 | 0.53178 | 0.39915 | 0.284 | 0.18807 | 0.11321 | 0.047549 | -0.029333 | -0.12323 | -0.22967 | -0.36146 | -0.51422 | -0.66313 | -0.77413 | -0.85065 | -0.89664 | -0.90184 | -0.89016 | -0.86536 | -0.80979 | -0.71422 | -0.58717 | -0.44576 | -0.28777 | -0.12088 | 0.030269 | 0.15741 | 0.0021421 | 0.001853 | 9.2651e-05 | 9.2651e-05 | 0 | 0 | 0.001847 | 0.05 | 0.10396 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.89613 | 0.81479 | 0.75379 | 0.71273 | 0.68395 | 0.66547 | 0.65863 | 0.66211 | 0.67206 | 0.68918 | 0.71239 | 0.74893 | 0.8 | 0.85744 | 0.91512 | 0.97208 | 0.96968 | 0.90737 | 0.84515 | 0.78593 | 0.72411 | 0.66457 | 0.60726 | 0.55628 | 0.51702 | 0.49647 | 0.49805 | 0.52541 | 0.57275 | 0.63397 | 0.70888 | 0.97208 | 15 | Slope | 0.53333 | 0.63204 | 0.60493 | 0.57349 | 0.54869 | 0.52798 | 0.51071 | 0.49732 | 0.48737 | 0.47957 | 0.47417 | 0.4708 | 0.47187 | 0.47778 | 0.48581 | 0.49393 | 0.50181 | 0.48989 | 0.45801 | 0.42616 | 0.39531 | 0.36359 | 0.33263 | 0.30242 | 0.27432 | 0.25012 | 0.23216 | 0.22157 | 0.21958 | 0.22425 | 0.23354 | 0.24741 | 0.63204 | 0 | 0.89613 | Slope | 1 | 0.042841 |  | 0.78794 | 0 | 0.89613 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00062539 | 0.00015789 | 0.001847
134 | 0:22 | 4.2841 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.6484 | 0.016484 | 0.016484 | 4.2841 | 0.0013179 | [13 empty] | 0.94645 | 1 | 0.95223 | 0.84494 | 0.71644 | 0.5858 | 0.46246 | 0.35166 | 0.26417 | 0.1977 | 0.13576 | 0.064043 | -0.028833 | -0.1612 | -0.32596 | -0.50197 | -0.65411 | -0.772 | -0.86149 | -0.90917 | -0.92636 | -0.9233 | -0.90056 | -0.84632 | -0.75796 | -0.64385 | -0.50396 | -0.34544 | -0.18848 | -0.040603 | 0.099594 | 0.00082419 | 0.002463 | 0.00012315 | 0.00012315 | 0 | 0 | 0.0017899 | 0.05 | 0.1853 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.81482 | 0.75382 | 0.71276 | 0.68399 | 0.6655 | 0.65866 | 0.66214 | 0.67209 | 0.68921 | 0.71242 | 0.74896 | 0.80003 | 0.85747 | 0.91515 | 0.97211 | 0.96965 | 0.90734 | 0.84511 | 0.7859 | 0.72408 | 0.66454 | 0.60723 | 0.55625 | 0.51699 | 0.49644 | 0.49802 | 0.52538 | 0.57272 | 0.63393 | 0.70885 | 0.79291 | 0.97211 | 14 | Slope | 0.56667 | 0.60494 | 0.58461 | 0.55981 | 0.53911 | 0.52183 | 0.50844 | 0.49849 | 0.4907 | 0.48529 | 0.48192 | 0.48299 | 0.4889 | 0.49694 | 0.50505 | 0.51293 | 0.501 | 0.46911 | 0.43726 | 0.40641 | 0.37469 | 0.34373 | 0.31352 | 0.28542 | 0.26122 | 0.24326 | 0.23267 | 0.23068 | 0.23535 | 0.24464 | 0.25851 | 0.27541 | 0.60494 | 0 | 0.81482 | Slope | 1 | 0.016484 |  | 0.91841 | 0 | 0.81482 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0013179 | 0.00015651 | 0.0017899
135 | 0:22 | 1.6484 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -0.58784 | -0.0058784 | -0.0058784 | 1.6484 | 0.0011181 | [13 empty] | 0.95223 | 1 | 0.95913 | 0.86264 | 0.74499 | 0.62291 | 0.50421 | 0.40029 | 0.31917 | 0.2546 | 0.19579 | 0.12585 | 0.012213 | -0.14674 | -0.32708 | -0.49852 | -0.64332 | -0.76122 | -0.84772 | -0.90096 | -0.92486 | -0.92949 | -0.91233 | -0.86522 | -0.78733 | -0.67521 | -0.53541 | -0.38631 | -0.23236 | -0.072463 | 0.086911 | -0.00029392 | 0.0028737 | 0.00014368 | 0.00014368 | 0 | 0 | 0.0017811 | 0.05 | 0.2463 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.75384 | 0.71278 | 0.68401 | 0.66552 | 0.65868 | 0.66216 | 0.67211 | 0.68923 | 0.71244 | 0.74898 | 0.80005 | 0.85749 | 0.91517 | 0.97213 | 0.96963 | 0.90732 | 0.84509 | 0.78588 | 0.72406 | 0.66452 | 0.60721 | 0.55623 | 0.51697 | 0.49642 | 0.498 | 0.52536 | 0.5727 | 0.63391 | 0.70883 | 0.79289 | 0.87601 | 0.97213 | 13 | Slope | 0.6 | 0.58461 | 0.57093 | 0.55022 | 0.53295 | 0.51956 | 0.50961 | 0.50181 | 0.49641 | 0.49303 | 0.49411 | 0.50002 | 0.50805 | 0.51617 | 0.52404 | 0.5121 | 0.48022 | 0.44836 | 0.41752 | 0.3858 | 0.35484 | 0.32462 | 0.29652 | 0.27232 | 0.25436 | 0.24378 | 0.24179 | 0.24646 | 0.25575 | 0.26961 | 0.28652 | 0.30312 | 0.58461 | 0 | 0.75384 | Slope | 1 | 0.0058784 |  | 0.9709 | 0 | 0.75384 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0011181 | 0.00015394 | 0.0017811
136 | 0:23 | -0.58784 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -1.833 | -0.01833 | -0.01833 | -0.58784 | 0.00062258 | [13 empty] | 0.95913 | 1 | 0.96215 | 0.87143 | 0.75913 | 0.64049 | 0.5264 | 0.42636 | 0.34205 | 0.27367 | 0.2132 | 0.12472 | -0.012319 | -0.18411 | -0.35706 | -0.51158 | -0.64426 | -0.75365 | -0.83728 | -0.89193 | -0.92303 | -0.93177 | -0.91637 | -0.87247 | -0.79104 | -0.67498 | -0.54147 | -0.39278 | -0.22547 | -0.048922 | 0.11773 | -0.0009165 | 0.0031614 | 0.00015807 | 0.00015807 | 0 | 0 | 0.0018023 | 0.05 | 0.28737 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.71279 | 0.68402 | 0.66554 | 0.6587 | 0.66218 | 0.67212 | 0.68925 | 0.71245 | 0.749 | 0.80007 | 0.85751 | 0.91518 | 0.97215 | 0.96962 | 0.9073 | 0.84508 | 0.78587 | 0.72404 | 0.6645 | 0.60719 | 0.55622 | 0.51696 | 0.4964 | 0.49798 | 0.52534 | 0.57269 | 0.6339 | 0.70882 | 0.79288 | 0.876 | 0.95003 | 0.97215 | 12 | Slope | 0.63333 | 0.57093 | 0.56134 | 0.54407 | 0.53068 | 0.52073 | 0.51293 | 0.50753 | 0.50415 | 0.50522 | 0.51113 | 0.51917 | 0.52728 | 0.53516 | 0.52321 | 0.49132 | 0.45947 | 0.42862 | 0.3969 | 0.36595 | 0.33573 | 0.30763 | 0.28343 | 0.26547 | 0.25488 | 0.25289 | 0.25756 | 0.26686 | 0.28072 | 0.29763 | 0.31422 | 0.32779 | 0.57093 | 0 | 0.71279 | Slope | 1 | 0.01833 |  | 0.90927 | 0 | 0.71279 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00062258 | 0.00015062 | 0.0018023
137 | 0:23 | -1.833 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.9106 | -0.029106 | -0.029106 | -1.833 | 0.00053881 | [13 empty] | 0.96215 | 1 | 0.96386 | 0.87614 | 0.76601 | 0.65034 | 0.53853 | 0.43374 | 0.34274 | 0.27018 | 0.19276 | 0.083422 | -0.065884 | -0.23087 | -0.38413 | -0.52151 | -0.64357 | -0.7458 | -0.82747 | -0.88921 | -0.92455 | -0.93296 | -0.91709 | -0.86758 | -0.78028 | -0.66817 | -0.53363 | -0.37075 | -0.18669 | -0.005508 | 0.15423 | -0.0014553 | 0.0033462 | 0.00016731 | 0.00016731 | 0 | 0 | 0.0018226 | 0.05 | 0.31614 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.68403 | 0.66555 | 0.65871 | 0.66219 | 0.67213 | 0.68925 | 0.71246 | 0.74901 | 0.80008 | 0.85752 | 0.91519 | 0.97216 | 0.96961 | 0.90729 | 0.84507 | 0.78586 | 0.72403 | 0.66449 | 0.60718 | 0.55621 | 0.51695 | 0.49639 | 0.49797 | 0.52533 | 0.57268 | 0.63389 | 0.70881 | 0.79287 | 0.87599 | 0.95003 | 0.98093 | 0.98093 | 30 | Slope | 0.033333 | 0.56134 | 0.55518 | 0.54179 | 0.53184 | 0.52404 | 0.51864 | 0.51527 | 0.51634 | 0.52225 | 0.53028 | 0.5384 | 0.54627 | 0.53431 | 0.50243 | 0.47058 | 0.43973 | 0.40801 | 0.37705 | 0.34684 | 0.31874 | 0.29454 | 0.27658 | 0.26599 | 0.264 | 0.26867 | 0.27796 | 0.29182 | 0.30873 | 0.32533 | 0.3389 | 0.33809 | 0.56134 | 0 | 0.68403 | Slope | 1 | 0.029106 |  | 0.85592 | 0 | 0.68403 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00053881 | 0.00014702 | 0.0018226
138 | 0:23 | -2.9106 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -3.7925 | -0.037925 | -0.037925 | -2.9106 | 0.00044092 | [13 empty] | 0.96386 | 1 | 0.96465 | 0.87773 | 0.76886 | 0.65381 | 0.53681 | 0.42379 | 0.32591 | 0.23744 | 0.14312 | 0.024168 | -0.11909 | -0.26313 | -0.39704 | -0.52379 | -0.63653 | -0.73531 | -0.82509 | -0.89222 | -0.92661 | -0.93242 | -0.91058 | -0.85441 | -0.76887 | -0.65461 | -0.50568 | -0.32578 | -0.13817 | 0.035571 | 0.19074 | -0.0018962 | 0.0034146 | 0.00017073 | 0.00017073 | 0 | 0 | 0.0018313 | 0.05 | 0.33462 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.66555 | 0.65871 | 0.66219 | 0.67213 | 0.68926 | 0.71247 | 0.74901 | 0.80008 | 0.85752 | 0.9152 | 0.97216 | 0.96961 | 0.90729 | 0.84507 | 0.78585 | 0.72403 | 0.66449 | 0.60718 | 0.55621 | 0.51694 | 0.49639 | 0.49797 | 0.52533 | 0.57268 | 0.63389 | 0.7088 | 0.79286 | 0.87599 | 0.95002 | 0.98093 | 0.91088 | 0.98093 | 29 | Slope | 0.066667 | 0.55518 | 0.5529 | 0.54295 | 0.53516 | 0.52975 | 0.52638 | 0.52745 | 0.53336 | 0.5414 | 0.54951 | 0.55739 | 0.54542 | 0.51354 | 0.48169 | 0.45084 | 0.41912 | 0.38816 | 0.35795 | 0.32985 | 0.30565 | 0.28769 | 0.2771 | 0.27511 | 0.27978 | 0.28907 | 0.30293 | 0.31984 | 0.33644 | 0.35001 | 0.3492 | 0.31474 | 0.55739 | 10 | 0.97216 | Slope | 0.7 | 0.037925 |  | 0.81227 | 0 | 0.97216 | Slope | 2 | 0.7 | 0 | 20 | -20 | 0.00044092 | 0.00014363 | 0.0018313
139 | 0:23 | -3.7925 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.299 | -0.04299 | -0.04299 | -3.7925 | 0.00025326 | [13 empty] | 0.96465 | 1 | 0.9646 | 0.87763 | 0.76804 | 0.64775 | 0.52172 | 0.39943 | 0.28502 | 0.18246 | 0.082052 | -0.031447 | -0.15404 | -0.27788 | -0.40199 | -0.51826 | -0.62677 | -0.73464 | -0.83075 | -0.89655 | -0.92677 | -0.92668 | -0.89788 | -0.84181 | -0.75348 | -0.62505 | -0.45877 | -0.27528 | -0.094798 | 0.075408 | 0.22538 | -0.0021495 | 0.0033798 | 0.00016899 | 0.00016899 | 0 | 0 | 0.0018264 | 0.05 | 0.34146 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.65871 | 0.66219 | 0.67213 | 0.68926 | 0.71246 | 0.74901 | 0.80008 | 0.85752 | 0.9152 | 0.97216 | 0.96961 | 0.90729 | 0.84507 | 0.78586 | 0.72403 | 0.66449 | 0.60718 | 0.55621 | 0.51695 | 0.49639 | 0.49797 | 0.52533 | 0.57268 | 0.63389 | 0.70881 | 0.79287 | 0.87599 | 0.95002 | 0.98093 | 0.91087 | 0.84328 | 0.98093 | 28 | Slope | 0.1 | 0.5529 | 0.55406 | 0.54627 | 0.54086 | 0.53749 | 0.53856 | 0.54447 | 0.55251 | 0.56062 | 0.5685 | 0.55654 | 0.52465 | 0.4928 | 0.46195 | 0.43023 | 0.39928 | 0.36906 | 0.34096 | 0.31676 | 0.2988 | 0.28821 | 0.28622 | 0.29089 | 0.30019 | 0.31405 | 0.33096 | 0.34755 | 0.36112 | 0.36031 | 0.32585 | 0.2922 | 0.5685 | 9 | 0.97216 | Slope | 0.73333 | 0.04299 |  | 0.7872 | 0 | 0.97216 | Slope | 2 | 0.73333 | 0 | 20 | -20 | 0.00025326 | 0.00014098 | 0.0018264
140 | 0:23 | -4.299 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.971 | -0.04971 | -0.04971 | -4.299 | 0.00033601 | [13 empty] | 0.9646 | 1 | 0.96453 | 0.87666 | 0.76245 | 0.63343 | 0.49718 | 0.35614 | 0.22706 | 0.12018 | 0.024983 | -0.069415 | -0.1725 | -0.28739 | -0.40038 | -0.51169 | -0.62885 | -0.74292 | -0.8371 | -0.89761 | -0.92198 | -0.91484 | -0.88536 | -0.82673 | -0.72491 | -0.57851 | -0.4074 | -0.23039 | -0.052684 | 0.11268 | 0.25575 | -0.0024855 | 0.0032804 | 0.00016402 | 0.00016402 | 0 | 0 | 0.0018116 | 0.05 | 0.33798 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.66218 | 0.67213 | 0.68925 | 0.71246 | 0.749 | 0.80008 | 0.85751 | 0.91519 | 0.97215 | 0.96961 | 0.9073 | 0.84507 | 0.78586 | 0.72403 | 0.6645 | 0.60719 | 0.55621 | 0.51695 | 0.4964 | 0.49798 | 0.52534 | 0.57268 | 0.63389 | 0.70881 | 0.79287 | 0.87599 | 0.95003 | 0.98092 | 0.91087 | 0.84328 | 0.7804 | 0.98092 | 27 | Slope | 0.13333 | 0.55406 | 0.55738 | 0.55197 | 0.5486 | 0.54967 | 0.55558 | 0.56362 | 0.57173 | 0.57961 | 0.56765 | 0.53577 | 0.50391 | 0.47306 | 0.44134 | 0.41039 | 0.38017 | 0.35207 | 0.32787 | 0.30991 | 0.29933 | 0.29733 | 0.30201 | 0.3113 | 0.32516 | 0.34207 | 0.35866 | 0.37223 | 0.37142 | 0.33696 | 0.30331 | 0.27125 | 0.57961 | 8 | 0.97215 | Slope | 0.76667 | 0.04971 |  | 0.75394 | 0 | 0.97215 | Slope | 2 | 0.76667 | 0 | 20 | -20 | 0.00033601 | 0.00013954 | 0.0018116
141 | 0:23 | -4.971 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.5317 | -0.055317 | -0.055317 | -4.971 | 0.00028036 | [13 empty] | 0.96453 | 1 | 0.96382 | 0.87153 | 0.7481 | 0.60766 | 0.45032 | 0.29278 | 0.16061 | 0.06041 | -0.014815 | -0.090444 | -0.18651 | -0.29005 | -0.39788 | -0.51796 | -0.64137 | -0.75261 | -0.83974 | -0.89381 | -0.91052 | -0.90093 | -0.86809 | -0.79668 | -0.67736 | -0.52608 | -0.36079 | -0.18518 | -0.011513 | 0.14716 | 0.28373 | -0.0027659 | 0.0031091 | 0.00015546 | 0.00015546 | 0 | 0 | 0.0017828 | 0.05 | 0.32804 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.67212 | 0.68924 | 0.71245 | 0.74899 | 0.80007 | 0.85751 | 0.91518 | 0.97215 | 0.96962 | 0.9073 | 0.84508 | 0.78587 | 0.72404 | 0.66451 | 0.60719 | 0.55622 | 0.51696 | 0.49641 | 0.49798 | 0.52535 | 0.57269 | 0.6339 | 0.70882 | 0.79288 | 0.876 | 0.95004 | 0.98091 | 0.91086 | 0.84327 | 0.7804 | 0.72221 | 0.98091 | 26 | Slope | 0.16667 | 0.55737 | 0.56308 | 0.55971 | 0.56078 | 0.56669 | 0.57472 | 0.58284 | 0.59072 | 0.57876 | 0.54688 | 0.51503 | 0.48418 | 0.45246 | 0.4215 | 0.39129 | 0.36319 | 0.33899 | 0.32102 | 0.31044 | 0.30845 | 0.31312 | 0.32241 | 0.33627 | 0.35318 | 0.36978 | 0.38335 | 0.38253 | 0.34806 | 0.31442 | 0.28235 | 0.25185 | 0.59072 | 7 | 0.97215 | Slope | 0.8 | 0.055317 |  | 0.72618 | 0 | 0.97215 | Slope | 2 | 0.8 | 0 | 20 | -20 | 0.00028036 | 0.00013967 | 0.0017828
142 | 0:24 | -5.5317 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -6.2973 | -0.062973 | -0.062973 | -5.5317 | 0.00038277 | [13 empty] | 0.96382 | 1 | 0.96097 | 0.85978 | 0.72433 | 0.56053 | 0.3836 | 0.22181 | 0.097413 | 0.019726 | -0.036602 | -0.10754 | -0.19264 | -0.29117 | -0.40797 | -0.5343 | -0.65399 | -0.75646 | -0.83655 | -0.88267 | -0.89537 | -0.88133 | -0.83655 | -0.74912 | -0.62562 | -0.47958 | -0.31424 | -0.1416 | 0.026026 | 0.17859 | 0.31149 | -0.0031486 | 0.0028771 | 0.00014385 | 0.00014385 | 0 | 0 | 0.0017389 | 0.05 | 0.31091 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.68923 | 0.71244 | 0.74898 | 0.80005 | 0.85749 | 0.91517 | 0.97213 | 0.96963 | 0.90732 | 0.84509 | 0.78588 | 0.72405 | 0.66452 | 0.60721 | 0.55623 | 0.51697 | 0.49642 | 0.498 | 0.52536 | 0.5727 | 0.63391 | 0.70883 | 0.79289 | 0.87601 | 0.95005 | 0.9809 | 0.91085 | 0.84326 | 0.78038 | 0.72219 | 0.66722 | 0.9809 | 25 | Slope | 0.2 | 0.56308 | 0.57081 | 0.57188 | 0.5778 | 0.58583 | 0.59395 | 0.60182 | 0.58988 | 0.55799 | 0.52614 | 0.49529 | 0.46357 | 0.43262 | 0.4024 | 0.3743 | 0.3501 | 0.33214 | 0.32155 | 0.31956 | 0.32423 | 0.33353 | 0.34739 | 0.3643 | 0.38089 | 0.39446 | 0.39363 | 0.35917 | 0.32553 | 0.29346 | 0.26295 | 0.23352 | 0.60182 | 6 | 0.97213 | Slope | 0.83333 | 0.062973 |  | 0.68829 | 0 | 0.97213 | Slope | 2 | 0.83333 | 0 | 20 | -20 | 0.00038277 | 0.00014161 | 0.0017389
143 | 0:24 | -6.2973 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.2255 | -0.072255 | -0.072255 | -6.2973 | 0.00046411 | [13 empty] | 0.96097 | 1 | 0.95719 | 0.84552 | 0.68787 | 0.50527 | 0.32618 | 0.175 | 0.078539 | 0.021101 | -0.033696 | -0.095353 | -0.17784 | -0.29075 | -0.41863 | -0.54403 | -0.65587 | -0.75491 | -0.83009 | -0.87159 | -0.88006 | -0.85756 | -0.80226 | -0.71504 | -0.5961 | -0.44744 | -0.28303 | -0.11477 | 0.048356 | 0.19907 | 0.33099 | -0.0036127 | 0.0025116 | 0.00012558 | 0.00012558 | 0 | 0 | 0.0016717 | 0.05 | 0.28771 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.71242 | 0.74896 | 0.80004 | 0.85748 | 0.91515 | 0.97212 | 0.96965 | 0.90733 | 0.84511 | 0.7859 | 0.72407 | 0.66454 | 0.60722 | 0.55625 | 0.51699 | 0.49644 | 0.49801 | 0.52538 | 0.57272 | 0.63393 | 0.70885 | 0.79291 | 0.87603 | 0.95007 | 0.98088 | 0.91083 | 0.84324 | 0.78037 | 0.72218 | 0.6672 | 0.61509 | 0.98088 | 24 | Slope | 0.23333 | 0.57081 | 0.58299 | 0.5889 | 0.59694 | 0.60505 | 0.61293 | 0.60099 | 0.56911 | 0.53726 | 0.50641 | 0.47469 | 0.44373 | 0.41352 | 0.38542 | 0.36122 | 0.34326 | 0.33267 | 0.33068 | 0.33535 | 0.34464 | 0.35851 | 0.37541 | 0.39201 | 0.40558 | 0.40474 | 0.37028 | 0.33663 | 0.30457 | 0.27406 | 0.24462 | 0.21614 | 0.61293 | 5 | 0.97212 | Slope | 0.86667 | 0.072255 |  | 0.64234 | 0 | 0.97212 | Slope | 2 | 0.86667 | 0 | 20 | -20 | 0.00046411 | 0.00014547 | 0.0016717
144 | 0:24 | -7.2255 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.6038 | -0.076038 | -0.076038 | -7.2255 | 0.00018915 | [13 empty] | 0.95719 | 1 | 0.952 | 0.82223 | 0.64811 | 0.4655 | 0.29825 | 0.17996 | 0.10649 | 0.048386 | 0.0022183 | -0.059184 | -0.16263 | -0.29248 | -0.42261 | -0.54092 | -0.65311 | -0.75053 | -0.82034 | -0.85818 | -0.86284 | -0.83739 | -0.78988 | -0.70781 | -0.58372 | -0.43397 | -0.27219 | -0.1064 | 0.05755 | 0.21005 | 0.34472 | -0.0038019 | 0.0020009 | 0.00010004 | 0.00010004 | 0 | 0 | 0.0015767 | 0.05 | 0.25116 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.74894 | 0.80001 | 0.85745 | 0.91513 | 0.97209 | 0.96968 | 0.90736 | 0.84514 | 0.78592 | 0.7241 | 0.66456 | 0.60725 | 0.55628 | 0.51701 | 0.49646 | 0.49804 | 0.5254 | 0.57275 | 0.63396 | 0.70888 | 0.79293 | 0.87606 | 0.95009 | 0.98086 | 0.91081 | 0.84321 | 0.78034 | 0.72215 | 0.66718 | 0.61506 | 0.56527 | 0.98086 | 23 | Slope | 0.26667 | 0.58298 | 0.6 | 0.60804 | 0.61615 | 0.62403 | 0.61211 | 0.58023 | 0.54838 | 0.51753 | 0.48581 | 0.45485 | 0.42464 | 0.39654 | 0.37234 | 0.35438 | 0.34379 | 0.3418 | 0.34647 | 0.35576 | 0.36963 | 0.38653 | 0.40313 | 0.4167 | 0.41584 | 0.38138 | 0.34774 | 0.31567 | 0.28516 | 0.25573 | 0.22724 | 0.19954 | 0.62403 | 4 | 0.97209 | Slope | 0.9 | 0.076038 |  | 0.62361 | 0 | 0.97209 | Slope | 2 | 0.9 | 0 | 20 | -20 | 0.00018915 | 0.00015114 | 0.0015767
145 | 0:24 | -7.6038 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -6.741 | -0.06741 | -0.06741 | -7.6038 | 0.00043138 | [13 empty] | 0.952 | 1 | 0.94341 | 0.79867 | 0.62212 | 0.44827 | 0.31429 | 0.22123 | 0.14644 | 0.097605 | 0.051203 | -0.033652 | -0.15633 | -0.28961 | -0.4123 | -0.53241 | -0.64483 | -0.7364 | -0.80352 | -0.84234 | -0.85106 | -0.84018 | -0.7999 | -0.71226 | -0.58637 | -0.4382 | -0.27733 | -0.1084 | 0.060156 | 0.21852 | 0.34433 | -0.0033705 | 0.0014265 | 7.1325e-05 | 7.1325e-05 | 0 | 0 | 0.0014616 | 0.05 | 0.20009 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.79998 | 0.85742 | 0.9151 | 0.97206 | 0.9697 | 0.90739 | 0.84517 | 0.78595 | 0.72413 | 0.66459 | 0.60728 | 0.55631 | 0.51704 | 0.49649 | 0.49807 | 0.52543 | 0.57277 | 0.63399 | 0.7089 | 0.79296 | 0.87609 | 0.95012 | 0.98083 | 0.91078 | 0.84318 | 0.78031 | 0.72212 | 0.66715 | 0.61503 | 0.56524 | 0.52397 | 0.98083 | 22 | Slope | 0.3 | 0.59999 | 0.61914 | 0.62725 | 0.63513 | 0.62323 | 0.59135 | 0.5595 | 0.52865 | 0.49693 | 0.46597 | 0.43576 | 0.40766 | 0.38346 | 0.3655 | 0.35491 | 0.35292 | 0.35759 | 0.36688 | 0.38075 | 0.39765 | 0.41425 | 0.42782 | 0.42694 | 0.39248 | 0.35884 | 0.32677 | 0.29626 | 0.26683 | 0.23834 | 0.21064 | 0.18577 | 0.63513 | 3 | 0.97206 | Slope | 0.93333 | 0.06741 |  | 0.66632 | 0 | 0.97206 | Slope | 2 | 0.93333 | 0 | 20 | -20 | 0.00043138 | 0.00015828 | 0.0014616
146 | 0:24 | -6.741 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.4893 | -0.054893 | -0.054893 | -6.741 | 0.00062585 | [13 empty] | 0.94341 | 1 | 0.93795 | 0.79126 | 0.62313 | 0.48126 | 0.37355 | 0.28115 | 0.21607 | 0.16703 | 0.097165 | -0.0066128 | -0.13349 | -0.2609 | -0.38902 | -0.51235 | -0.61971 | -0.71162 | -0.78614 | -0.83497 | -0.86042 | -0.85759 | -0.81463 | -0.72797 | -0.60586 | -0.46078 | -0.29917 | -0.12781 | 0.044942 | 0.19435 | 0.31037 | -0.0027447 | 0.00084974 | 4.2487e-05 | 4.2487e-05 | 0 | 0 | 0.0013791 | 0.05 | 0.14265 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.85739 | 0.91507 | 0.97203 | 0.96973 | 0.90742 | 0.8452 | 0.78598 | 0.72416 | 0.66462 | 0.60731 | 0.55633 | 0.51707 | 0.49652 | 0.4981 | 0.52546 | 0.5728 | 0.63402 | 0.70893 | 0.79299 | 0.87612 | 0.95015 | 0.9808 | 0.91075 | 0.84316 | 0.78028 | 0.72209 | 0.66712 | 0.615 | 0.56522 | 0.52394 | 0.49187 | 0.9808 | 21 | Slope | 0.33333 | 0.61913 | 0.63836 | 0.64623 | 0.63436 | 0.60247 | 0.57062 | 0.53977 | 0.50805 | 0.47709 | 0.44688 | 0.41878 | 0.39458 | 0.37662 | 0.36603 | 0.36404 | 0.36871 | 0.37801 | 0.39187 | 0.40878 | 0.42537 | 0.43894 | 0.43804 | 0.40358 | 0.36994 | 0.33787 | 0.30736 | 0.27793 | 0.24945 | 0.22174 | 0.19687 | 0.17507 | 0.64623 | 2 | 0.97203 | Slope | 0.96667 | 0.054893 |  | 0.72828 | 0 | 0.97203 | Slope | 2 | 0.96667 | 0 | 20 | -20 | 0.00062585 | 0.00016643 | 0.0013791
147 | 0:24 | -5.4893 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.2643 | -0.042643 | -0.042643 | -5.4893 | 0.0006125 | [13 empty] | 0.93795 | 1 | 0.93879 | 0.80182 | 0.66394 | 0.54964 | 0.44741 | 0.36647 | 0.30258 | 0.23109 | 0.14243 | 0.033172 | -0.090002 | -0.22734 | -0.36174 | -0.48018 | -0.59007 | -0.69398 | -0.78106 | -0.84377 | -0.87449 | -0.87029 | -0.83008 | -0.74943 | -0.63381 | -0.49295 | -0.33461 | -0.16516 | -0.0044948 | 0.13316 | 0.24646 | -0.0021322 | 0.0002801 | 1.4005e-05 | 1.4005e-05 | 0 | 0 | 0.0013575 | 0.05 | 0.084974 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.91504 | 0.972 | 0.96976 | 0.90745 | 0.84522 | 0.78601 | 0.72418 | 0.66465 | 0.60734 | 0.55636 | 0.5171 | 0.49655 | 0.49813 | 0.52549 | 0.57283 | 0.63404 | 0.70896 | 0.79302 | 0.87614 | 0.95018 | 0.98077 | 0.91072 | 0.84313 | 0.78025 | 0.72206 | 0.66709 | 0.61497 | 0.56519 | 0.52391 | 0.49184 | 0.46458 | 0.98077 | 20 | Slope | 0.36667 | 0.63835 | 0.65733 | 0.64548 | 0.61359 | 0.58174 | 0.55089 | 0.51917 | 0.48822 | 0.458 | 0.4299 | 0.4057 | 0.38774 | 0.37715 | 0.37516 | 0.37983 | 0.38913 | 0.40299 | 0.4199 | 0.43649 | 0.45006 | 0.44915 | 0.41468 | 0.38104 | 0.34897 | 0.31847 | 0.28903 | 0.26055 | 0.23284 | 0.20797 | 0.18617 | 0.16597 | 0.65733 | 1 | 0.972 | Slope | 1 | 0.042643 |  | 0.78892 | 0 | 0.972 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0006125 | 0.00017496 | 0.0013575
148 | 0:24 | -4.2643 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -3.6515 | -0.036515 | -0.036515 | -4.2643 | 0.00030644 | [13 empty] | 0.93879 | 1 | 0.94513 | 0.83396 | 0.7241 | 0.62127 | 0.53319 | 0.45667 | 0.37332 | 0.28297 | 0.18549 | 0.076093 | -0.061883 | -0.20793 | -0.33664 | -0.45846 | -0.58238 | -0.69741 | -0.79074 | -0.85159 | -0.87881 | -0.87526 | -0.83946 | -0.76594 | -0.65818 | -0.52604 | -0.3765 | -0.22346 | -0.078712 | 0.050896 | 0.1557 | -0.0018257 | -0.00030224 | -1.5112e-05 | -1.5112e-05 | 0 | 0 | 0.001411 | 0.05 | 0.02801 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.97198 | 0.96979 | 0.90747 | 0.84525 | 0.78604 | 0.72421 | 0.66468 | 0.60736 | 0.55639 | 0.51713 | 0.49658 | 0.49815 | 0.52552 | 0.57286 | 0.63407 | 0.70899 | 0.79305 | 0.87617 | 0.95021 | 0.98074 | 0.91069 | 0.8431 | 0.78023 | 0.72203 | 0.66706 | 0.61495 | 0.56516 | 0.52388 | 0.49181 | 0.46455 | 0.44424 | 0.98074 | 19 | Slope | 0.4 | 0.65733 | 0.6566 | 0.62471 | 0.59286 | 0.56201 | 0.53029 | 0.49934 | 0.46912 | 0.44102 | 0.41682 | 0.39886 | 0.38827 | 0.38628 | 0.39095 | 0.40025 | 0.41411 | 0.43102 | 0.44761 | 0.46118 | 0.46025 | 0.42579 | 0.39214 | 0.36008 | 0.32957 | 0.30013 | 0.27165 | 0.24394 | 0.21907 | 0.19727 | 0.17707 | 0.15919 | 0.65733 | 0 | 0.97198 | Slope | 1 | 0.036515 |  | 0.81925 | 0 | 0.97198 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00030644 | 0.00018414 | 0.001411
149 | 0:25 | -3.6515 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.5351 | -0.025351 | -0.025351 | -3.6515 | 0.00055819 | [13 empty] | 0.94513 | 1 | 0.95736 | 0.87059 | 0.77559 | 0.68883 | 0.60835 | 0.51686 | 0.41669 | 0.31593 | 0.21513 | 0.087128 | -0.060609 | -0.19886 | -0.33006 | -0.46622 | -0.59955 | -0.71465 | -0.79886 | -0.85197 | -0.87569 | -0.87235 | -0.84012 | -0.77308 | -0.6747 | -0.55361 | -0.42162 | -0.28676 | -0.15445 | -0.037204 | -0.011212 | -0.0012675 | -0.0009254 | -4.627e-05 | -4.627e-05 | 0 | 0 | 0.0015236 | 0.05 | -0.030224 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.96982 | 0.90751 | 0.84528 | 0.78607 | 0.72425 | 0.66471 | 0.6074 | 0.55642 | 0.51716 | 0.49661 | 0.49819 | 0.52555 | 0.57289 | 0.6341 | 0.70902 | 0.79308 | 0.8762 | 0.95024 | 0.98071 | 0.91066 | 0.84307 | 0.78019 | 0.722 | 0.66703 | 0.61491 | 0.56513 | 0.52385 | 0.49178 | 0.46452 | 0.44421 | 0.40215 | 0.98071 | 18 | Slope | 0.43333 | 0.65661 | 0.63584 | 0.60398 | 0.57313 | 0.54142 | 0.51046 | 0.48024 | 0.45214 | 0.42794 | 0.40998 | 0.3994 | 0.3974 | 0.40208 | 0.41137 | 0.42523 | 0.44214 | 0.45873 | 0.4723 | 0.47135 | 0.43689 | 0.40324 | 0.37118 | 0.34067 | 0.31123 | 0.28275 | 0.25504 | 0.23017 | 0.20837 | 0.18817 | 0.17029 | 0.14516 | 0.65661 | 0 | 0.96982 | Slope | 1 | 0.025351 |  | 0.87451 | 0 | 0.96982 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00055819 | 0.00019291 | 0.0015236
150 | 0:25 | -2.5351 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -1.8231 | -0.018231 | -0.018231 | -2.5351 | 0.00035596 | [13 empty] | 0.95736 | 1 | 0.96654 | 0.89367 | 0.81395 | 0.73653 | 0.64679 | 0.54201 | 0.43067 | 0.32288 | 0.19882 | 0.057928 | -0.082871 | -0.22434 | -0.36975 | -0.51136 | -0.63573 | -0.73395 | -0.80612 | -0.85043 | -0.86855 | -0.86322 | -0.83269 | -0.77153 | -0.68257 | -0.57559 | -0.45952 | -0.33823 | -0.21979 | -0.18025 | -0.13354 | -0.00091157 | -0.0015476 | -7.7381e-05 | -7.7381e-05 | 0 | 0 | 0.0016922 | 0.05 | -0.09254 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.90754 | 0.84532 | 0.7861 | 0.72428 | 0.66474 | 0.60743 | 0.55645 | 0.51719 | 0.49664 | 0.49822 | 0.52558 | 0.57292 | 0.63414 | 0.70905 | 0.79311 | 0.87624 | 0.95027 | 0.98068 | 0.91063 | 0.84304 | 0.78016 | 0.72197 | 0.667 | 0.61488 | 0.5651 | 0.52382 | 0.49175 | 0.46449 | 0.44417 | 0.40212 | 0.38478 | 0.98068 | 17 | Slope | 0.46667 | 0.63585 | 0.61511 | 0.58426 | 0.55254 | 0.52158 | 0.49136 | 0.46326 | 0.43906 | 0.4211 | 0.41052 | 0.40853 | 0.4132 | 0.42249 | 0.43635 | 0.45326 | 0.46986 | 0.48342 | 0.48245 | 0.44799 | 0.41435 | 0.38228 | 0.35177 | 0.32233 | 0.29385 | 0.26614 | 0.24127 | 0.21947 | 0.19927 | 0.18139 | 0.15626 | 0.13937 | 0.63585 | 0 | 0.90754 | Slope | 1 | 0.018231 |  | 0.90975 | 0 | 0.90754 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00035596 | 0.00020026 | 0.0016922
151 | 0:25 | -1.8231 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.202 | -0.02202 | -0.02202 | -1.8231 | 0.00018941 | [13 empty] | 0.96654 | 1 | 0.97194 | 0.91007 | 0.83955 | 0.75779 | 0.65793 | 0.54236 | 0.4229 | 0.29128 | 0.15217 | 0.014997 | -0.13099 | -0.28711 | -0.43679 | -0.56614 | -0.67177 | -0.75707 | -0.81789 | -0.85305 | -0.86544 | -0.85783 | -0.82815 | -0.77142 | -0.69023 | -0.59378 | -0.48808 | -0.37796 | -0.32676 | -0.27054 | -0.20212 | -0.001101 | -0.0021398 | -0.00010699 | -0.00010699 | 0 | 0 | 0.0018683 | 0.05 | -0.15476 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.84534 | 0.78613 | 0.72431 | 0.66477 | 0.60746 | 0.55648 | 0.51722 | 0.49667 | 0.49825 | 0.52561 | 0.57295 | 0.63416 | 0.70908 | 0.79314 | 0.87627 | 0.9503 | 0.98065 | 0.9106 | 0.84301 | 0.78013 | 0.72194 | 0.66697 | 0.61485 | 0.56507 | 0.52379 | 0.49172 | 0.46446 | 0.44415 | 0.40209 | 0.38475 | 0.39533 | 0.98065 | 16 | Slope | 0.5 | 0.61511 | 0.59538 | 0.56366 | 0.5327 | 0.50249 | 0.47438 | 0.45018 | 0.43222 | 0.42164 | 0.41965 | 0.42432 | 0.43361 | 0.44747 | 0.46438 | 0.48098 | 0.49454 | 0.49355 | 0.45909 | 0.42545 | 0.39338 | 0.36287 | 0.33344 | 0.30495 | 0.27724 | 0.25237 | 0.23057 | 0.21038 | 0.19249 | 0.16736 | 0.15047 | 0.14289 | 0.61511 | 0 | 0.84534 | Slope | 1 | 0.02202 |  | 0.891 | 0 | 0.84534 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00018941 | 0.00020545 | 0.0018683
152 | 0:25 | -2.202 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -1.9115 | -0.019115 | -0.019115 | -2.202 | 0.00014522 | [13 empty] | 0.97194 | 1 | 0.97629 | 0.92195 | 0.84958 | 0.75962 | 0.65029 | 0.52832 | 0.38789 | 0.24257 | 0.10737 | -0.034555 | -0.19548 | -0.35777 | -0.4976 | -0.60944 | -0.70238 | -0.77594 | -0.82665 | -0.85476 | -0.86321 | -0.85402 | -0.82518 | -0.77234 | -0.69848 | -0.60983 | -0.51326 | -0.46073 | -0.39915 | -0.32695 | -0.23896 | -0.00095576 | -0.002758 | -0.0001379 | -0.0001379 | 0 | 0 | 0.0020397 | 0.05 | -0.21398 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.78616 | 0.72434 | 0.6648 | 0.60749 | 0.55652 | 0.51725 | 0.4967 | 0.49828 | 0.52564 | 0.57298 | 0.6342 | 0.70911 | 0.79317 | 0.8763 | 0.95033 | 0.98062 | 0.91057 | 0.84297 | 0.7801 | 0.72191 | 0.66694 | 0.61482 | 0.56504 | 0.52376 | 0.49169 | 0.46443 | 0.44411 | 0.40206 | 0.38472 | 0.3953 | 0.4345 | 0.98062 | 15 | Slope | 0.53333 | 0.59539 | 0.57478 | 0.54382 | 0.51361 | 0.48551 | 0.46131 | 0.44334 | 0.43276 | 0.43077 | 0.43544 | 0.44473 | 0.45859 | 0.4755 | 0.4921 | 0.50567 | 0.50465 | 0.47019 | 0.43655 | 0.40448 | 0.37397 | 0.34454 | 0.31605 | 0.28835 | 0.26347 | 0.24167 | 0.22148 | 0.20359 | 0.17846 | 0.16157 | 0.15399 | 0.15594 | 0.59539 | 0 | 0.78616 | Slope | 1 | 0.019115 |  | 0.90538 | 0 | 0.78616 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00014522 | 0.00020812 | 0.0020397
153 | 0:25 | -1.9115 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -1.9854 | -0.019854 | -0.019854 | -1.9115 | 3.692e-05 | [13 empty] | 0.97629 | 1 | 0.97901 | 0.92448 | 0.84567 | 0.74605 | 0.62928 | 0.4868 | 0.33265 | 0.19025 | 0.049253 | -0.10867 | -0.27676 | -0.42873 | -0.55071 | -0.65031 | -0.73131 | -0.79359 | -0.83559 | -0.85811 | -0.86324 | -0.85267 | -0.82372 | -0.77412 | -0.70515 | -0.62304 | -0.57381 | -0.51405 | -0.4399 | -0.35088 | -0.24231 | -0.00099268 | -0.0033534 | -0.00016767 | -0.00016767 | 0 | 0 | 0.0022058 | 0.05 | -0.2758 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.72437 | 0.66483 | 0.60752 | 0.55654 | 0.51728 | 0.49673 | 0.49831 | 0.52567 | 0.57301 | 0.63423 | 0.70914 | 0.7932 | 0.87633 | 0.95036 | 0.98059 | 0.91054 | 0.84294 | 0.78007 | 0.72188 | 0.66691 | 0.61479 | 0.56501 | 0.52373 | 0.49166 | 0.4644 | 0.44408 | 0.40203 | 0.38469 | 0.39527 | 0.43447 | 0.49564 | 0.98059 | 14 | Slope | 0.56667 | 0.57479 | 0.55494 | 0.52473 | 0.49663 | 0.47243 | 0.45447 | 0.44388 | 0.44189 | 0.44656 | 0.45585 | 0.46971 | 0.48662 | 0.50322 | 0.51679 | 0.51575 | 0.48129 | 0.44765 | 0.41558 | 0.38507 | 0.35564 | 0.32715 | 0.29945 | 0.27458 | 0.25278 | 0.23258 | 0.21469 | 0.18956 | 0.17267 | 0.16509 | 0.16705 | 0.17632 | 0.57479 | 0 | 0.72437 | Slope | 1 | 0.019854 |  | 0.90172 | 0 | 0.72437 | Slope | 2 | 1 | 0 | 20 | -20 | 3.692e-05 | 0.00020825 | 0.0022058
154 | 0:25 | -1.9854 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.8861 | -0.028861 | -0.028861 | -1.9854 | 0.00045038 | [13 empty] | 0.97901 | 1 | 0.97822 | 0.91847 | 0.83075 | 0.72378 | 0.58779 | 0.43206 | 0.28077 | 0.13282 | -0.024677 | -0.19197 | -0.3519 | -0.48681 | -0.5971 | -0.68539 | -0.75539 | -0.80861 | -0.84429 | -0.86255 | -0.8652 | -0.85258 | -0.82431 | -0.7771 | -0.71246 | -0.66757 | -0.61464 | -0.5462 | -0.45915 | -0.35236 | -0.24997 | -0.0014431 | -0.0039265 | -0.00019633 | -0.00019633 | 0 | 0 | 0.0023559 | 0.05 | -0.33534 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.66486 | 0.60755 | 0.55657 | 0.51731 | 0.49676 | 0.49834 | 0.5257 | 0.57304 | 0.63425 | 0.70917 | 0.79323 | 0.87635 | 0.95039 | 0.98056 | 0.91051 | 0.84292 | 0.78004 | 0.72185 | 0.66688 | 0.61476 | 0.56498 | 0.5237 | 0.49163 | 0.46437 | 0.44406 | 0.402 | 0.38466 | 0.39524 | 0.43444 | 0.49561 | 0.56257 | 0.98056 | 13 | Slope | 0.6 | 0.55495 | 0.53585 | 0.50775 | 0.48355 | 0.46559 | 0.455 | 0.45301 | 0.45768 | 0.46697 | 0.48083 | 0.49774 | 0.51434 | 0.52791 | 0.52685 | 0.49239 | 0.45875 | 0.42668 | 0.39617 | 0.36674 | 0.33825 | 0.31055 | 0.28568 | 0.26388 | 0.24368 | 0.2258 | 0.20067 | 0.18378 | 0.17619 | 0.17815 | 0.18743 | 0.19863 | 0.55495 | 0 | 0.66486 | Slope | 1 | 0.028861 |  | 0.85714 | 0 | 0.66486 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00045038 | 0.00020594 | 0.0023559
155 | 0:26 | -2.8861 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -3.1459 | -0.031459 | -0.031459 | -2.8861 | 0.00012988 | [13 empty] | 0.97822 | 1 | 0.97635 | 0.91189 | 0.82084 | 0.70055 | 0.55442 | 0.40241 | 0.24759 | 0.083909 | -0.086706 | -0.25284 | -0.40076 | -0.52654 | -0.62839 | -0.70867 | -0.77206 | -0.82042 | -0.85263 | -0.86869 | -0.86996 | -0.85821 | -0.83124 | -0.78713 | -0.74396 | -0.70299 | -0.64961 | -0.57678 | -0.47871 | -0.37878 | -0.29217 | -0.0015729 | -0.0044362 | -0.00022181 | -0.00022181 | 0 | 0 | 0.0024498 | 0.05 | -0.39265 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.60757 | 0.5566 | 0.51734 | 0.49678 | 0.49836 | 0.52572 | 0.57307 | 0.63428 | 0.7092 | 0.79326 | 0.87638 | 0.95041 | 0.98054 | 0.91048 | 0.84289 | 0.78002 | 0.72183 | 0.66686 | 0.61474 | 0.56495 | 0.52367 | 0.4916 | 0.46435 | 0.44403 | 0.40197 | 0.38464 | 0.39522 | 0.43442 | 0.49558 | 0.56255 | 0.62925 | 0.98054 | 12 | Slope | 0.63333 | 0.53586 | 0.51887 | 0.49467 | 0.47671 | 0.46612 | 0.46413 | 0.4688 | 0.47809 | 0.49195 | 0.50886 | 0.52546 | 0.53903 | 0.53796 | 0.50349 | 0.46985 | 0.43778 | 0.40728 | 0.37784 | 0.34936 | 0.32165 | 0.29678 | 0.27498 | 0.25478 | 0.2369 | 0.21177 | 0.19488 | 0.1873 | 0.18925 | 0.19853 | 0.20974 | 0.22086 | 0.53903 | 11 | 0.95041 | Slope | 0.66667 | 0.031459 |  | 0.84428 | 0 | 0.95041 | Slope | 2 | 0.66667 | 0 | 20 | -20 | 0.00012988 | 0.00020126 | 0.0024498
156 | 0:26 | -3.1459 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.1587 | -0.021587 | -0.021587 | -3.1459 | 0.0004936 | [13 empty] | 0.97635 | 1 | 0.97537 | 0.91093 | 0.81231 | 0.68504 | 0.54328 | 0.3895 | 0.21994 | 0.040766 | -0.13318 | -0.29114 | -0.43224 | -0.5517 | -0.64745 | -0.7228 | -0.78263 | -0.82838 | -0.85887 | -0.87388 | -0.87615 | -0.86546 | -0.84101 | -0.80316 | -0.77058 | -0.73634 | -0.68632 | -0.60931 | -0.51896 | -0.43394 | -0.371 | -0.0010793 | -0.0048289 | -0.00024144 | -0.00024144 | 0 | 0 | 0.0024987 | 0.05 | -0.44362 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.55662 | 0.51736 | 0.4968 | 0.49838 | 0.52574 | 0.57309 | 0.6343 | 0.70922 | 0.79328 | 0.8764 | 0.95043 | 0.98052 | 0.91046 | 0.84287 | 0.78 | 0.72181 | 0.66684 | 0.61472 | 0.56493 | 0.52365 | 0.49158 | 0.46433 | 0.44401 | 0.40195 | 0.38462 | 0.3952 | 0.4344 | 0.49556 | 0.56253 | 0.62923 | 0.688 | 0.98052 | 11 | Slope | 0.66667 | 0.51887 | 0.50579 | 0.48782 | 0.47724 | 0.47525 | 0.47992 | 0.48921 | 0.50307 | 0.51998 | 0.53658 | 0.55014 | 0.54906 | 0.5146 | 0.48096 | 0.44889 | 0.41838 | 0.38895 | 0.36046 | 0.33276 | 0.30788 | 0.28608 | 0.26589 | 0.248 | 0.22287 | 0.20598 | 0.1984 | 0.20035 | 0.20963 | 0.22084 | 0.23197 | 0.24044 | 0.55014 | 10 | 0.95043 | Slope | 0.7 | 0.021587 |  | 0.89315 | 0 | 0.95043 | Slope | 2 | 0.7 | 0 | 20 | -20 | 0.0004936 | 0.00019428 | 0.0024987
157 | 0:26 | -2.1587 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -0.4051 | -0.004051 | -0.004051 | -2.1587 | 0.00087679 | [13 empty] | 0.97537 | 1 | 0.97605 | 0.90752 | 0.80366 | 0.67992 | 0.53676 | 0.36913 | 0.18377 | 0.0010885 | -0.16597 | -0.31888 | -0.45456 | -0.56812 | -0.65895 | -0.73102 | -0.78848 | -0.83266 | -0.86079 | -0.87537 | -0.87821 | -0.86901 | -0.8367 | -0.81288 | -0.79124 | -0.76509 | -0.71605 | -0.64684 | -0.56928 | -0.5019 | -0.44261 | -0.00020255 | -0.0050344 | -0.00025172 | -0.00025172 | 0 | 0 | 0.0025198 | 0.05 | -0.48289 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.51737 | 0.49681 | 0.49839 | 0.52575 | 0.5731 | 0.63431 | 0.70923 | 0.79329 | 0.87641 | 0.95044 | 0.98051 | 0.91045 | 0.84286 | 0.77999 | 0.7218 | 0.66683 | 0.61471 | 0.56492 | 0.52364 | 0.49157 | 0.46432 | 0.444 | 0.40194 | 0.38461 | 0.39519 | 0.43439 | 0.49555 | 0.56252 | 0.62922 | 0.68799 | 0.73351 | 0.98051 | 10 | Slope | 0.7 | 0.50579 | 0.49894 | 0.48835 | 0.48636 | 0.49103 | 0.50033 | 0.51419 | 0.5311 | 0.54769 | 0.56126 | 0.56017 | 0.52571 | 0.49206 | 0.46 | 0.42949 | 0.40005 | 0.37157 | 0.34386 | 0.31899 | 0.29719 | 0.27699 | 0.25911 | 0.23398 | 0.21709 | 0.20951 | 0.21146 | 0.22074 | 0.23195 | 0.24307 | 0.25155 | 0.25561 | 0.56126 | 9 | 0.95044 | Slope | 0.73333 | 0.004051 |  | 0.97995 | 0 | 0.95044 | Slope | 2 | 0.73333 | 0 | 20 | -20 | 0.00087679 | 0.00018508 | 0.0025198
158 | 0:26 | -0.4051 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.0985 | 0.010985 | 0.010985 | -0.4051 | 0.00075179 | [13 empty] | 0.97605 | 1 | 0.97344 | 0.89997 | 0.79733 | 0.6712 | 0.51471 | 0.33198 | 0.14496 | -0.030972 | -0.19467 | -0.34264 | -0.47193 | -0.57985 | -0.66713 | -0.73669 | -0.79257 | -0.8321 | -0.85734 | -0.87169 | -0.87445 | -0.84485 | -0.82733 | -0.8159 | -0.8041 | -0.78206 | -0.73992 | -0.68067 | -0.61375 | -0.54205 | -0.4725 | 0.00054924 | -0.0050186 | -0.00025093 | -0.00025093 | 0 | 0 | 0.0025181 | 0.05 | -0.50344 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.49681 | 0.49839 | 0.52575 | 0.5731 | 0.63431 | 0.70923 | 0.79329 | 0.87641 | 0.95044 | 0.98051 | 0.91045 | 0.84286 | 0.77999 | 0.7218 | 0.66683 | 0.61471 | 0.56492 | 0.52364 | 0.49158 | 0.46432 | 0.444 | 0.40194 | 0.38461 | 0.39519 | 0.43439 | 0.49556 | 0.56252 | 0.62922 | 0.68799 | 0.73351 | 0.76639 | 0.98051 | 9 | Slope | 0.73333 | 0.49894 | 0.49946 | 0.49747 | 0.50214 | 0.51144 | 0.5253 | 0.54221 | 0.5588 | 0.57237 | 0.57128 | 0.53682 | 0.50318 | 0.47111 | 0.4406 | 0.41116 | 0.38268 | 0.35497 | 0.3301 | 0.3083 | 0.28811 | 0.27022 | 0.24509 | 0.2282 | 0.22062 | 0.22257 | 0.23185 | 0.24306 | 0.25419 | 0.26266 | 0.26672 | 0.26657 | 0.57237 | 8 | 0.95044 | Slope | 0.76667 | 0.010985 |  | 0.94562 | 0 | 0.95044 | Slope | 2 | 0.76667 | 0 | 20 | -20 | 0.00075179 | 0.00017391 | 0.0025181
159 | 0:26 | 1.0985 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.3948 | 0.023948 | 0.023948 | 1.0985 | 0.00064816 | [13 empty] | 0.97344 | 1 | 0.97196 | 0.89912 | 0.79508 | 0.65867 | 0.48941 | 0.30673 | 0.12558 | -0.048931 | -0.20874 | -0.35064 | -0.47439 | -0.57912 | -0.66428 | -0.73277 | -0.78256 | -0.81759 | -0.84241 | -0.85582 | -0.82263 | -0.81064 | -0.80923 | -0.81179 | -0.80928 | -0.79338 | -0.75782 | -0.70081 | -0.61994 | -0.52725 | -0.44563 | 0.0011974 | -0.004745 | -0.00023725 | -0.00023725 | 0 | 0 | 0.0024947 | 0.05 | -0.50186 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.49838 | 0.52574 | 0.57308 | 0.6343 | 0.70921 | 0.79327 | 0.8764 | 0.95043 | 0.98052 | 0.91047 | 0.84288 | 0.78 | 0.72181 | 0.66684 | 0.61472 | 0.56494 | 0.52366 | 0.49159 | 0.46433 | 0.44401 | 0.40196 | 0.38462 | 0.3952 | 0.4344 | 0.49557 | 0.56253 | 0.62924 | 0.688 | 0.73352 | 0.7664 | 0.79391 | 0.98052 | 8 | Slope | 0.76667 | 0.49946 | 0.50858 | 0.51325 | 0.52254 | 0.5364 | 0.55331 | 0.56991 | 0.58348 | 0.5824 | 0.54793 | 0.51429 | 0.48222 | 0.45172 | 0.42228 | 0.3938 | 0.36609 | 0.34122 | 0.31942 | 0.29922 | 0.28134 | 0.25621 | 0.23932 | 0.23173 | 0.23369 | 0.24297 | 0.25418 | 0.2653 | 0.27378 | 0.27784 | 0.27769 | 0.27575 | 0.58348 | 7 | 0.95043 | Slope | 0.8 | 0.023948 |  | 0.88146 | 0 | 0.95043 | Slope | 2 | 0.8 | 0 | 20 | -20 | 0.00064816 | 0.00016123 | 0.0024947
160 | 0:26 | 2.3948 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.9007 | 0.039007 | 0.039007 | 2.3948 | 0.00075294 | [13 empty] | 0.97196 | 1 | 0.97262 | 0.89965 | 0.78819 | 0.64113 | 0.47312 | 0.29593 | 0.11502 | -0.056142 | -0.20987 | -0.34609 | -0.46674 | -0.56946 | -0.65377 | -0.71473 | -0.75844 | -0.79275 | -0.81575 | -0.78222 | -0.76763 | -0.77326 | -0.78779 | -0.80296 | -0.80536 | -0.79331 | -0.75424 | -0.67745 | -0.5675 | -0.45847 | -0.37332 | 0.0019503 | -0.0042715 | -0.00021358 | -0.00021358 | 0 | 0 | 0.002459 | 0.05 | -0.4745 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.52571 | 0.57306 | 0.63427 | 0.70919 | 0.79325 | 0.87637 | 0.95041 | 0.98054 | 0.91049 | 0.8429 | 0.78003 | 0.72184 | 0.66687 | 0.61475 | 0.56496 | 0.52368 | 0.49161 | 0.46435 | 0.44404 | 0.40198 | 0.38465 | 0.39523 | 0.43442 | 0.49559 | 0.56255 | 0.62926 | 0.68803 | 0.73354 | 0.76643 | 0.79393 | 0.82106 | 0.98054 | 7 | Slope | 0.8 | 0.50857 | 0.52435 | 0.53365 | 0.54751 | 0.56442 | 0.58101 | 0.59458 | 0.59351 | 0.55905 | 0.52541 | 0.49334 | 0.46283 | 0.4334 | 0.40492 | 0.37721 | 0.35234 | 0.33054 | 0.31034 | 0.29246 | 0.26733 | 0.25044 | 0.24285 | 0.24481 | 0.25409 | 0.2653 | 0.27642 | 0.2849 | 0.28896 | 0.28881 | 0.28687 | 0.2848 | 0.59458 | 6 | 0.95041 | Slope | 0.83333 | 0.039007 |  | 0.80692 | 0 | 0.95041 | Slope | 2 | 0.83333 | 0 | 20 | -20 | 0.00075294 | 0.00014787 | 0.002459
161 | 0:27 | 3.9007 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 5.1011 | 0.051011 | 0.051011 | 3.9007 | 0.00060021 | [13 empty] | 0.97262 | 1 | 0.97193 | 0.89203 | 0.77055 | 0.62552 | 0.46228 | 0.28315 | 0.10422 | -0.061452 | -0.20982 | -0.34352 | -0.4627 | -0.56513 | -0.64028 | -0.69311 | -0.73553 | -0.76668 | -0.73788 | -0.71975 | -0.71972 | -0.73849 | -0.76471 | -0.78244 | -0.78507 | -0.7653 | -0.70459 | -0.59528 | -0.46507 | -0.3489 | -0.28172 | 0.0025506 | -0.0036594 | -0.00018297 | -0.00018297 | 0 | 0 | 0.0023951 | 0.05 | -0.42715 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.57303 | 0.63424 | 0.70916 | 0.79322 | 0.87634 | 0.95038 | 0.98057 | 0.91052 | 0.84293 | 0.78006 | 0.72187 | 0.6669 | 0.61478 | 0.56499 | 0.52371 | 0.49164 | 0.46439 | 0.44407 | 0.40201 | 0.38468 | 0.39526 | 0.43445 | 0.49562 | 0.56258 | 0.62929 | 0.68806 | 0.73357 | 0.76646 | 0.79396 | 0.82109 | 0.84699 | 0.98057 | 6 | Slope | 0.83333 | 0.52434 | 0.54475 | 0.55861 | 0.57552 | 0.59211 | 0.60568 | 0.60464 | 0.57017 | 0.53653 | 0.50446 | 0.47396 | 0.44452 | 0.41604 | 0.38833 | 0.36346 | 0.34166 | 0.32146 | 0.30358 | 0.27845 | 0.26156 | 0.25397 | 0.25593 | 0.26521 | 0.27642 | 0.28754 | 0.29602 | 0.30008 | 0.29993 | 0.29799 | 0.29592 | 0.29344 | 0.60568 | 5 | 0.95038 | Slope | 0.86667 | 0.051011 |  | 0.7475 | 0 | 0.95038 | Slope | 2 | 0.86667 | 0 | 20 | -20 | 0.00060021 | 0.00013474 | 0.0023951
162 | 0:27 | 5.1011 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 5.1751 | 0.051751 | 0.051751 | 5.1011 | 3.6978e-05 | [13 empty] | 0.97193 | 1 | 0.96831 | 0.88116 | 0.76366 | 0.62289 | 0.45561 | 0.27684 | 0.10227 | -0.05898 | -0.20594 | -0.33927 | -0.45932 | -0.5517 | -0.61729 | -0.66868 | -0.70701 | -0.68031 | -0.66461 | -0.65895 | -0.66961 | -0.69956 | -0.7254 | -0.73866 | -0.72631 | -0.68267 | -0.58782 | -0.45674 | -0.31642 | -0.22392 | -0.19818 | 0.0025875 | -0.0029102 | -0.00014551 | -0.00014551 | 0 | 0 | 0.0023042 | 0.05 | -0.36594 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.6342 | 0.70912 | 0.79318 | 0.8763 | 0.95034 | 0.98061 | 0.91056 | 0.84297 | 0.78009 | 0.7219 | 0.66693 | 0.61482 | 0.56503 | 0.52375 | 0.49168 | 0.46442 | 0.44411 | 0.40205 | 0.38471 | 0.39529 | 0.43449 | 0.49566 | 0.56262 | 0.62933 | 0.6881 | 0.73361 | 0.7665 | 0.794 | 0.82113 | 0.84702 | 0.87779 | 0.98061 | 5 | Slope | 0.86667 | 0.54473 | 0.56971 | 0.58662 | 0.60321 | 0.61678 | 0.61576 | 0.5813 | 0.54766 | 0.51559 | 0.48508 | 0.45564 | 0.42716 | 0.39945 | 0.37458 | 0.35278 | 0.33259 | 0.3147 | 0.28957 | 0.27268 | 0.2651 | 0.26705 | 0.27633 | 0.28754 | 0.29866 | 0.30714 | 0.3112 | 0.31105 | 0.30911 | 0.30704 | 0.30456 | 0.30371 | 0.61678 | 4 | 0.95034 | Slope | 0.9 | 0.051751 |  | 0.74383 | 0 | 0.95034 | Slope | 2 | 0.9 | 0 | 20 | -20 | 3.6978e-05 | 0.00012284 | 0.0023042
163 | 0:27 | 5.1751 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.8698 | 0.038698 | 0.038698 | 5.1751 | 0.00065261 | [13 empty] | 0.96831 | 1 | 0.96657 | 0.88531 | 0.77264 | 0.62865 | 0.46234 | 0.2883 | 0.1185 | -0.041045 | -0.18742 | -0.32152 | -0.43109 | -0.51342 | -0.57761 | -0.6247 | -0.59847 | -0.58605 | -0.58454 | -0.59089 | -0.61407 | -0.64134 | -0.6582 | -0.64922 | -0.60886 | -0.53064 | -0.41664 | -0.27816 | -0.16821 | -0.12827 | -0.14159 | 0.0019349 | -0.0020697 | -0.00010348 | -0.00010348 | 0 | 0 | 0.002225 | 0.05 | -0.29102 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.70908 | 0.79314 | 0.87626 | 0.9503 | 0.98065 | 0.9106 | 0.84301 | 0.78014 | 0.72195 | 0.66698 | 0.61486 | 0.56507 | 0.52379 | 0.49172 | 0.46446 | 0.44415 | 0.40209 | 0.38476 | 0.39534 | 0.43453 | 0.4957 | 0.56266 | 0.62937 | 0.68814 | 0.73365 | 0.76654 | 0.79404 | 0.82117 | 0.84707 | 0.87783 | 0.91972 | 0.98065 | 4 | Slope | 0.9 | 0.56969 | 0.59771 | 0.61431 | 0.62788 | 0.62688 | 0.59242 | 0.55878 | 0.52671 | 0.4962 | 0.46677 | 0.43829 | 0.41058 | 0.38571 | 0.36391 | 0.34371 | 0.32583 | 0.3007 | 0.28381 | 0.27622 | 0.27818 | 0.28746 | 0.29867 | 0.30979 | 0.31827 | 0.32233 | 0.32218 | 0.32024 | 0.31817 | 0.31569 | 0.31483 | 0.31768 | 0.62788 | 3 | 0.9503 | Slope | 0.93333 | 0.038698 |  | 0.80844 | 0 | 0.9503 | Slope | 2 | 0.93333 | 0 | 20 | -20 | 0.00065261 | 0.00011348 | 0.002225
164 | 0:27 | 3.8698 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.7303 | 0.017303 | 0.017303 | 3.8698 | 0.0010698 | [13 empty] | 0.96657 | 1 | 0.97055 | 0.89429 | 0.78188 | 0.6416 | 0.48227 | 0.31553 | 0.15048 | -0.005527 | -0.14985 | -0.27271 | -0.37196 | -0.45211 | -0.51206 | -0.49199 | -0.4838 | -0.48974 | -0.50497 | -0.52759 | -0.54752 | -0.5641 | -0.55541 | -0.51664 | -0.44161 | -0.34891 | -0.23464 | -0.13279 | -0.082015 | -0.091249 | -0.15291 | 0.00086516 | -0.0012384 | -6.1921e-05 | -6.1921e-05 | 0 | 0 | 0.0022032 | 0.05 | -0.20697 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.7931 | 0.87622 | 0.95025 | 0.9807 | 0.91064 | 0.84305 | 0.78018 | 0.72199 | 0.66702 | 0.6149 | 0.56511 | 0.52383 | 0.49176 | 0.46451 | 0.44419 | 0.40213 | 0.3848 | 0.39538 | 0.43458 | 0.49574 | 0.56271 | 0.62941 | 0.68818 | 0.73369 | 0.76658 | 0.79408 | 0.82121 | 0.84711 | 0.87787 | 0.91976 | 0.96789 | 0.9807 | 3 | Slope | 0.93333 | 0.5977 | 0.62541 | 0.63897 | 0.63801 | 0.60355 | 0.56991 | 0.53784 | 0.50733 | 0.47789 | 0.44941 | 0.4217 | 0.39683 | 0.37503 | 0.35484 | 0.33695 | 0.31182 | 0.29493 | 0.28735 | 0.2893 | 0.29858 | 0.30979 | 0.32091 | 0.32939 | 0.33345 | 0.3333 | 0.33136 | 0.32929 | 0.32681 | 0.32596 | 0.32881 | 0.33374 | 0.63897 | 2 | 0.95025 | Slope | 0.96667 | 0.017303 |  | 0.91435 | 0 | 0.95025 | Slope | 2 | 0.96667 | 0 | 20 | -20 | 0.0010698 | 0.00010775 | 0.0022032
165 | 0:27 | 1.7303 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.0756 | 0.010756 | 0.010756 | 1.7303 | 0.00032735 | [13 empty] | 0.97055 | 1 | 0.97232 | 0.89868 | 0.79117 | 0.65849 | 0.50805 | 0.3492 | 0.19125 | 0.041036 | -0.091849 | -0.20458 | -0.30016 | -0.37601 | -0.37134 | -0.37314 | -0.38761 | -0.41537 | -0.45144 | -0.4734 | -0.48433 | -0.47739 | -0.44001 | -0.36831 | -0.28139 | -0.19399 | -0.11765 | -0.075605 | -0.078737 | -0.1358 | -0.23161 | 0.00053781 | -0.00049808 | -2.4904e-05 | -2.4904e-05 | 0 | 0 | 0.0022473 | 0.05 | -0.12384 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.87618 | 0.95022 | 0.98073 | 0.91068 | 0.84309 | 0.78022 | 0.72202 | 0.66705 | 0.61494 | 0.56515 | 0.52387 | 0.4918 | 0.46454 | 0.44423 | 0.40217 | 0.38483 | 0.39542 | 0.43461 | 0.49578 | 0.56274 | 0.62945 | 0.68822 | 0.73373 | 0.76662 | 0.79412 | 0.82125 | 0.84714 | 0.87791 | 0.9198 | 0.96793 | 0.98213 | 0.98213 | 30 | Slope | 0.033333 | 0.62539 | 0.65007 | 0.64913 | 0.61467 | 0.58103 | 0.54896 | 0.51845 | 0.48902 | 0.46053 | 0.43283 | 0.40796 | 0.38616 | 0.36596 | 0.34808 | 0.32295 | 0.30606 | 0.29847 | 0.30043 | 0.3097 | 0.32091 | 0.33204 | 0.34052 | 0.34458 | 0.34443 | 0.34248 | 0.34042 | 0.33794 | 0.33708 | 0.33993 | 0.34486 | 0.33849 | 0.65007 | 1 | 0.95022 | Slope | 1 | 0.010756 |  | 0.94676 | 0 | 0.95022 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00032735 | 0.00010616 | 0.0022473
166 | 0:27 | 1.0756 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.3902 | 0.013902 | 0.013902 | 1.0756 | 0.00015731 | [13 empty] | 0.97232 | 1 | 0.97348 | 0.90298 | 0.80102 | 0.67567 | 0.53262 | 0.38103 | 0.22953 | 0.090235 | -0.032648 | -0.14091 | -0.23167 | -0.24893 | -0.26321 | -0.2856 | -0.32056 | -0.36858 | -0.40474 | -0.41845 | -0.40653 | -0.37272 | -0.30463 | -0.22201 | -0.14031 | -0.090347 | -0.071509 | -0.081576 | -0.12954 | -0.21708 | -0.32422 | 0.00069512 | 0.00019242 | 9.6211e-06 | 9.6211e-06 | 0 | 0 | 0.002301 | 0.05 | -0.049808 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.95018 | 0.98077 | 0.91072 | 0.84312 | 0.78025 | 0.72206 | 0.66709 | 0.61497 | 0.56518 | 0.5239 | 0.49184 | 0.46458 | 0.44426 | 0.4022 | 0.38487 | 0.39545 | 0.43465 | 0.49582 | 0.56278 | 0.62948 | 0.68825 | 0.73377 | 0.76665 | 0.79416 | 0.82128 | 0.84718 | 0.87794 | 0.91983 | 0.96796 | 0.98209 | 0.92828 | 0.98209 | 29 | Slope | 0.066667 | 0.65006 | 0.66026 | 0.62579 | 0.59215 | 0.56008 | 0.52958 | 0.50014 | 0.47166 | 0.44395 | 0.41908 | 0.39728 | 0.37708 | 0.3592 | 0.33407 | 0.31718 | 0.30959 | 0.31155 | 0.32083 | 0.33204 | 0.34316 | 0.35164 | 0.3557 | 0.35555 | 0.35361 | 0.35154 | 0.34906 | 0.3482 | 0.35105 | 0.35599 | 0.34959 | 0.32054 | 0.66026 | 1 | 0.98077 | Slope | 1 | 0.013902 |  | 0.93118 | 0 | 0.98077 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00015731 | 0.00010835 | 0.002301
167 | 0:28 | 1.3902 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.1491 | 0.011491 | 0.011491 | 1.3902 | 0.00012058 | [13 empty] | 0.97348 | 1 | 0.97464 | 0.90788 | 0.81166 | 0.69244 | 0.55582 | 0.41027 | 0.2696 | 0.14081 | 0.023004 | -0.07956 | -0.11682 | -0.14759 | -0.17818 | -0.21739 | -0.27016 | -0.3169 | -0.34365 | -0.33283 | -0.29367 | -0.23098 | -0.15269 | -0.074776 | -0.031858 | -0.04087 | -0.073715 | -0.12778 | -0.20725 | -0.30803 | -0.40698 | 0.00057454 | 0.00089294 | 4.4647e-05 | 4.4647e-05 | 0 | 0 | 0.0023481 | 0.05 | 0.019242 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.9808 | 0.91075 | 0.84316 | 0.78029 | 0.72209 | 0.66712 | 0.61501 | 0.56522 | 0.52394 | 0.49187 | 0.46461 | 0.4443 | 0.40224 | 0.3849 | 0.39548 | 0.43468 | 0.49585 | 0.56281 | 0.62952 | 0.68829 | 0.7338 | 0.76669 | 0.79419 | 0.82132 | 0.84721 | 0.87798 | 0.91987 | 0.968 | 0.98206 | 0.92824 | 0.87586 | 0.98206 | 28 | Slope | 0.1 | 0.66027 | 0.63692 | 0.60327 | 0.57121 | 0.5407 | 0.51126 | 0.48278 | 0.45507 | 0.4302 | 0.4084 | 0.3882 | 0.37032 | 0.34519 | 0.3283 | 0.32072 | 0.32267 | 0.33195 | 0.34316 | 0.35428 | 0.36276 | 0.36682 | 0.36667 | 0.36473 | 0.36266 | 0.36018 | 0.35933 | 0.36218 | 0.36711 | 0.36069 | 0.33164 | 0.30307 | 0.66027 | 0 | 0.9808 | Slope | 1 | 0.011491 |  | 0.94312 | 0 | 0.9808 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00012058 | 0.00011386 | 0.0023481
168 | 0:28 | 1.1491 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 0.57287 | 0.0057287 | 0.0057287 | 1.1491 | 0.00028811 | [13 empty] | 0.97464 | 1 | 0.97608 | 0.91319 | 0.82182 | 0.7081 | 0.5771 | 0.44167 | 0.31138 | 0.18815 | 0.076586 | 0.021536 | -0.024819 | -0.068524 | -0.11345 | -0.1688 | -0.21942 | -0.25631 | -0.25923 | -0.22222 | -0.15536 | -0.083541 | -0.0095964 | 0.029984 | 0.014742 | -0.046273 | -0.12161 | -0.2044 | -0.29636 | -0.38891 | -0.47521 | 0.00028644 | 0.0015689 | 7.8444e-05 | 7.8444e-05 | 0 | 0 | 0.0023973 | 0.05 | 0.089294 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.91078 | 0.84319 | 0.78032 | 0.72213 | 0.66716 | 0.61504 | 0.56525 | 0.52397 | 0.4919 | 0.46465 | 0.44433 | 0.40227 | 0.38494 | 0.39552 | 0.43472 | 0.49588 | 0.56285 | 0.62955 | 0.68832 | 0.73384 | 0.76672 | 0.79422 | 0.82135 | 0.84725 | 0.87801 | 0.9199 | 0.96803 | 0.98202 | 0.92821 | 0.87583 | 0.82042 | 0.98202 | 27 | Slope | 0.13333 | 0.63693 | 0.6144 | 0.58233 | 0.55182 | 0.52239 | 0.4939 | 0.4662 | 0.44132 | 0.41952 | 0.39933 | 0.38144 | 0.35631 | 0.33942 | 0.33184 | 0.33379 | 0.34307 | 0.35428 | 0.36541 | 0.37388 | 0.37795 | 0.3778 | 0.37585 | 0.37378 | 0.3713 | 0.37045 | 0.3733 | 0.37823 | 0.37179 | 0.34274 | 0.31417 | 0.28458 | 0.63693 | 0 | 0.91078 | Slope | 1 | 0.0057287 |  | 0.97164 | 0 | 0.91078 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00028811 | 0.00012186 | 0.0023973
169 | 0:28 | 0.57287 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 0.039203 | 0.00039203 | 0.00039203 | 0.57287 | 0.00026683 | [13 empty] | 0.97608 | 1 | 0.97746 | 0.91778 | 0.83072 | 0.72187 | 0.59956 | 0.47374 | 0.34928 | 0.23253 | 0.16186 | 0.10159 | 0.04521 | -0.010941 | -0.070842 | -0.1237 | -0.16429 | -0.17855 | -0.15825 | -0.095645 | -0.019741 | 0.047917 | 0.085318 | 0.069044 | 0.0021166 | -0.10007 | -0.19917 | -0.2907 | -0.37393 | -0.45417 | -0.52979 | 1.9602e-05 | 0.0021976 | 0.00010988 | 0.00010988 | 0 | 0 | 0.0024522 | 0.05 | 0.15689 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.84322 | 0.78035 | 0.72216 | 0.66719 | 0.61507 | 0.56528 | 0.524 | 0.49194 | 0.46468 | 0.44436 | 0.4023 | 0.38497 | 0.39555 | 0.43475 | 0.49592 | 0.56288 | 0.62958 | 0.68835 | 0.73387 | 0.76675 | 0.79426 | 0.82138 | 0.84728 | 0.87804 | 0.91993 | 0.96806 | 0.98199 | 0.92818 | 0.8758 | 0.82039 | 0.76744 | 0.98199 | 26 | Slope | 0.16667 | 0.61441 | 0.59345 | 0.56294 | 0.53351 | 0.50502 | 0.47732 | 0.45245 | 0.43065 | 0.41045 | 0.39257 | 0.36743 | 0.35055 | 0.34296 | 0.34492 | 0.35419 | 0.3654 | 0.37653 | 0.38501 | 0.38907 | 0.38892 | 0.38697 | 0.3849 | 0.38243 | 0.38157 | 0.38442 | 0.38935 | 0.38289 | 0.35384 | 0.32527 | 0.29568 | 0.26693 | 0.61441 | 0 | 0.84322 | Slope | 1 | 0.00039203 |  | 0.99806 | 0.30139 | 0.84322 | Slope | 2 | 1 | 0.30139 | 20 | -20 | 0.00026683 | 0.00013133 | 0.0024522
170 | 0:28 | 0.039203 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -0.23417 | -0.0023417 | -0.0023417 | 0.039203 | 0.00013669 | [13 empty] | 0.97746 | 1 | 0.97856 | 0.92167 | 0.83836 | 0.73636 | 0.62247 | 0.5024 | 0.38442 | 0.30172 | 0.22973 | 0.16253 | 0.095847 | 0.025892 | -0.031254 | -0.073798 | -0.092207 | -0.08586 | -0.043616 | 0.027261 | 0.10026 | 0.13311 | 0.1172 | 0.049887 | -0.058056 | -0.1799 | -0.28281 | -0.36411 | -0.43598 | -0.50593 | -0.57351 | -0.00011708 | 0.0027795 | 0.00013898 | 0.00013898 | 0 | 0 | 0.0025103 | 0.05 | 0.21976 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.78038 | 0.72219 | 0.66722 | 0.6151 | 0.56531 | 0.52403 | 0.49197 | 0.46471 | 0.44439 | 0.40233 | 0.385 | 0.39558 | 0.43478 | 0.49595 | 0.56291 | 0.62961 | 0.68838 | 0.7339 | 0.76678 | 0.79428 | 0.82141 | 0.84731 | 0.87807 | 0.91996 | 0.96809 | 0.98196 | 0.92815 | 0.87577 | 0.82036 | 0.76742 | 0.72051 | 0.98196 | 25 | Slope | 0.2 | 0.59346 | 0.57406 | 0.54463 | 0.51614 | 0.48844 | 0.46357 | 0.44177 | 0.42157 | 0.40369 | 0.37856 | 0.36167 | 0.35408 | 0.35604 | 0.36532 | 0.37652 | 0.38765 | 0.39613 | 0.40019 | 0.40004 | 0.39809 | 0.39603 | 0.39355 | 0.39269 | 0.39554 | 0.40047 | 0.39399 | 0.36494 | 0.33637 | 0.30679 | 0.27803 | 0.25128 | 0.59346 | 0 | 0.78038 | Slope | 1 | 0.0023417 |  | 0.98841 | 0 | 0.78038 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00013669 | 0.00014136 | 0.0025103
171 | 0:28 | -0.23417 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -0.433 | -0.00433 | -0.00433 | -0.23417 | 9.9414e-05 | [13 empty] | 0.97856 | 1 | 0.97954 | 0.92507 | 0.84688 | 0.75201 | 0.64346 | 0.52972 | 0.43915 | 0.35926 | 0.28389 | 0.20917 | 0.13037 | 0.063727 | 0.017636 | -0.002237 | -0.001526 | 0.023388 | 0.071564 | 0.13988 | 0.18013 | 0.16135 | 0.095049 | -0.013849 | -0.14108 | -0.26279 | -0.35282 | -0.42292 | -0.48551 | -0.54789 | -0.60987 | -0.0002165 | 0.0033292 | 0.00016646 | 0.00016646 | 0 | 0 | 0.002568 | 0.05 | 0.27795 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.72222 | 0.66725 | 0.61513 | 0.56534 | 0.52406 | 0.49199 | 0.46473 | 0.44442 | 0.40236 | 0.38503 | 0.39561 | 0.4348 | 0.49597 | 0.56293 | 0.62964 | 0.68841 | 0.73392 | 0.76681 | 0.79431 | 0.82144 | 0.84734 | 0.8781 | 0.91999 | 0.96812 | 0.98193 | 0.92812 | 0.87574 | 0.82033 | 0.76739 | 0.72049 | 0.67836 | 0.98193 | 24 | Slope | 0.23333 | 0.57407 | 0.55575 | 0.52726 | 0.49956 | 0.47469 | 0.45289 | 0.43269 | 0.41481 | 0.38968 | 0.37279 | 0.3652 | 0.36716 | 0.37644 | 0.38764 | 0.39877 | 0.40725 | 0.41131 | 0.41116 | 0.40922 | 0.40715 | 0.40467 | 0.40381 | 0.40666 | 0.41159 | 0.40509 | 0.37604 | 0.34747 | 0.31789 | 0.28913 | 0.26238 | 0.23723 | 0.57407 | 0 | 0.72222 | Slope | 1 | 0.00433 |  | 0.97857 | 0 | 0.72222 | Slope | 2 | 1 | 0 | 20 | -20 | 9.9414e-05 | 0.00015128 | 0.002568
172 | 0:28 | -0.433 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -0.53822 | -0.0053822 | -0.0053822 | -0.433 | 5.2611e-05 | [13 empty] | 0.97954 | 1 | 0.98039 | 0.9293 | 0.8569 | 0.76667 | 0.66407 | 0.57121 | 0.48736 | 0.40765 | 0.32778 | 0.24286 | 0.16826 | 0.11343 | 0.090691 | 0.088883 | 0.10558 | 0.13423 | 0.17848 | 0.21513 | 0.20598 | 0.13731 | 0.02874 | -0.099899 | -0.22626 | -0.33138 | -0.40887 | -0.46997 | -0.52578 | -0.58293 | -0.6406 | -0.00026911 | 0.0038504 | 0.00019252 | 0.00019252 | 0 | 0 | 0.0026242 | 0.05 | 0.33292 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.66727 | 0.61515 | 0.56537 | 0.52409 | 0.49202 | 0.46476 | 0.44444 | 0.40239 | 0.38505 | 0.39563 | 0.43483 | 0.496 | 0.56296 | 0.62967 | 0.68843 | 0.73395 | 0.76683 | 0.79434 | 0.82146 | 0.84736 | 0.87813 | 0.92001 | 0.96814 | 0.98191 | 0.9281 | 0.87572 | 0.8203 | 0.76736 | 0.72046 | 0.67833 | 0.64139 | 0.98191 | 23 | Slope | 0.26667 | 0.55576 | 0.53838 | 0.51068 | 0.48581 | 0.46401 | 0.44381 | 0.42593 | 0.4008 | 0.38391 | 0.37632 | 0.37828 | 0.38756 | 0.39876 | 0.40989 | 0.41837 | 0.42243 | 0.42228 | 0.42033 | 0.41827 | 0.41579 | 0.41493 | 0.41778 | 0.42271 | 0.41619 | 0.38714 | 0.35857 | 0.32899 | 0.30023 | 0.27349 | 0.24833 | 0.22491 | 0.55576 | 0 | 0.66727 | Slope | 1 | 0.0053822 |  | 0.97336 | 0 | 0.66727 | Slope | 2 | 1 | 0 | 20 | -20 | 5.2611e-05 | 0.00016049 | 0.0026242
173 | 0:29 | -0.53822 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -1.5938 | -0.015938 | -0.015938 | -0.53822 | 0.00052779 | [13 empty] | 0.98039 | 1 | 0.982 | 0.93536 | 0.86679 | 0.78192 | 0.69394 | 0.61137 | 0.53123 | 0.45024 | 0.36236 | 0.28295 | 0.22151 | 0.1908 | 0.18508 | 0.19697 | 0.21598 | 0.23966 | 0.25095 | 0.23954 | 0.18138 | 0.069561 | -0.05967 | -0.18768 | -0.29605 | -0.38636 | -0.45391 | -0.50848 | -0.55964 | -0.61282 | -0.66653 | -0.0007969 | 0.0043483 | 0.00021741 | 0.00021741 | 0 | 0 | 0.0026782 | 0.05 | 0.38504 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.61518 | 0.56539 | 0.52411 | 0.49204 | 0.46479 | 0.44447 | 0.40241 | 0.38508 | 0.39566 | 0.43485 | 0.49602 | 0.56299 | 0.62969 | 0.68846 | 0.73397 | 0.76686 | 0.79436 | 0.82149 | 0.84739 | 0.87815 | 0.92004 | 0.96817 | 0.98188 | 0.92807 | 0.87569 | 0.82028 | 0.76734 | 0.72044 | 0.6783 | 0.64137 | 0.61217 | 0.98188 | 22 | Slope | 0.3 | 0.53839 | 0.5218 | 0.49693 | 0.47513 | 0.45493 | 0.43705 | 0.41192 | 0.39503 | 0.38744 | 0.3894 | 0.39867 | 0.40988 | 0.42101 | 0.42949 | 0.43355 | 0.4334 | 0.43145 | 0.42938 | 0.42691 | 0.42605 | 0.4289 | 0.43383 | 0.42729 | 0.39825 | 0.36967 | 0.34009 | 0.31133 | 0.28459 | 0.25943 | 0.23601 | 0.21517 | 0.53839 | 0 | 0.61518 | Slope | 1 | 0.015938 |  | 0.92111 | 0 | 0.61518 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00052779 | 0.00016855 | 0.0026782
174 | 0:29 | -1.5938 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.6921 | -0.026921 | -0.026921 | -1.5938 | 0.00054915 | [13 empty] | 0.982 | 1 | 0.98354 | 0.93928 | 0.87453 | 0.79719 | 0.72071 | 0.64332 | 0.56306 | 0.47487 | 0.39229 | 0.32553 | 0.28665 | 0.27025 | 0.27558 | 0.28892 | 0.30317 | 0.29573 | 0.26179 | 0.20292 | 0.10323 | -0.025879 | -0.15141 | -0.25835 | -0.35067 | -0.42867 | -0.48864 | -0.53835 | -0.58561 | -0.63478 | -0.68516 | -0.0013461 | 0.0047611 | 0.00023805 | 0.00023805 | 0 | 0 | 0.0027329 | 0.05 | 0.43483 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.56541 | 0.52413 | 0.49206 | 0.46481 | 0.44449 | 0.40243 | 0.3851 | 0.39568 | 0.43488 | 0.49604 | 0.56301 | 0.62971 | 0.68848 | 0.73399 | 0.76688 | 0.79438 | 0.82151 | 0.84741 | 0.87817 | 0.92006 | 0.96819 | 0.98186 | 0.92805 | 0.87567 | 0.82026 | 0.76732 | 0.72041 | 0.67828 | 0.64135 | 0.61215 | 0.5892 | 0.98186 | 21 | Slope | 0.33333 | 0.5218 | 0.50804 | 0.48624 | 0.46605 | 0.44816 | 0.42303 | 0.40614 | 0.39856 | 0.40051 | 0.40979 | 0.421 | 0.43213 | 0.4406 | 0.44466 | 0.44452 | 0.44257 | 0.4405 | 0.43802 | 0.43717 | 0.44002 | 0.44495 | 0.4384 | 0.40935 | 0.38078 | 0.3512 | 0.32244 | 0.29569 | 0.27054 | 0.24712 | 0.22627 | 0.20751 | 0.5218 | 0 | 0.56541 | Slope | 1 | 0.026921 |  | 0.86674 | 0 | 0.56541 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00054915 | 0.00017513 | 0.0027329
175 | 0:29 | -2.6921 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -3.039 | -0.03039 | -0.03039 | -2.6921 | 0.00017345 | [13 empty] | 0.98354 | 1 | 0.9842 | 0.94196 | 0.87808 | 0.81247 | 0.74195 | 0.66515 | 0.57821 | 0.49485 | 0.42411 | 0.37807 | 0.35062 | 0.34191 | 0.34774 | 0.35691 | 0.34311 | 0.29366 | 0.21328 | 0.11581 | 0.001818 | -0.12042 | -0.22261 | -0.31308 | -0.39206 | -0.46091 | -0.51531 | -0.56101 | -0.60441 | -0.65025 | -0.69789 | -0.0015195 | 0.0050817 | 0.00025409 | 0.00025409 | 0 | 0 | 0.0027831 | 0.05 | 0.47611 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.52415 | 0.49208 | 0.46482 | 0.44451 | 0.40245 | 0.38511 | 0.39569 | 0.43489 | 0.49606 | 0.56302 | 0.62973 | 0.6885 | 0.73401 | 0.76689 | 0.7944 | 0.82152 | 0.84742 | 0.87819 | 0.92007 | 0.9682 | 0.98185 | 0.92803 | 0.87565 | 0.82024 | 0.7673 | 0.7204 | 0.67827 | 0.64133 | 0.61213 | 0.58918 | 0.57132 | 0.98185 | 20 | Slope | 0.36667 | 0.50805 | 0.49736 | 0.47716 | 0.45928 | 0.43415 | 0.41726 | 0.40968 | 0.41163 | 0.42091 | 0.43212 | 0.44324 | 0.45172 | 0.45578 | 0.45563 | 0.45369 | 0.45162 | 0.44914 | 0.44829 | 0.45114 | 0.45607 | 0.4495 | 0.42046 | 0.39188 | 0.3623 | 0.33354 | 0.3068 | 0.28164 | 0.25822 | 0.23738 | 0.21862 | 0.20155 | 0.50805 | 0 | 0.52415 | Slope | 1 | 0.03039 |  | 0.84957 | 0 | 0.52415 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00017345 | 0.00017991 | 0.0027831
176 | 0:29 | -3.039 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -3.6942 | -0.036942 | -0.036942 | -3.039 | 0.00032761 | [13 empty] | 0.9842 | 1 | 0.98497 | 0.93864 | 0.88737 | 0.82936 | 0.7614 | 0.67954 | 0.59826 | 0.52771 | 0.47802 | 0.4414 | 0.41828 | 0.40813 | 0.40992 | 0.39213 | 0.33792 | 0.24238 | 0.12482 | 0.014836 | -0.093042 | -0.19146 | -0.27765 | -0.35457 | -0.42394 | -0.48642 | -0.5365 | -0.57851 | -0.61886 | -0.66213 | -0.70515 | -0.0018471 | 0.0053543 | 0.00026772 | 0.00026772 | 0 | 0 | 0.0028274 | 0.05 | 0.50817 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.49209 | 0.46484 | 0.44452 | 0.40246 | 0.38513 | 0.39571 | 0.43491 | 0.49607 | 0.56304 | 0.62974 | 0.68851 | 0.73402 | 0.76691 | 0.79441 | 0.82154 | 0.84744 | 0.8782 | 0.92009 | 0.96822 | 0.98183 | 0.92802 | 0.87564 | 0.82023 | 0.76729 | 0.72039 | 0.67825 | 0.64132 | 0.61212 | 0.58917 | 0.57131 | 0.56401 | 0.98183 | 19 | Slope | 0.4 | 0.49736 | 0.48828 | 0.4704 | 0.44527 | 0.42838 | 0.42079 | 0.42275 | 0.43202 | 0.44323 | 0.45436 | 0.46284 | 0.4669 | 0.46675 | 0.4648 | 0.46274 | 0.46026 | 0.4594 | 0.46225 | 0.46718 | 0.46061 | 0.43156 | 0.40299 | 0.37341 | 0.34465 | 0.31791 | 0.29275 | 0.26933 | 0.24848 | 0.22972 | 0.21266 | 0.19911 | 0.49736 | 0 | 0.49209 | Slope | 1 | 0.036942 |  | 0.81714 | 0 | 0.49209 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00032761 | 0.00018309 | 0.0028274
177 | 0:29 | -3.6942 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.7084 | -0.047084 | -0.047084 | -3.6942 | 0.00050709 | [13 empty] | 0.98497 | 1 | 0.97627 | 0.94214 | 0.899 | 0.84453 | 0.7726 | 0.69673 | 0.62863 | 0.57906 | 0.53686 | 0.5012 | 0.47459 | 0.45966 | 0.43633 | 0.38073 | 0.28099 | 0.1491 | 0.023115 | -0.078737 | -0.16344 | -0.24612 | -0.31884 | -0.38592 | -0.44864 | -0.50618 | -0.55232 | -0.59133 | -0.62926 | -0.66812 | -0.71287 | -0.0023542 | 0.0055575 | 0.00027787 | 0.00027787 | 0 | 0 | 0.0028631 | 0.05 | 0.53543 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.46485 | 0.44453 | 0.40247 | 0.38514 | 0.39572 | 0.43492 | 0.49608 | 0.56305 | 0.62975 | 0.68852 | 0.73403 | 0.76692 | 0.79442 | 0.82155 | 0.84745 | 0.87821 | 0.9201 | 0.96823 | 0.98182 | 0.92801 | 0.87563 | 0.82022 | 0.76728 | 0.72038 | 0.67824 | 0.64131 | 0.61211 | 0.58916 | 0.5713 | 0.564 | 0.55032 | 0.98182 | 18 | Slope | 0.43333 | 0.48828 | 0.48151 | 0.45638 | 0.43949 | 0.43191 | 0.43386 | 0.44314 | 0.45435 | 0.46547 | 0.47395 | 0.47801 | 0.47786 | 0.47592 | 0.47385 | 0.47137 | 0.47052 | 0.47337 | 0.4783 | 0.47172 | 0.44267 | 0.4141 | 0.38452 | 0.35576 | 0.32901 | 0.30386 | 0.28044 | 0.25959 | 0.24083 | 0.22377 | 0.21022 | 0.19455 | 0.48828 | 0 | 0.46485 | Slope | 1 | 0.047084 |  | 0.76693 | 0 | 0.46485 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00050709 | 0.00018474 | 0.0028631
178 | 0:29 | -4.7084 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -6.173 | -0.06173 | -0.06173 | -4.7084 | 0.0007323 | [13 empty] | 0.97627 | 1 | 0.97663 | 0.93899 | 0.8881 | 0.82017 | 0.75619 | 0.70086 | 0.66826 | 0.63848 | 0.60683 | 0.5687 | 0.53174 | 0.47634 | 0.39257 | 0.26613 | 0.11466 | -0.028942 | -0.14595 | -0.21704 | -0.28227 | -0.34159 | -0.39335 | -0.44557 | -0.49572 | -0.54007 | -0.57649 | -0.6081 | -0.63229 | -0.67793 | -0.72589 | -0.0030865 | 0.005978 | 0.0002989 | 0.0002989 | 0 | 0 | 0.0029941 | 0.05 | 0.55575 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.44455 | 0.40249 | 0.38516 | 0.39574 | 0.43494 | 0.49611 | 0.56307 | 0.62977 | 0.68854 | 0.73406 | 0.76694 | 0.79444 | 0.82157 | 0.84747 | 0.87823 | 0.92012 | 0.96825 | 0.9818 | 0.92799 | 0.87561 | 0.8202 | 0.76726 | 0.72035 | 0.67822 | 0.64129 | 0.61209 | 0.58914 | 0.57128 | 0.56398 | 0.5503 | 0.53173 | 0.9818 | 17 | Slope | 0.46667 | 0.48152 | 0.4675 | 0.45061 | 0.44302 | 0.44498 | 0.45426 | 0.46547 | 0.47659 | 0.48507 | 0.48913 | 0.48898 | 0.48704 | 0.48497 | 0.48249 | 0.48163 | 0.48448 | 0.48942 | 0.48282 | 0.45377 | 0.4252 | 0.39562 | 0.36686 | 0.34012 | 0.31496 | 0.29154 | 0.2707 | 0.25194 | 0.23487 | 0.22133 | 0.20566 | 0.18835 | 0.48942 | 16 | 0.96825 | Slope | 0.5 | 0.06173 |  | 0.69444 | 0 | 0.96825 | Slope | 2 | 0.5 | 0 | 20 | -20 | 0.0007323 | 0.00018474 | 0.0029941
179 | 0:30 | -6.173 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.6289 | -0.076289 | -0.076289 | -6.173 | 0.00072798 | [13 empty] | 0.97663 | 1 | 0.97528 | 0.93205 | 0.86977 | 0.80604 | 0.75668 | 0.72779 | 0.70855 | 0.68288 | 0.64712 | 0.6003 | 0.5319 | 0.42907 | 0.28496 | 0.11734 | -0.03438 | -0.15854 | -0.24358 | -0.30003 | -0.34962 | -0.39513 | -0.43722 | -0.48104 | -0.52238 | -0.55996 | -0.59119 | -0.61332 | -0.64243 | -0.68976 | -0.73369 | -0.0038145 | 0.0061514 | 0.00030757 | 0.00030757 | 0 | 0 | 0.0030459 | 0.05 | 0.5978 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.4025 | 0.38517 | 0.39575 | 0.43495 | 0.49611 | 0.56308 | 0.62978 | 0.68855 | 0.73406 | 0.76695 | 0.79445 | 0.82158 | 0.84748 | 0.87824 | 0.92013 | 0.96826 | 0.98179 | 0.92798 | 0.8756 | 0.82019 | 0.76725 | 0.72035 | 0.67821 | 0.64128 | 0.61208 | 0.58913 | 0.57127 | 0.56397 | 0.55029 | 0.53172 | 0.51792 | 0.98179 | 16 | Slope | 0.5 | 0.4675 | 0.46172 | 0.45414 | 0.45609 | 0.46537 | 0.47658 | 0.4877 | 0.49618 | 0.50024 | 0.50009 | 0.49815 | 0.49608 | 0.4936 | 0.49275 | 0.4956 | 0.50053 | 0.49393 | 0.46488 | 0.43631 | 0.40673 | 0.37797 | 0.35123 | 0.32607 | 0.30265 | 0.2818 | 0.26304 | 0.24598 | 0.23243 | 0.21676 | 0.19946 | 0.18375 | 0.50053 | 15 | 0.96826 | Slope | 0.53333 | 0.076289 |  | 0.62237 | 0 | 0.96826 | Slope | 2 | 0.53333 | 0 | 20 | -20 | 0.00072798 | 0.0001815 | 0.0030459
180 | 0:30 | -7.6289 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -9.0693 | -0.090693 | -0.090693 | -7.6289 | 0.00072019 | [13 empty] | 0.97528 | 1 | 0.97276 | 0.92117 | 0.85956 | 0.80344 | 0.7699 | 0.74603 | 0.72466 | 0.69389 | 0.65249 | 0.58505 | 0.48385 | 0.33121 | 0.1547 | -0.0039564 | -0.12855 | -0.22071 | -0.29191 | -0.33868 | -0.38077 | -0.42074 | -0.45827 | -0.49758 | -0.53524 | -0.56983 | -0.59599 | -0.61993 | -0.64896 | -0.69429 | -0.72665 | -0.0045347 | 0.0060456 | 0.00030228 | 0.00030228 | 0 | 0 | 0.0030161 | 0.05 | 0.61514 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.38516 | 0.39574 | 0.43494 | 0.49611 | 0.56307 | 0.62978 | 0.68854 | 0.73406 | 0.76694 | 0.79445 | 0.82157 | 0.84747 | 0.87824 | 0.92012 | 0.96825 | 0.9818 | 0.92799 | 0.87561 | 0.82019 | 0.76725 | 0.72035 | 0.67822 | 0.64128 | 0.61208 | 0.58914 | 0.57128 | 0.56397 | 0.5503 | 0.53172 | 0.51792 | 0.54364 | 0.9818 | 15 | Slope | 0.53333 | 0.46172 | 0.46525 | 0.4672 | 0.47648 | 0.48769 | 0.49881 | 0.50729 | 0.51135 | 0.5112 | 0.50926 | 0.50719 | 0.50471 | 0.50386 | 0.50671 | 0.51164 | 0.50504 | 0.476 | 0.44742 | 0.41784 | 0.38908 | 0.36234 | 0.33718 | 0.31376 | 0.29292 | 0.27416 | 0.25709 | 0.24355 | 0.22788 | 0.21057 | 0.19486 | 0.19232 | 0.51164 | 14 | 0.96825 | Slope | 0.56667 | 0.090693 |  | 0.55107 | 0 | 0.96825 | Slope | 2 | 0.56667 | 0 | 20 | -20 | 0.00072019 | 0.00017561 | 0.0030161
181 | 0:30 | -9.0693 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -9.7669 | -0.097669 | -0.097669 | -9.0693 | 0.00034877 | [13 empty] | 0.97276 | 1 | 0.96842 | 0.91446 | 0.85322 | 0.79959 | 0.76086 | 0.72667 | 0.69958 | 0.66684 | 0.61927 | 0.53624 | 0.39718 | 0.21987 | 0.059721 | -0.065151 | -0.15785 | -0.2377 | -0.30218 | -0.34652 | -0.38659 | -0.42512 | -0.46205 | -0.50059 | -0.53747 | -0.57151 | -0.5962 | -0.61742 | -0.64608 | -0.6681 | -0.70507 | -0.0048834 | 0.0056536 | 0.00028268 | 0.00028268 | 0 | 0 | 0.0029108 | 0.05 | 0.60456 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.39572 | 0.43492 | 0.49609 | 0.56305 | 0.62976 | 0.68852 | 0.73404 | 0.76692 | 0.79443 | 0.82155 | 0.84745 | 0.87822 | 0.9201 | 0.96823 | 0.98182 | 0.92801 | 0.87563 | 0.82021 | 0.76727 | 0.72037 | 0.67824 | 0.6413 | 0.6121 | 0.58916 | 0.57129 | 0.56399 | 0.55032 | 0.53174 | 0.51794 | 0.54366 | 0.56376 | 0.98182 | 14 | Slope | 0.56667 | 0.46524 | 0.47831 | 0.48759 | 0.49879 | 0.50992 | 0.5184 | 0.52246 | 0.52231 | 0.52036 | 0.5183 | 0.51582 | 0.51496 | 0.51781 | 0.52274 | 0.51616 | 0.48711 | 0.45854 | 0.42896 | 0.4002 | 0.37346 | 0.3483 | 0.32488 | 0.30403 | 0.28527 | 0.26821 | 0.25466 | 0.239 | 0.22169 | 0.20598 | 0.20344 | 0.19903 | 0.52274 | 13 | 0.96823 | Slope | 0.6 | 0.097669 |  | 0.51654 | 0 | 0.96823 | Slope | 2 | 0.6 | 0 | 20 | -20 | 0.00034877 | 0.00016805 | 0.0029108
182 | 0:30 | -9.7669 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -10.3243 | -0.10324 | -0.10324 | -9.7669 | 0.00027872 | [13 empty] | 0.96842 | 1 | 0.96566 | 0.90734 | 0.83731 | 0.76596 | 0.70728 | 0.66414 | 0.63853 | 0.61447 | 0.57065 | 0.46379 | 0.30768 | 0.15121 | 0.028772 | -0.063991 | -0.14583 | -0.22126 | -0.28628 | -0.33125 | -0.37238 | -0.41353 | -0.45212 | -0.49179 | -0.53228 | -0.5621 | -0.58156 | -0.60348 | -0.59822 | -0.62711 | -0.67213 | -0.0051622 | 0.0050419 | 0.0002521 | 0.0002521 | 0 | 0 | 0.0027592 | 0.05 | 0.56536 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.43489 | 0.49606 | 0.56302 | 0.62973 | 0.68849 | 0.73401 | 0.76689 | 0.7944 | 0.82152 | 0.84742 | 0.87819 | 0.92007 | 0.9682 | 0.98185 | 0.92804 | 0.87566 | 0.82024 | 0.7673 | 0.7204 | 0.67827 | 0.64133 | 0.61213 | 0.58919 | 0.57133 | 0.56402 | 0.55035 | 0.53177 | 0.51797 | 0.54369 | 0.56379 | 0.56747 | 0.98185 | 13 | Slope | 0.6 | 0.4783 | 0.49869 | 0.5099 | 0.52102 | 0.5295 | 0.53356 | 0.53341 | 0.53147 | 0.5294 | 0.52692 | 0.52606 | 0.52891 | 0.53385 | 0.52728 | 0.49823 | 0.46966 | 0.44008 | 0.41132 | 0.38458 | 0.35942 | 0.336 | 0.31516 | 0.2964 | 0.27933 | 0.26579 | 0.25012 | 0.23281 | 0.2171 | 0.21456 | 0.21015 | 0.20027 | 0.53385 | 12 | 0.9682 | Slope | 0.63333 | 0.10324 |  | 0.48895 | 0 | 0.9682 | Slope | 2 | 0.63333 | 0 | 20 | -20 | 0.00027872 | 0.00015997 | 0.0027592
183 | 0:30 | -10.3243 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -10.7974 | -0.10797 | -0.10797 | -10.3243 | 0.00023653 | [13 empty] | 0.96566 | 1 | 0.96099 | 0.89042 | 0.79614 | 0.69614 | 0.62322 | 0.57799 | 0.56849 | 0.55662 | 0.49267 | 0.36845 | 0.23127 | 0.11103 | 0.023131 | -0.058565 | -0.13425 | -0.20839 | -0.2734 | -0.31907 | -0.36246 | -0.40528 | -0.44501 | -0.48829 | -0.52544 | -0.55052 | -0.57031 | -0.54503 | -0.54654 | -0.58867 | -0.6533 | -0.0053987 | 0.0043723 | 0.00021862 | 0.00021862 | 0 | 0 | 0.0025675 | 0.05 | 0.50419 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.49603 | 0.56299 | 0.62969 | 0.68846 | 0.73398 | 0.76686 | 0.79436 | 0.82149 | 0.84739 | 0.87815 | 0.92004 | 0.96817 | 0.98188 | 0.92807 | 0.87569 | 0.82028 | 0.76734 | 0.72043 | 0.6783 | 0.64137 | 0.61217 | 0.58922 | 0.57136 | 0.56406 | 0.55038 | 0.53181 | 0.51801 | 0.54373 | 0.56382 | 0.56751 | 0.55464 | 0.98188 | 12 | Slope | 0.63333 | 0.49868 | 0.521 | 0.53212 | 0.5406 | 0.54466 | 0.54451 | 0.54257 | 0.5405 | 0.53802 | 0.53716 | 0.54001 | 0.54495 | 0.53841 | 0.50936 | 0.48079 | 0.4512 | 0.42245 | 0.3957 | 0.37055 | 0.34712 | 0.32628 | 0.30752 | 0.29045 | 0.27691 | 0.26124 | 0.24394 | 0.22822 | 0.22569 | 0.22127 | 0.21139 | 0.19599 | 0.54495 | 11 | 0.96817 | Slope | 0.66667 | 0.10797 |  | 0.46553 | 0 | 0.96817 | Slope | 2 | 0.66667 | 0 | 20 | -20 | 0.00023653 | 0.0001523 | 0.0025675
184 | 0:30 | -10.7974 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -10.9428 | -0.10943 | -0.10943 | -10.7974 | 7.2721e-05 | [13 empty] | 0.96099 | 1 | 0.95053 | 0.85416 | 0.72458 | 0.59944 | 0.51506 | 0.48533 | 0.49167 | 0.45858 | 0.37749 | 0.27127 | 0.16765 | 0.085386 | 0.0087246 | -0.063934 | -0.13508 | -0.20789 | -0.27307 | -0.31941 | -0.36355 | -0.40723 | -0.44872 | -0.49134 | -0.52606 | -0.55101 | -0.50701 | -0.48822 | -0.50779 | -0.57841 | -0.67617 | -0.0054714 | 0.0037053 | 0.00018526 | 0.00018526 | 0 | 0 | 0.0023272 | 0.05 | 0.43723 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.56295 | 0.62966 | 0.68843 | 0.73394 | 0.76683 | 0.79433 | 0.82146 | 0.84735 | 0.87812 | 0.92001 | 0.96814 | 0.98192 | 0.9281 | 0.87572 | 0.82031 | 0.76737 | 0.72047 | 0.67834 | 0.6414 | 0.6122 | 0.58925 | 0.57139 | 0.56409 | 0.55042 | 0.53184 | 0.51804 | 0.54376 | 0.56386 | 0.56754 | 0.55467 | 0.53306 | 0.98192 | 11 | Slope | 0.66667 | 0.52098 | 0.54322 | 0.5517 | 0.55576 | 0.55561 | 0.55367 | 0.5516 | 0.54912 | 0.54826 | 0.55111 | 0.55605 | 0.54953 | 0.52048 | 0.49191 | 0.46233 | 0.43357 | 0.40682 | 0.38167 | 0.35824 | 0.3374 | 0.31864 | 0.30158 | 0.28803 | 0.27236 | 0.25506 | 0.23935 | 0.23681 | 0.2324 | 0.22251 | 0.20711 | 0.1888 | 0.55605 | 10 | 0.96814 | Slope | 0.7 | 0.10943 |  | 0.45833 | 0 | 0.96814 | Slope | 2 | 0.7 | 0 | 20 | -20 | 7.2721e-05 | 0.00014523 | 0.0023272
185 | 0:31 | -10.9428 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -9.5312 | -0.095312 | -0.095312 | -10.9428 | 0.00070583 | [13 empty] | 0.95053 | 1 | 0.93293 | 0.80182 | 0.63623 | 0.47973 | 0.39841 | 0.37347 | 0.34853 | 0.29693 | 0.23634 | 0.16208 | 0.10113 | 0.031045 | -0.031757 | -0.094071 | -0.16057 | -0.23149 | -0.2952 | -0.34006 | -0.38358 | -0.42495 | -0.47047 | -0.51511 | -0.54909 | -0.49084 | -0.45197 | -0.45783 | -0.51443 | -0.62586 | -0.72536 | -0.0047656 | 0.0031176 | 0.00015588 | 0.00015588 | 0 | 0 | 0.0020456 | 0.05 | 0.37053 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.62963 | 0.6884 | 0.73391 | 0.7668 | 0.7943 | 0.82143 | 0.84733 | 0.87809 | 0.91998 | 0.96811 | 0.98194 | 0.92813 | 0.87575 | 0.82034 | 0.7674 | 0.7205 | 0.67837 | 0.64143 | 0.61223 | 0.58928 | 0.57142 | 0.56412 | 0.55045 | 0.53187 | 0.51807 | 0.54379 | 0.56389 | 0.56757 | 0.5547 | 0.53309 | 0.51782 | 0.98194 | 10 | Slope | 0.7 | 0.54321 | 0.5628 | 0.56686 | 0.56671 | 0.56477 | 0.5627 | 0.56022 | 0.55936 | 0.56221 | 0.56715 | 0.56065 | 0.5316 | 0.50303 | 0.47345 | 0.44469 | 0.41794 | 0.39279 | 0.36937 | 0.34852 | 0.32976 | 0.3127 | 0.29915 | 0.28348 | 0.26618 | 0.25047 | 0.24793 | 0.24352 | 0.23363 | 0.21823 | 0.19992 | 0.18372 | 0.56715 | 9 | 0.96811 | Slope | 0.73333 | 0.095312 |  | 0.52821 | 0 | 0.96811 | Slope | 2 | 0.73333 | 0 | 20 | -20 | 0.00070583 | 0.00013855 | 0.0020456
186 | 0:31 | -9.5312 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.7611 | -0.077611 | -0.077611 | -9.5312 | 0.00088502 | [13 empty] | 0.93293 | 1 | 0.91106 | 0.74333 | 0.532 | 0.35234 | 0.25366 | 0.18005 | 0.137 | 0.11188 | 0.084767 | 0.056239 | 0.0092096 | -0.042288 | -0.088709 | -0.14193 | -0.20254 | -0.26823 | -0.32938 | -0.37154 | -0.40798 | -0.45702 | -0.50778 | -0.55114 | -0.49466 | -0.43961 | -0.4276 | -0.47393 | -0.5709 | -0.68368 | -0.76502 | -0.0038806 | 0.0026624 | 0.00013312 | 0.00013312 | 0 | 0 | 0.001792 | 0.05 | 0.31176 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.68837 | 0.73389 | 0.76677 | 0.79428 | 0.8214 | 0.8473 | 0.87807 | 0.91995 | 0.96808 | 0.98197 | 0.92816 | 0.87577 | 0.82036 | 0.76742 | 0.72052 | 0.67839 | 0.64145 | 0.61225 | 0.58931 | 0.57144 | 0.56414 | 0.55047 | 0.53189 | 0.51809 | 0.54381 | 0.56391 | 0.56759 | 0.55472 | 0.53311 | 0.51784 | 0.52043 | 0.98197 | 9 | Slope | 0.73333 | 0.56279 | 0.57796 | 0.57781 | 0.57587 | 0.5738 | 0.57132 | 0.57047 | 0.57332 | 0.57825 | 0.57177 | 0.54272 | 0.51415 | 0.48457 | 0.45581 | 0.42906 | 0.40391 | 0.38048 | 0.35964 | 0.34088 | 0.32381 | 0.31027 | 0.2946 | 0.2773 | 0.26159 | 0.25905 | 0.25464 | 0.24475 | 0.22935 | 0.21104 | 0.19484 | 0.18459 | 0.57825 | 8 | 0.96808 | Slope | 0.76667 | 0.077611 |  | 0.61582 | 0 | 0.96808 | Slope | 2 | 0.76667 | 0 | 20 | -20 | 0.00088502 | 0.00013173 | 0.001792
187 | 0:31 | -7.7611 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -6.0284 | -0.060284 | -0.060284 | -7.7611 | 0.00086638 | [13 empty] | 0.91106 | 1 | 0.88786 | 0.6745 | 0.41799 | 0.18791 | 0.016955 | -0.079478 | -0.088234 | -0.075947 | -0.056956 | -0.070526 | -0.095348 | -0.12555 | -0.15836 | -0.20113 | -0.25101 | -0.3108 | -0.36848 | -0.39873 | -0.44491 | -0.50152 | -0.54957 | -0.5007 | -0.44838 | -0.42125 | -0.44982 | -0.53366 | -0.62715 | -0.71753 | -0.75662 | -0.0030142 | 0.0023336 | 0.00011668 | 0.00011668 | 0 | 0 | 0.0015906 | 0.05 | 0.26624 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.73387 | 0.76676 | 0.79426 | 0.82139 | 0.84729 | 0.87805 | 0.91994 | 0.96807 | 0.98198 | 0.92817 | 0.87579 | 0.82038 | 0.76744 | 0.72054 | 0.67841 | 0.64147 | 0.61227 | 0.58932 | 0.57146 | 0.56416 | 0.55049 | 0.53191 | 0.51811 | 0.54383 | 0.56392 | 0.56761 | 0.55474 | 0.53313 | 0.51786 | 0.52045 | 0.5499 | 0.98198 | 8 | Slope | 0.76667 | 0.57796 | 0.58892 | 0.58698 | 0.58491 | 0.58243 | 0.58157 | 0.58442 | 0.58936 | 0.58288 | 0.55383 | 0.52526 | 0.49568 | 0.46692 | 0.44018 | 0.41502 | 0.3916 | 0.37076 | 0.352 | 0.33493 | 0.32139 | 0.30572 | 0.28841 | 0.2727 | 0.27016 | 0.26575 | 0.25587 | 0.24047 | 0.22215 | 0.20595 | 0.19571 | 0.19441 | 0.58936 | 7 | 0.96807 | Slope | 0.8 | 0.060284 |  | 0.7016 | 0 | 0.96807 | Slope | 2 | 0.8 | 0 | 20 | -20 | 0.00086638 | 0.00012431 | 0.0015906
188 | 0:31 | -6.0284 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.498 | -0.04498 | -0.04498 | -6.0284 | 0.00076517 | [13 empty] | 0.88786 | 1 | 0.85816 | 0.59425 | 0.26666 | -0.059877 | -0.25839 | -0.31115 | -0.27391 | -0.21916 | -0.18736 | -0.18065 | -0.18448 | -0.20039 | -0.22114 | -0.25107 | -0.2928 | -0.34826 | -0.3948 | -0.43438 | -0.48798 | -0.54193 | -0.49944 | -0.45599 | -0.43198 | -0.4433 | -0.5065 | -0.58462 | -0.65191 | -0.69929 | -0.69735 | -0.002249 | 0.0020585 | 0.00010293 | 0.00010293 | 0 | 0 | 0.0014216 | 0.05 | 0.23336 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.76674 | 0.79425 | 0.82137 | 0.84727 | 0.87804 | 0.91992 | 0.96805 | 0.982 | 0.92819 | 0.8758 | 0.82039 | 0.76745 | 0.72055 | 0.67842 | 0.64148 | 0.61228 | 0.58934 | 0.57147 | 0.56417 | 0.5505 | 0.53192 | 0.51812 | 0.54384 | 0.56394 | 0.56762 | 0.55475 | 0.53314 | 0.51787 | 0.52046 | 0.54991 | 0.60268 | 0.982 | 7 | Slope | 0.8 | 0.58891 | 0.59808 | 0.59601 | 0.59354 | 0.59268 | 0.59553 | 0.60046 | 0.594 | 0.56495 | 0.53638 | 0.5068 | 0.47804 | 0.45129 | 0.42614 | 0.40272 | 0.38187 | 0.36311 | 0.34605 | 0.3325 | 0.31683 | 0.29953 | 0.28382 | 0.28128 | 0.27687 | 0.26699 | 0.25158 | 0.23327 | 0.21707 | 0.20682 | 0.20553 | 0.212 | 0.60046 | 6 | 0.96805 | Slope | 0.83333 | 0.04498 |  | 0.77735 | 0 | 0.96805 | Slope | 2 | 0.83333 | 0 | 20 | -20 | 0.00076517 | 0.00011613 | 0.0014216
189 | 0:31 | -4.498 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.1118 | -0.021118 | -0.021118 | -4.498 | 0.0011931 | [13 empty] | 0.85816 | 1 | 0.82304 | 0.4852 | 0.044425 | -0.32559 | -0.47507 | -0.47035 | -0.39515 | -0.33072 | -0.28414 | -0.26061 | -0.25157 | -0.25648 | -0.26501 | -0.28654 | -0.3233 | -0.36961 | -0.42601 | -0.47132 | -0.52298 | -0.48936 | -0.45298 | -0.4369 | -0.44991 | -0.49439 | -0.55087 | -0.60308 | -0.62586 | -0.63477 | -0.583 | -0.0010559 | 0.0017873 | 8.9365e-05 | 8.9365e-05 | 0 | 0 | 0.001264 | 0.05 | 0.20585 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.79423 | 0.82136 | 0.84726 | 0.87802 | 0.91991 | 0.96804 | 0.98201 | 0.9282 | 0.87582 | 0.82041 | 0.76746 | 0.72056 | 0.67843 | 0.6415 | 0.6123 | 0.58935 | 0.57149 | 0.56419 | 0.55051 | 0.53194 | 0.51814 | 0.54385 | 0.56395 | 0.56764 | 0.55477 | 0.53315 | 0.51788 | 0.52048 | 0.54993 | 0.60269 | 0.67678 | 0.98201 | 6 | Slope | 0.83333 | 0.59808 | 0.60712 | 0.60464 | 0.60379 | 0.60664 | 0.61157 | 0.60511 | 0.57607 | 0.5475 | 0.51791 | 0.48915 | 0.46241 | 0.43726 | 0.41383 | 0.39299 | 0.37423 | 0.35716 | 0.34362 | 0.32795 | 0.31065 | 0.29493 | 0.2924 | 0.28798 | 0.2781 | 0.2627 | 0.24438 | 0.22818 | 0.21794 | 0.21664 | 0.22312 | 0.2367 | 0.61157 | 5 | 0.96804 | Slope | 0.86667 | 0.021118 |  | 0.89547 | 0 | 0.96804 | Slope | 2 | 0.86667 | 0 | 20 | -20 | 0.0011931 | 0.00010765 | 0.001264
190 | 0:31 | -2.1118 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -0.40451 | -0.0040451 | -0.0040451 | -2.1118 | 0.00085362 | [13 empty] | 0.82304 | 1 | 0.78028 | 0.35091 | -0.13719 | -0.46215 | -0.54853 | -0.51684 | -0.43977 | -0.3733 | -0.32124 | -0.29111 | -0.27555 | -0.27373 | -0.27657 | -0.29417 | -0.32583 | -0.37635 | -0.43556 | -0.47991 | -0.46512 | -0.43724 | -0.41979 | -0.43151 | -0.47248 | -0.51122 | -0.54861 | -0.56875 | -0.56294 | -0.54099 | -0.44464 | -0.00020225 | 0.0015283 | 7.6415e-05 | 7.6415e-05 | 0 | 0 | 0.0011532 | 0.05 | 0.17873 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.82135 | 0.84725 | 0.87801 | 0.9199 | 0.96803 | 0.98202 | 0.92821 | 0.87583 | 0.82042 | 0.76748 | 0.72058 | 0.67845 | 0.64151 | 0.61231 | 0.58936 | 0.5715 | 0.5642 | 0.55053 | 0.53195 | 0.51815 | 0.54387 | 0.56396 | 0.56765 | 0.55478 | 0.53317 | 0.5179 | 0.52049 | 0.54994 | 0.60271 | 0.67679 | 0.76508 | 0.98202 | 5 | Slope | 0.86667 | 0.60712 | 0.61575 | 0.61489 | 0.61774 | 0.62268 | 0.61623 | 0.58718 | 0.55861 | 0.52903 | 0.50027 | 0.47353 | 0.44837 | 0.42495 | 0.4041 | 0.38534 | 0.36828 | 0.35473 | 0.33906 | 0.32176 | 0.30605 | 0.30351 | 0.2991 | 0.28922 | 0.27382 | 0.2555 | 0.2393 | 0.22905 | 0.22776 | 0.23424 | 0.24782 | 0.26614 | 0.62268 | 4 | 0.96803 | Slope | 0.9 | 0.0040451 |  | 0.97998 | 0 | 0.96803 | Slope | 2 | 0.9 | 0 | 20 | -20 | 0.00085362 | 9.988e-05 | 0.0011532
191 | 0:32 | -0.40451 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 0.095144 | 0.00095144 | 0.00095144 | -0.40451 | 0.00024983 | [13 empty] | 0.78028 | 1 | 0.73883 | 0.27401 | -0.1727 | -0.42502 | -0.48819 | -0.45933 | -0.39517 | -0.33884 | -0.28983 | -0.26087 | -0.2472 | -0.24581 | -0.24826 | -0.26897 | -0.29565 | -0.34188 | -0.40354 | -0.4 | -0.392 | -0.37337 | -0.3734 | -0.40966 | -0.44838 | -0.47826 | -0.499 | -0.50727 | -0.48846 | -0.45318 | -0.32375 | 4.7572e-05 | 0.0012206 | 6.1032e-05 | 6.1032e-05 | 0 | 0 | 0.0010808 | 0.05 | 0.15283 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.84723 | 0.878 | 0.91988 | 0.96801 | 0.98204 | 0.92823 | 0.87585 | 0.82043 | 0.76749 | 0.72059 | 0.67846 | 0.64152 | 0.61233 | 0.58938 | 0.57152 | 0.56422 | 0.55054 | 0.53197 | 0.51816 | 0.54388 | 0.56398 | 0.56766 | 0.5548 | 0.53318 | 0.51791 | 0.5205 | 0.54996 | 0.60272 | 0.6768 | 0.7651 | 0.86233 | 0.98204 | 4 | Slope | 0.9 | 0.61574 | 0.626 | 0.62885 | 0.63378 | 0.62735 | 0.5983 | 0.56973 | 0.54014 | 0.51139 | 0.48464 | 0.45949 | 0.43606 | 0.41522 | 0.39646 | 0.37939 | 0.36585 | 0.35018 | 0.33288 | 0.31717 | 0.31463 | 0.31022 | 0.30033 | 0.28493 | 0.26662 | 0.25042 | 0.24017 | 0.23887 | 0.24535 | 0.25893 | 0.27725 | 0.29856 | 0.63378 | 3 | 0.96801 | Slope | 0.93333 | 0.00095144 |  | 0.99529 | 0 | 0.96801 | Slope | 2 | 0.93333 | 0 | 20 | -20 | 0.00024983 | 9.3915e-05 | 0.0010808
192 | 0:32 | 0.095144 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 0.82705 | 0.0082705 | 0.0082705 | 0.095144 | 0.00036595 | [13 empty] | 0.73883 | 1 | 0.72947 | 0.30729 | -0.054075 | -0.26671 | -0.32759 | -0.31925 | -0.27855 | -0.23473 | -0.19496 | -0.17693 | -0.16976 | -0.17227 | -0.1869 | -0.19348 | -0.20781 | -0.25755 | -0.27417 | -0.27972 | -0.2767 | -0.27136 | -0.29759 | -0.33351 | -0.37074 | -0.39296 | -0.41182 | -0.42237 | -0.41011 | -0.38107 | -0.23651 | 0.00041352 | 0.00080179 | 4.009e-05 | 4.009e-05 | 0 | 0 | 0.0010458 | 0.05 | 0.12206 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.87798 | 0.91986 | 0.96799 | 0.98206 | 0.92825 | 0.87587 | 0.82045 | 0.76751 | 0.72061 | 0.67848 | 0.64155 | 0.61235 | 0.5894 | 0.57154 | 0.56424 | 0.55056 | 0.53199 | 0.51819 | 0.5439 | 0.564 | 0.56769 | 0.55482 | 0.5332 | 0.51793 | 0.52053 | 0.54998 | 0.60274 | 0.67683 | 0.76512 | 0.86236 | 0.95243 | 0.98206 | 3 | Slope | 0.93333 | 0.62599 | 0.63995 | 0.64489 | 0.63846 | 0.60942 | 0.58084 | 0.55126 | 0.5225 | 0.49576 | 0.47061 | 0.44718 | 0.42634 | 0.40758 | 0.39051 | 0.37697 | 0.3613 | 0.344 | 0.32828 | 0.32575 | 0.32133 | 0.31145 | 0.29605 | 0.27773 | 0.26153 | 0.25129 | 0.24999 | 0.25647 | 0.27005 | 0.28837 | 0.30967 | 0.32859 | 0.64489 | 2 | 0.96799 | Slope | 0.96667 | 0.0082705 |  | 0.95906 | 0 | 0.96799 | Slope | 2 | 0.96667 | 0 | 20 | -20 | 0.00036595 | 9.1028e-05 | 0.0010458
193 | 0:32 | 0.82705 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.9746 | 0.019746 | 0.019746 | 0.82705 | 0.00057378 | [13 empty] | 0.72947 | 1 | 0.76483 | 0.43115 | 0.13819 | -0.046522 | -0.12026 | -0.13857 | -0.11711 | -0.089685 | -0.069147 | -0.063088 | -0.063529 | -0.085185 | -0.079694 | -0.069598 | -0.088504 | -0.099065 | -0.12474 | -0.12959 | -0.13447 | -0.15376 | -0.18094 | -0.22111 | -0.25979 | -0.2895 | -0.32327 | -0.36051 | -0.38004 | -0.36206 | -0.24811 | 0.0009873 | 0.00032049 | 1.6025e-05 | 1.6025e-05 | 0 | 0 | 0.0010797 | 0.05 | 0.080179 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.91984 | 0.96797 | 0.98208 | 0.92827 | 0.87589 | 0.82048 | 0.76754 | 0.72064 | 0.67851 | 0.64157 | 0.61237 | 0.58942 | 0.57156 | 0.56426 | 0.55059 | 0.53201 | 0.51821 | 0.54393 | 0.56403 | 0.56771 | 0.55484 | 0.53323 | 0.51796 | 0.52055 | 0.55 | 0.60277 | 0.67685 | 0.76514 | 0.86238 | 0.95245 | 0.96275 | 0.98208 | 2 | Slope | 0.96667 | 0.63995 | 0.65599 | 0.64958 | 0.62054 | 0.59196 | 0.56238 | 0.53362 | 0.50688 | 0.48172 | 0.4583 | 0.43746 | 0.4187 | 0.40163 | 0.38809 | 0.37242 | 0.35511 | 0.3394 | 0.33686 | 0.33245 | 0.32257 | 0.30717 | 0.28885 | 0.27265 | 0.26241 | 0.26111 | 0.26759 | 0.28117 | 0.29949 | 0.32079 | 0.33971 | 0.33203 | 0.65599 | 1 | 0.96797 | Slope | 1 | 0.019746 |  | 0.90226 | 0 | 0.96797 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00057378 | 9.2175e-05 | 0.0010797
194 | 0:32 | 1.9746 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.9989 | 0.029989 | 0.029989 | 1.9746 | 0.00051215 | [13 empty] | 0.76483 | 1 | 0.81915 | 0.56308 | 0.32733 | 0.15936 | 0.072264 | 0.039378 | 0.042536 | 0.04668 | 0.051118 | 0.04696 | 0.02308 | 0.025109 | 0.047483 | 0.049268 | 0.051573 | 0.034725 | 0.018279 | 0.013962 | -0.0087633 | -0.031161 | -0.069211 | -0.12044 | -0.17571 | -0.23191 | -0.306 | -0.39364 | -0.43149 | -0.44384 | -0.3534 | 0.0014995 | -0.000179 | -8.9498e-06 | -8.9498e-06 | 0 | 0 | 0.0011931 | 0.05 | 0.032049 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.96794 | 0.98211 | 0.9283 | 0.87592 | 0.8205 | 0.76756 | 0.72066 | 0.67853 | 0.64159 | 0.6124 | 0.58945 | 0.57159 | 0.56429 | 0.55061 | 0.53204 | 0.51823 | 0.54395 | 0.56405 | 0.56773 | 0.55487 | 0.53325 | 0.51798 | 0.52057 | 0.55003 | 0.60279 | 0.67687 | 0.76517 | 0.8624 | 0.95248 | 0.96273 | 0.88789 | 0.98211 | 1 | Slope | 1 | 0.65598 | 0.6607 | 0.63165 | 0.60308 | 0.5735 | 0.54474 | 0.518 | 0.49284 | 0.46942 | 0.44858 | 0.42982 | 0.41275 | 0.39921 | 0.38354 | 0.36623 | 0.35052 | 0.34798 | 0.34357 | 0.33369 | 0.31829 | 0.29997 | 0.28377 | 0.27352 | 0.27223 | 0.27871 | 0.29229 | 0.31061 | 0.33191 | 0.35083 | 0.34313 | 0.30708 | 0.6607 | 1 | 0.98211 | Slope | 1 | 0.029989 |  | 0.85155 | 0 | 0.98211 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00051215 | 9.7302e-05 | 0.0011931
195 | 0:32 | 2.9989 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.7201 | 0.037201 | 0.037201 | 2.9989 | 0.00036062 | [13 empty] | 0.81915 | 1 | 0.8657 | 0.66981 | 0.4739 | 0.31783 | 0.23003 | 0.18674 | 0.16783 | 0.15586 | 0.14847 | 0.11855 | 0.1207 | 0.14043 | 0.15071 | 0.15577 | 0.15279 | 0.15036 | 0.14249 | 0.12561 | 0.098821 | 0.059872 | 0.0027696 | -0.070738 | -0.15948 | -0.26444 | -0.39866 | -0.50479 | -0.5633 | -0.56681 | -0.4829 | 0.0018601 | -0.00071712 | -3.5856e-05 | -3.5856e-05 | 0 | 0 | 0.0013847 | 0.05 | -0.0179 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.98214 | 0.92832 | 0.87594 | 0.82053 | 0.76759 | 0.72069 | 0.67856 | 0.64162 | 0.61242 | 0.58947 | 0.57161 | 0.56431 | 0.55064 | 0.53206 | 0.51826 | 0.54398 | 0.56408 | 0.56776 | 0.55489 | 0.53328 | 0.51801 | 0.5206 | 0.55005 | 0.60282 | 0.6769 | 0.76519 | 0.86243 | 0.95251 | 0.9627 | 0.88787 | 0.82251 | 0.98214 | 0 | Slope | 1 | 0.66071 | 0.64277 | 0.6142 | 0.58462 | 0.55586 | 0.52912 | 0.50396 | 0.48054 | 0.4597 | 0.44094 | 0.42387 | 0.41033 | 0.39466 | 0.37735 | 0.36164 | 0.3591 | 0.35469 | 0.34481 | 0.32941 | 0.31109 | 0.29489 | 0.28465 | 0.28335 | 0.28983 | 0.30341 | 0.32173 | 0.34303 | 0.36195 | 0.35423 | 0.31818 | 0.28528 | 0.66071 | 0 | 0.98214 | Slope | 1 | 0.037201 |  | 0.81585 | 0 | 0.98214 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00036062 | 0.00010544 | 0.0013847
196 | 0:32 | 3.7201 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.7271 | 0.037271 | 0.037271 | 3.7201 | 3.4523e-06 | [13 empty] | 0.8657 | 1 | 0.89649 | 0.7365 | 0.56406 | 0.42266 | 0.33581 | 0.28017 | 0.24976 | 0.2289 | 0.19772 | 0.19236 | 0.21039 | 0.21889 | 0.22326 | 0.22421 | 0.23497 | 0.24125 | 0.22543 | 0.20315 | 0.15935 | 0.09903 | 0.018349 | -0.089376 | -0.22762 | -0.39406 | -0.54613 | -0.65805 | -0.6861 | -0.66634 | -0.57849 | 0.0018635 | -0.0012409 | -6.2046e-05 | -6.2046e-05 | 0 | 0 | 0.0015867 | 0.05 | -0.071712 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.92835 | 0.87597 | 0.82056 | 0.76762 | 0.72071 | 0.67858 | 0.64165 | 0.61245 | 0.5895 | 0.57164 | 0.56434 | 0.55066 | 0.53209 | 0.51829 | 0.54401 | 0.5641 | 0.56779 | 0.55492 | 0.53331 | 0.51804 | 0.52063 | 0.55008 | 0.60284 | 0.67693 | 0.76522 | 0.86246 | 0.95253 | 0.96268 | 0.88784 | 0.82248 | 0.76834 | 0.96268 | 27 | Slope | 0.13333 | 0.64278 | 0.62532 | 0.59574 | 0.56698 | 0.54024 | 0.51508 | 0.49166 | 0.47082 | 0.45206 | 0.43499 | 0.42145 | 0.40578 | 0.38847 | 0.37276 | 0.37022 | 0.36581 | 0.35593 | 0.34053 | 0.32221 | 0.30601 | 0.29576 | 0.29447 | 0.30095 | 0.31453 | 0.33285 | 0.35415 | 0.37307 | 0.36534 | 0.32928 | 0.29638 | 0.26723 | 0.64278 | 0 | 0.92835 | Slope | 1 | 0.037271 |  | 0.81551 | 0 | 0.92835 | Slope | 2 | 1 | 0 | 20 | -20 | 3.4523e-06 | 0.00011529 | 0.0015867
197 | 0:33 | 3.7271 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.734 | 0.03734 | 0.03734 | 3.7271 | 3.4523e-06 | [13 empty] | 0.89649 | 1 | 0.91587 | 0.77713 | 0.62459 | 0.49466 | 0.40419 | 0.34341 | 0.30726 | 0.26583 | 0.25774 | 0.26813 | 0.27584 | 0.27919 | 0.27957 | 0.29275 | 0.30994 | 0.30729 | 0.28626 | 0.24753 | 0.18454 | 0.10279 | -0.0094641 | -0.16485 | -0.36428 | -0.54947 | -0.70179 | -0.77076 | -0.76646 | -0.72878 | -0.64299 | 0.001867 | -0.001795 | -8.9752e-05 | -8.9752e-05 | 0 | 0 | 0.0017981 | 0.05 | -0.12409 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.876 | 0.82058 | 0.76764 | 0.72074 | 0.67861 | 0.64168 | 0.61248 | 0.58953 | 0.57167 | 0.56437 | 0.55069 | 0.53212 | 0.51832 | 0.54403 | 0.56413 | 0.56782 | 0.55495 | 0.53333 | 0.51806 | 0.52066 | 0.55011 | 0.60287 | 0.67696 | 0.76525 | 0.86249 | 0.95256 | 0.96265 | 0.88781 | 0.82245 | 0.76832 | 0.72827 | 0.96265 | 26 | Slope | 0.16667 | 0.62533 | 0.60686 | 0.5781 | 0.55136 | 0.5262 | 0.50278 | 0.48194 | 0.46318 | 0.44611 | 0.43257 | 0.4169 | 0.39959 | 0.38388 | 0.38134 | 0.37693 | 0.36705 | 0.35165 | 0.33333 | 0.31713 | 0.30689 | 0.30559 | 0.31207 | 0.32565 | 0.34397 | 0.36527 | 0.38419 | 0.37644 | 0.34038 | 0.30748 | 0.27833 | 0.25387 | 0.62533 | 0 | 0.876 | Slope | 1 | 0.03734 |  | 0.81517 | 0 | 0.876 | Slope | 2 | 1 | 0 | 20 | -20 | 3.4523e-06 | 0.00012587 | 0.0017981
198 | 0:33 | 3.734 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.7409 | 0.037409 | 0.037409 | 3.734 | 3.4523e-06 | [13 empty] | 0.91587 | 1 | 0.92712 | 0.80386 | 0.66493 | 0.53903 | 0.44868 | 0.38636 | 0.33396 | 0.31328 | 0.31895 | 0.32132 | 0.32531 | 0.325 | 0.33567 | 0.35416 | 0.36285 | 0.35414 | 0.31863 | 0.26289 | 0.18134 | 0.071311 | -0.085765 | -0.30113 | -0.52307 | -0.7064 | -0.80952 | -0.83745 | -0.81181 | -0.76687 | -0.6892 | 0.0018704 | -0.0023245 | -0.00011622 | -0.00011622 | 0 | 0 | 0.0019836 | 0.05 | -0.1795 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.82061 | 0.76767 | 0.72077 | 0.67864 | 0.6417 | 0.6125 | 0.58955 | 0.57169 | 0.56439 | 0.55072 | 0.53214 | 0.51834 | 0.54406 | 0.56416 | 0.56784 | 0.55497 | 0.53336 | 0.51809 | 0.52068 | 0.55013 | 0.6029 | 0.67698 | 0.76527 | 0.86251 | 0.95259 | 0.96262 | 0.88779 | 0.82242 | 0.76829 | 0.72825 | 0.69612 | 0.96262 | 25 | Slope | 0.2 | 0.60687 | 0.58922 | 0.56248 | 0.53732 | 0.5139 | 0.49306 | 0.4743 | 0.45723 | 0.44369 | 0.42802 | 0.41071 | 0.395 | 0.39246 | 0.38805 | 0.37817 | 0.36277 | 0.34445 | 0.32825 | 0.31801 | 0.31671 | 0.32319 | 0.33677 | 0.35509 | 0.37639 | 0.39531 | 0.38754 | 0.35148 | 0.31859 | 0.28943 | 0.26497 | 0.24315 | 0.60687 | 0 | 0.82061 | Slope | 1 | 0.037409 |  | 0.81483 | 0 | 0.82061 | Slope | 2 | 1 | 0 | 20 | -20 | 3.4523e-06 | 0.00013637 | 0.0019836
199 | 0:33 | 3.7409 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.7478 | 0.037478 | 0.037478 | 3.7409 | 3.4523e-06 | [13 empty] | 0.92712 | 1 | 0.93501 | 0.82227 | 0.68989 | 0.56815 | 0.4792 | 0.40564 | 0.37076 | 0.36223 | 0.36176 | 0.36226 | 0.36287 | 0.37063 | 0.38583 | 0.39773 | 0.40038 | 0.37864 | 0.32898 | 0.25758 | 0.15171 | 0.00073414 | -0.21391 | -0.45651 | -0.67823 | -0.81098 | -0.86863 | -0.87102 | -0.83628 | -0.79402 | -0.72451 | 0.0018739 | -0.0027935 | -0.00013967 | -0.00013967 | 0 | 0 | 0.0021298 | 0.05 | -0.23245 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.76769 | 0.72079 | 0.67866 | 0.64173 | 0.61253 | 0.58958 | 0.57172 | 0.56442 | 0.55074 | 0.53217 | 0.51837 | 0.54408 | 0.56418 | 0.56787 | 0.555 | 0.53338 | 0.51811 | 0.52071 | 0.55016 | 0.60292 | 0.67701 | 0.7653 | 0.86254 | 0.95261 | 0.9626 | 0.88776 | 0.8224 | 0.76827 | 0.72822 | 0.6961 | 0.67296 | 0.9626 | 24 | Slope | 0.23333 | 0.58923 | 0.5736 | 0.54844 | 0.52502 | 0.50418 | 0.48541 | 0.46835 | 0.45481 | 0.43914 | 0.42183 | 0.40612 | 0.40358 | 0.39917 | 0.38929 | 0.37389 | 0.35557 | 0.33937 | 0.32912 | 0.32783 | 0.33431 | 0.34789 | 0.36621 | 0.38751 | 0.40643 | 0.39864 | 0.36259 | 0.32969 | 0.30053 | 0.27607 | 0.25426 | 0.23543 | 0.58923 | 0 | 0.76769 | Slope | 1 | 0.037478 |  | 0.81449 | 0 | 0.76769 | Slope | 2 | 1 | 0 | 20 | -20 | 3.4523e-06 | 0.00014626 | 0.0021298
200 | 0:33 | 3.7478 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.7547 | 0.037547 | 0.037547 | 3.7478 | 3.4523e-06 | [13 empty] | 0.93501 | 1 | 0.94051 | 0.83356 | 0.70646 | 0.58862 | 0.49221 | 0.43445 | 0.41058 | 0.39782 | 0.39648 | 0.39391 | 0.40104 | 0.41285 | 0.42319 | 0.4296 | 0.42021 | 0.38591 | 0.32303 | 0.23092 | 0.087751 | -0.11816 | -0.36295 | -0.61045 | -0.7828 | -0.86776 | -0.89669 | -0.88642 | -0.85351 | -0.81602 | -0.75049 | 0.0018773 | -0.0032148 | -0.00016074 | -0.00016074 | 0 | 0 | 0.0022513 | 0.05 | -0.27935 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.72081 | 0.67868 | 0.64175 | 0.61255 | 0.5896 | 0.57174 | 0.56444 | 0.55076 | 0.53219 | 0.51839 | 0.5441 | 0.5642 | 0.56789 | 0.55502 | 0.5334 | 0.51814 | 0.52073 | 0.55018 | 0.60294 | 0.67703 | 0.76532 | 0.86256 | 0.95263 | 0.96258 | 0.88774 | 0.82238 | 0.76825 | 0.7282 | 0.69608 | 0.67294 | 0.65602 | 0.96258 | 23 | Slope | 0.26667 | 0.5736 | 0.55956 | 0.53614 | 0.51529 | 0.49653 | 0.47947 | 0.46592 | 0.45025 | 0.43295 | 0.41724 | 0.4147 | 0.41029 | 0.40041 | 0.38501 | 0.36669 | 0.35049 | 0.34024 | 0.33895 | 0.34543 | 0.35901 | 0.37733 | 0.39863 | 0.41754 | 0.40975 | 0.37369 | 0.34079 | 0.31164 | 0.28718 | 0.26536 | 0.24654 | 0.22978 | 0.5736 | 0 | 0.72081 | Slope | 1 | 0.037547 |  | 0.81414 | 0 | 0.72081 | Slope | 2 | 1 | 0 | 20 | -20 | 3.4523e-06 | 0.00015517 | 0.0022513
201 | 0:33 | 3.7547 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.7616 | 0.037616 | 0.037616 | 3.7547 | 3.4523e-06 | [13 empty] | 0.94051 | 1 | 0.94366 | 0.84093 | 0.71814 | 0.59628 | 0.51376 | 0.46615 | 0.43965 | 0.42733 | 0.4231 | 0.42582 | 0.43646 | 0.44493 | 0.45055 | 0.44622 | 0.42569 | 0.38038 | 0.3003 | 0.17526 | -0.01982 | -0.25765 | -0.51362 | -0.71644 | -0.83954 | -0.8936 | -0.90699 | -0.89635 | -0.86767 | -0.83278 | -0.76704 | 0.0018808 | -0.0035841 | -0.00017921 | -0.00017921 | 0 | 0 | 0.0023505 | 0.05 | -0.32148 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.6787 | 0.64176 | 0.61257 | 0.58962 | 0.57176 | 0.56446 | 0.55078 | 0.53221 | 0.5184 | 0.54412 | 0.56422 | 0.5679 | 0.55504 | 0.53342 | 0.51815 | 0.52075 | 0.5502 | 0.60296 | 0.67705 | 0.76534 | 0.86257 | 0.95265 | 0.96256 | 0.88772 | 0.82236 | 0.76823 | 0.72818 | 0.69606 | 0.67292 | 0.656 | 0.64418 | 0.96256 | 22 | Slope | 0.3 | 0.55957 | 0.54725 | 0.52641 | 0.50765 | 0.49059 | 0.47704 | 0.46137 | 0.44407 | 0.42836 | 0.42582 | 0.42141 | 0.41152 | 0.39612 | 0.37781 | 0.36161 | 0.35136 | 0.35007 | 0.35654 | 0.37013 | 0.38845 | 0.40975 | 0.42866 | 0.42085 | 0.3848 | 0.3519 | 0.32274 | 0.29828 | 0.27646 | 0.25764 | 0.24089 | 0.22584 | 0.55957 | 0 | 0.6787 | Slope | 1 | 0.037616 |  | 0.8138 | 0 | 0.6787 | Slope | 2 | 1 | 0 | 20 | -20 | 3.4523e-06 | 0.00016294 | 0.0023505
202 | 0:33 | 3.7616 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.7685 | 0.037685 | 0.037685 | 3.7616 | 3.4525e-06 | [13 empty] | 0.94366 | 1 | 0.94593 | 0.84641 | 0.72189 | 0.61083 | 0.5366 | 0.48818 | 0.4638 | 0.4487 | 0.4481 | 0.45371 | 0.46253 | 0.46721 | 0.46406 | 0.45071 | 0.42188 | 0.36384 | 0.25609 | 0.084513 | -0.14369 | -0.39876 | -0.61742 | -0.77267 | -0.86301 | -0.89965 | -0.91105 | -0.90327 | -0.878 | -0.84331 | -0.77946 | 0.0018842 | -0.0038761 | -0.00019381 | -0.00019381 | 0 | 0 | 0.0024209 | 0.05 | -0.35841 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.64178 | 0.61258 | 0.58963 | 0.57177 | 0.56447 | 0.5508 | 0.53222 | 0.51842 | 0.54414 | 0.56423 | 0.56792 | 0.55505 | 0.53344 | 0.51817 | 0.52076 | 0.55021 | 0.60298 | 0.67706 | 0.76535 | 0.86259 | 0.95266 | 0.96254 | 0.88771 | 0.82235 | 0.76821 | 0.72817 | 0.69605 | 0.67291 | 0.65599 | 0.64417 | 0.63507 | 0.96254 | 21 | Slope | 0.33333 | 0.54726 | 0.53753 | 0.51877 | 0.5017 | 0.48816 | 0.47249 | 0.45518 | 0.43947 | 0.43693 | 0.43252 | 0.42264 | 0.40724 | 0.38892 | 0.37272 | 0.36248 | 0.36118 | 0.36766 | 0.38124 | 0.39956 | 0.42086 | 0.43978 | 0.43196 | 0.3959 | 0.363 | 0.33385 | 0.30939 | 0.28757 | 0.26875 | 0.252 | 0.23694 | 0.2228 | 0.54726 | 0 | 0.64178 | Slope | 1 | 0.037685 |  | 0.81346 | 0 | 0.64178 | Slope | 2 | 1 | 0 | 20 | -20 | 3.4525e-06 | 0.00016944 | 0.0024209
203 | 0:34 | 3.7685 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.7754 | 0.037754 | 0.037754 | 3.7685 | 3.4523e-06 | [13 empty] | 0.94593 | 1 | 0.94759 | 0.84744 | 0.7305 | 0.62617 | 0.55263 | 0.50824 | 0.48087 | 0.46816 | 0.47001 | 0.47513 | 0.4807 | 0.47792 | 0.46718 | 0.44738 | 0.40936 | 0.32912 | 0.17973 | -0.024027 | -0.27596 | -0.50174 | -0.67612 | -0.79741 | -0.86732 | -0.90028 | -0.91313 | -0.90854 | -0.88474 | -0.85111 | -0.78831 | 0.0018877 | -0.0041056 | -0.00020528 | -0.00020528 | 0 | 0 | 0.002472 | 0.05 | -0.38761 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.61259 | 0.58964 | 0.57178 | 0.56448 | 0.55081 | 0.53223 | 0.51843 | 0.54415 | 0.56425 | 0.56793 | 0.55506 | 0.53345 | 0.51818 | 0.52077 | 0.55022 | 0.60299 | 0.67707 | 0.76536 | 0.8626 | 0.95267 | 0.96253 | 0.8877 | 0.82234 | 0.7682 | 0.72816 | 0.69603 | 0.67289 | 0.65598 | 0.64415 | 0.63506 | 0.62873 | 0.96253 | 20 | Slope | 0.36667 | 0.53753 | 0.52988 | 0.51282 | 0.49927 | 0.4836 | 0.4663 | 0.45059 | 0.44805 | 0.44364 | 0.43375 | 0.41835 | 0.40004 | 0.38384 | 0.37359 | 0.3723 | 0.37877 | 0.39236 | 0.41068 | 0.43198 | 0.45089 | 0.44307 | 0.40701 | 0.37411 | 0.34496 | 0.3205 | 0.29868 | 0.27985 | 0.2631 | 0.24805 | 0.23391 | 0.22069 | 0.53753 | 0 | 0.61259 | Slope | 1 | 0.037754 |  | 0.81312 | 0 | 0.61259 | Slope | 2 | 1 | 0 | 20 | -20 | 3.4523e-06 | 0.00017464 | 0.002472
204 | 0:34 | 3.7754 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.7823 | 0.037823 | 0.037823 | 3.7754 | 3.4523e-06 | [13 empty] | 0.94759 | 1 | 0.9472 | 0.85154 | 0.73925 | 0.63699 | 0.56993 | 0.52195 | 0.49572 | 0.48528 | 0.4877 | 0.49006 | 0.48896 | 0.47946 | 0.4634 | 0.43664 | 0.38086 | 0.26459 | 0.084411 | -0.14851 | -0.37934 | -0.56478 | -0.70498 | -0.80314 | -0.86668 | -0.89949 | -0.91504 | -0.91235 | -0.88963 | -0.85665 | -0.79257 | 0.0018911 | -0.0042842 | -0.00021421 | -0.00021421 | 0 | 0 | 0.0025097 | 0.05 | -0.41056 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.58965 | 0.57179 | 0.56449 | 0.55082 | 0.53224 | 0.51844 | 0.54416 | 0.56426 | 0.56794 | 0.55507 | 0.53346 | 0.51819 | 0.52078 | 0.55023 | 0.603 | 0.67708 | 0.76537 | 0.86261 | 0.95268 | 0.96252 | 0.88769 | 0.82233 | 0.76819 | 0.72815 | 0.69602 | 0.67289 | 0.65597 | 0.64414 | 0.63505 | 0.62872 | 0.62557 | 0.96252 | 19 | Slope | 0.4 | 0.52988 | 0.52393 | 0.51039 | 0.49472 | 0.47741 | 0.4617 | 0.45916 | 0.45475 | 0.44487 | 0.42947 | 0.41115 | 0.39495 | 0.3847 | 0.38341 | 0.38989 | 0.40347 | 0.42179 | 0.44309 | 0.46201 | 0.45417 | 0.41812 | 0.38522 | 0.35606 | 0.33161 | 0.30979 | 0.29096 | 0.27421 | 0.25916 | 0.24502 | 0.23179 | 0.21963 | 0.52988 | 0 | 0.58965 | Slope | 1 | 0.037823 |  | 0.81278 | 0 | 0.58965 | Slope | 2 | 1 | 0 | 20 | -20 | 3.4523e-06 | 0.00017848 | 0.0025097
205 | 0:34 | 3.7823 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.7892 | 0.037892 | 0.037892 | 3.7823 | 3.4523e-06 | [13 empty] | 0.9472 | 1 | 0.94714 | 0.85191 | 0.74236 | 0.65021 | 0.57831 | 0.52845 | 0.50323 | 0.49507 | 0.49567 | 0.49361 | 0.48833 | 0.47633 | 0.45723 | 0.41891 | 0.33595 | 0.19307 | -0.018834 | -0.23899 | -0.43505 | -0.58868 | -0.70561 | -0.79614 | -0.85814 | -0.89423 | -0.91353 | -0.91225 | -0.8909 | -0.85841 | -0.79341 | 0.0018946 | -0.0043572 | -0.00021786 | -0.00021786 | 0 | 0 | 0.0025227 | 0.05 | -0.42842 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.5718 | 0.56449 | 0.55082 | 0.53224 | 0.51844 | 0.54416 | 0.56426 | 0.56794 | 0.55508 | 0.53346 | 0.51819 | 0.52078 | 0.55023 | 0.603 | 0.67708 | 0.76538 | 0.86261 | 0.95269 | 0.96252 | 0.88769 | 0.82232 | 0.76819 | 0.72814 | 0.69602 | 0.67288 | 0.65596 | 0.64414 | 0.63505 | 0.62871 | 0.62556 | 0.62687 | 0.96252 | 18 | Slope | 0.43333 | 0.52393 | 0.5215 | 0.50583 | 0.48853 | 0.47281 | 0.47028 | 0.46586 | 0.45598 | 0.44058 | 0.42227 | 0.40606 | 0.39582 | 0.39452 | 0.401 | 0.41458 | 0.4329 | 0.4542 | 0.47312 | 0.46528 | 0.42923 | 0.39633 | 0.36717 | 0.34271 | 0.3209 | 0.30207 | 0.28532 | 0.27027 | 0.25613 | 0.2429 | 0.23074 | 0.22007 | 0.52393 | 0 | 0.5718 | Slope | 1 | 0.037892 |  | 0.81243 | 0 | 0.5718 | Slope | 2 | 1 | 0 | 20 | -20 | 3.4523e-06 | 0.0001809 | 0.0025227
206 | 0:34 | 3.7892 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.7961 | 0.037961 | 0.037961 | 3.7892 | 3.4523e-06 | [13 empty] | 0.94714 | 1 | 0.94809 | 0.8555 | 0.75941 | 0.66155 | 0.58845 | 0.54088 | 0.51804 | 0.50749 | 0.50136 | 0.49195 | 0.48118 | 0.46281 | 0.42868 | 0.36026 | 0.25278 | 0.071771 | -0.13424 | -0.32219 | -0.48318 | -0.60892 | -0.71385 | -0.79856 | -0.86007 | -0.8968 | -0.91612 | -0.91505 | -0.89262 | -0.85761 | -0.78814 | 0.001898 | -0.004494 | -0.0002247 | -0.0002247 | 0 | 0 | 0.0025522 | 0.05 | -0.43572 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.5645 | 0.55083 | 0.53225 | 0.51845 | 0.54417 | 0.56427 | 0.56795 | 0.55508 | 0.53347 | 0.5182 | 0.52079 | 0.55024 | 0.60301 | 0.67709 | 0.76538 | 0.86262 | 0.95269 | 0.96251 | 0.88768 | 0.82232 | 0.76818 | 0.72814 | 0.69601 | 0.67288 | 0.65596 | 0.64413 | 0.63504 | 0.62871 | 0.62556 | 0.62686 | 0.63383 | 0.96251 | 17 | Slope | 0.46667 | 0.5215 | 0.51694 | 0.49964 | 0.48393 | 0.48139 | 0.47698 | 0.46709 | 0.45169 | 0.43338 | 0.41718 | 0.40693 | 0.40564 | 0.41211 | 0.4257 | 0.44402 | 0.46532 | 0.48423 | 0.47639 | 0.44034 | 0.40744 | 0.37828 | 0.35382 | 0.332 | 0.31318 | 0.29643 | 0.28138 | 0.26724 | 0.25401 | 0.24185 | 0.23118 | 0.22239 | 0.5215 | 0 | 0.5645 | Slope | 1 | 0.037961 |  | 0.81209 | 0 | 0.5645 | Slope | 2 | 1 | 0 | 20 | -20 | 3.4523e-06 | 0.00018207 | 0.0025522
207 | 0:34 | 3.7961 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.803 | 0.03803 | 0.03803 | 3.7961 | 3.4523e-06 | [13 empty] | 0.94809 | 1 | 0.94952 | 0.87344 | 0.77129 | 0.67231 | 0.60241 | 0.55789 | 0.53259 | 0.51376 | 0.49771 | 0.47996 | 0.45955 | 0.42234 | 0.3542 | 0.26171 | 0.11392 | -0.064914 | -0.24029 | -0.39137 | -0.52049 | -0.63062 | -0.72599 | -0.80651 | -0.86538 | -0.9007 | -0.91892 | -0.91516 | -0.88892 | -0.84801 | -0.76868 | 0.0019015 | -0.0046797 | -0.00023399 | -0.00023399 | 0 | 0 | 0.0025982 | 0.05 | -0.4494 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.55084 | 0.53226 | 0.51846 | 0.54418 | 0.56428 | 0.56796 | 0.55509 | 0.53348 | 0.51821 | 0.5208 | 0.55025 | 0.60302 | 0.6771 | 0.76539 | 0.86263 | 0.9527 | 0.9625 | 0.88767 | 0.82231 | 0.76817 | 0.72813 | 0.69601 | 0.67287 | 0.65595 | 0.64412 | 0.63503 | 0.6287 | 0.62555 | 0.62685 | 0.63382 | 0.6431 | 0.9625 | 16 | Slope | 0.5 | 0.51695 | 0.51075 | 0.49504 | 0.4925 | 0.48809 | 0.47821 | 0.46281 | 0.44449 | 0.42829 | 0.41804 | 0.41675 | 0.42323 | 0.43681 | 0.45513 | 0.47643 | 0.49535 | 0.4875 | 0.45145 | 0.41855 | 0.38939 | 0.36493 | 0.34311 | 0.32429 | 0.30754 | 0.29249 | 0.27834 | 0.26512 | 0.25296 | 0.24228 | 0.23349 | 0.22548 | 0.51695 | 0 | 0.55084 | Slope | 1 | 0.03803 |  | 0.81175 | 0 | 0.55084 | Slope | 2 | 1 | 0 | 20 | -20 | 3.4523e-06 | 0.00018154 | 0.0025982
208 | 0:34 | 3.803 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 8.9791 | 0.089791 | 0.089791 | 3.803 | 0.002588 | [13 empty] | 0.94952 | 1 | 0.9678 | 0.88494 | 0.77855 | 0.68124 | 0.61545 | 0.56939 | 0.53685 | 0.50869 | 0.48456 | 0.45716 | 0.41861 | 0.34848 | 0.25694 | 0.12708 | -0.019617 | -0.17121 | -0.3116 | -0.43134 | -0.54414 | -0.64362 | -0.73416 | -0.81189 | -0.86902 | -0.90325 | -0.91937 | -0.91243 | -0.88103 | -0.83124 | -0.73272 | 0.0044895 | -0.0048177 | -0.00024089 | -0.00024089 | 0 | 0 | 0.0026314 | 0.05 | -0.46797 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.53227 | 0.51847 | 0.54418 | 0.56428 | 0.56797 | 0.5551 | 0.53349 | 0.51822 | 0.52081 | 0.55026 | 0.60302 | 0.67711 | 0.7654 | 0.86264 | 0.95271 | 0.9625 | 0.88766 | 0.8223 | 0.76817 | 0.72812 | 0.696 | 0.67286 | 0.65594 | 0.64412 | 0.63502 | 0.62869 | 0.62554 | 0.62684 | 0.63381 | 0.64309 | 0.67226 | 0.9625 | 15 | Slope | 0.53333 | 0.51076 | 0.50616 | 0.50362 | 0.49921 | 0.48932 | 0.47392 | 0.45561 | 0.43941 | 0.42916 | 0.42786 | 0.43434 | 0.44792 | 0.46624 | 0.48755 | 0.50646 | 0.49861 | 0.46255 | 0.42966 | 0.4005 | 0.37604 | 0.35422 | 0.3354 | 0.31865 | 0.30359 | 0.28945 | 0.27623 | 0.26407 | 0.25339 | 0.2446 | 0.23659 | 0.2352 | 0.51076 | 0 | 0.53227 | Slope | 1 | 0.089791 |  | 0.55554 | 0 | 0.53227 | Slope | 2 | 1 | 0 | 20 | -20 | 0.002588 | 0.00017901 | 0.0026314
209 | 0:35 | 8.9791 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 7.3666 | 0.073666 | 0.073666 | 8.9791 | 0.00080622 | [13 empty] | 0.9678 | 1 | 0.96621 | 0.88402 | 0.7863 | 0.7027 | 0.62944 | 0.56468 | 0.50291 | 0.44742 | 0.39268 | 0.33053 | 0.24734 | 0.15196 | 0.040632 | -0.064842 | -0.16772 | -0.27111 | -0.36278 | -0.45973 | -0.55384 | -0.64856 | -0.7417 | -0.8204 | -0.87901 | -0.91743 | -0.93427 | -0.92387 | -0.8934 | -0.80898 | -0.6694 | 0.0036833 | -0.0045606 | -0.00022803 | -0.00022803 | 0 | 0 | 0.002537 | 0.05 | -0.48177 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.51845 | 0.54417 | 0.56427 | 0.56795 | 0.55509 | 0.53347 | 0.5182 | 0.52079 | 0.55024 | 0.60301 | 0.67709 | 0.76539 | 0.86262 | 0.9527 | 0.96251 | 0.88767 | 0.82231 | 0.76818 | 0.72813 | 0.69601 | 0.67287 | 0.65595 | 0.64413 | 0.63504 | 0.6287 | 0.62555 | 0.62686 | 0.63382 | 0.6431 | 0.67227 | 0.72209 | 0.96251 | 14 | Slope | 0.56667 | 0.50615 | 0.51472 | 0.51031 | 0.50043 | 0.48503 | 0.46671 | 0.45051 | 0.44026 | 0.43897 | 0.44545 | 0.45903 | 0.47735 | 0.49865 | 0.51757 | 0.50973 | 0.47367 | 0.44077 | 0.41161 | 0.38716 | 0.36534 | 0.34651 | 0.32976 | 0.31471 | 0.30057 | 0.28735 | 0.27518 | 0.26451 | 0.25572 | 0.2477 | 0.24631 | 0.25181 | 0.51757 | 13 | 0.9527 | Slope | 0.6 | 0.073666 |  | 0.63535 | 0 | 0.9527 | Slope | 2 | 0.6 | 0 | 20 | -20 | 0.00080622 | 0.0001746 | 0.002537
210 | 0:35 | 7.3666 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 5.2066 | 0.052066 | 0.052066 | 7.3666 | 0.00108 | [13 empty] | 0.96621 | 1 | 0.96635 | 0.88996 | 0.80421 | 0.71487 | 0.62603 | 0.53586 | 0.44835 | 0.36186 | 0.27012 | 0.16157 | 0.05331 | -0.055466 | -0.13822 | -0.20134 | -0.26045 | -0.31959 | -0.38991 | -0.46866 | -0.55685 | -0.65236 | -0.74576 | -0.82559 | -0.88794 | -0.92725 | -0.9415 | -0.93155 | -0.87065 | -0.74945 | -0.58117 | 0.0026033 | -0.0043596 | -0.00021798 | -0.00021798 | 0 | 0 | 0.0024686 | 0.05 | -0.45606 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.54416 | 0.56426 | 0.56794 | 0.55508 | 0.53346 | 0.51819 | 0.52078 | 0.55023 | 0.603 | 0.67708 | 0.76538 | 0.86261 | 0.95269 | 0.96252 | 0.88768 | 0.82232 | 0.76819 | 0.72814 | 0.69602 | 0.67288 | 0.65596 | 0.64414 | 0.63505 | 0.62871 | 0.62556 | 0.62687 | 0.63383 | 0.64311 | 0.67228 | 0.7221 | 0.78207 | 0.96252 | 13 | Slope | 0.6 | 0.51472 | 0.52142 | 0.51154 | 0.49614 | 0.47782 | 0.46162 | 0.45137 | 0.45008 | 0.45656 | 0.47014 | 0.48846 | 0.50976 | 0.52867 | 0.52084 | 0.48478 | 0.45189 | 0.42273 | 0.39827 | 0.37645 | 0.35763 | 0.34088 | 0.32582 | 0.31168 | 0.29846 | 0.2863 | 0.27562 | 0.26683 | 0.25882 | 0.25743 | 0.26292 | 0.2718 | 0.52867 | 12 | 0.95269 | Slope | 0.63333 | 0.052066 |  | 0.74228 | 0 | 0.95269 | Slope | 2 | 0.63333 | 0 | 20 | -20 | 0.00108 | 0.00016947 | 0.0024686
211 | 0:35 | 5.2066 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.8675 | 0.028675 | 0.028675 | 5.2066 | 0.0011695 | [13 empty] | 0.96635 | 1 | 0.96913 | 0.90144 | 0.8131 | 0.71327 | 0.60645 | 0.496 | 0.38069 | 0.25593 | 0.11431 | -0.021577 | -0.14371 | -0.22435 | -0.26836 | -0.29374 | -0.31603 | -0.35648 | -0.41023 | -0.48073 | -0.56483 | -0.65769 | -0.74931 | -0.8285 | -0.88851 | -0.923 | -0.93276 | -0.89547 | -0.80143 | -0.65078 | -0.47055 | 0.0014338 | -0.0043227 | -0.00021614 | -0.00021614 | 0 | 0 | 0.0024567 | 0.05 | -0.43596 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.56426 | 0.56794 | 0.55507 | 0.53346 | 0.51819 | 0.52078 | 0.55023 | 0.603 | 0.67708 | 0.76537 | 0.86261 | 0.95269 | 0.96252 | 0.88769 | 0.82232 | 0.76819 | 0.72815 | 0.69602 | 0.67288 | 0.65597 | 0.64414 | 0.63505 | 0.62872 | 0.62556 | 0.62687 | 0.63383 | 0.64312 | 0.67228 | 0.7221 | 0.78207 | 0.84608 | 0.96252 | 12 | Slope | 0.63333 | 0.52142 | 0.52265 | 0.50725 | 0.48893 | 0.47273 | 0.46248 | 0.46119 | 0.46767 | 0.48125 | 0.49957 | 0.52087 | 0.53978 | 0.53195 | 0.4959 | 0.463 | 0.43384 | 0.40938 | 0.38756 | 0.36874 | 0.35199 | 0.33694 | 0.32279 | 0.30957 | 0.29741 | 0.28673 | 0.27794 | 0.26993 | 0.26854 | 0.27403 | 0.28291 | 0.29314 | 0.53978 | 11 | 0.95269 | Slope | 0.66667 | 0.028675 |  | 0.85806 | 0 | 0.95269 | Slope | 2 | 0.66667 | 0 | 20 | -20 | 0.0011695 | 0.00016384 | 0.0024567
212 | 0:35 | 2.8675 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 0.77473 | 0.0077473 | 0.0077473 | 2.8675 | 0.0010464 | [13 empty] | 0.96913 | 1 | 0.97224 | 0.90464 | 0.81214 | 0.70488 | 0.58742 | 0.45803 | 0.3083 | 0.13337 | -0.038269 | -0.19245 | -0.29019 | -0.33737 | -0.35136 | -0.35038 | -0.35984 | -0.38829 | -0.43386 | -0.4971 | -0.57657 | -0.66506 | -0.75142 | -0.82461 | -0.87715 | -0.90151 | -0.88762 | -0.82136 | -0.69715 | -0.53376 | -0.36688 | 0.00038737 | -0.0044514 | -0.00022257 | -0.00022257 | 0 | 0 | 0.0024934 | 0.05 | -0.43227 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.56795 | 0.55508 | 0.53347 | 0.5182 | 0.52079 | 0.55024 | 0.603 | 0.67709 | 0.76538 | 0.86262 | 0.95269 | 0.96252 | 0.88768 | 0.82232 | 0.76818 | 0.72814 | 0.69602 | 0.67288 | 0.65596 | 0.64414 | 0.63504 | 0.62871 | 0.62556 | 0.62686 | 0.63383 | 0.64311 | 0.67228 | 0.72209 | 0.78207 | 0.84607 | 0.90881 | 0.96252 | 11 | Slope | 0.66667 | 0.52265 | 0.51836 | 0.50004 | 0.48384 | 0.4736 | 0.4723 | 0.47878 | 0.49236 | 0.51068 | 0.53198 | 0.5509 | 0.54306 | 0.507 | 0.47411 | 0.44495 | 0.42049 | 0.39867 | 0.37985 | 0.3631 | 0.34805 | 0.3339 | 0.32068 | 0.30852 | 0.29784 | 0.28905 | 0.28104 | 0.27965 | 0.28514 | 0.29402 | 0.30425 | 0.31405 | 0.5509 | 10 | 0.95269 | Slope | 0.7 | 0.0077473 |  | 0.96165 | 0 | 0.95269 | Slope | 2 | 0.7 | 0 | 20 | -20 | 0.0010464 | 0.00015766 | 0.0024934
213 | 0:35 | 0.77473 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.1144 | 0.011144 | 0.011144 | 0.77473 | 0.00016984 | [13 empty] | 0.97224 | 1 | 0.97318 | 0.9071 | 0.81805 | 0.71136 | 0.58739 | 0.43259 | 0.23703 | 0.028691 | -0.16848 | -0.30475 | -0.3746 | -0.39903 | -0.39651 | -0.38931 | -0.39335 | -0.4166 | -0.45576 | -0.51504 | -0.59022 | -0.6722 | -0.75174 | -0.81722 | -0.85719 | -0.8636 | -0.82665 | -0.73097 | -0.59243 | -0.44244 | -0.29656 | 0.00055721 | -0.0046676 | -0.00023338 | -0.00023338 | 0 | 0 | 0.0025415 | 0.05 | -0.44514 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.55509 | 0.53348 | 0.51821 | 0.5208 | 0.55025 | 0.60302 | 0.6771 | 0.76539 | 0.86263 | 0.9527 | 0.9625 | 0.88767 | 0.82231 | 0.76817 | 0.72813 | 0.69601 | 0.67287 | 0.65595 | 0.64413 | 0.63503 | 0.6287 | 0.62555 | 0.62685 | 0.63382 | 0.6431 | 0.67227 | 0.72208 | 0.78205 | 0.84606 | 0.9088 | 0.97165 | 0.97165 | 30 | Slope | 0.033333 | 0.51836 | 0.51116 | 0.49496 | 0.48471 | 0.48342 | 0.48989 | 0.50348 | 0.5218 | 0.5431 | 0.56201 | 0.55417 | 0.51811 | 0.48521 | 0.45606 | 0.4316 | 0.40978 | 0.39096 | 0.3742 | 0.35915 | 0.34501 | 0.33179 | 0.31963 | 0.30895 | 0.30016 | 0.29214 | 0.29076 | 0.29625 | 0.30513 | 0.31535 | 0.32515 | 0.33499 | 0.56201 | 9 | 0.9527 | Slope | 0.73333 | 0.011144 |  | 0.94484 | 0 | 0.9527 | Slope | 2 | 0.73333 | 0 | 20 | -20 | 0.00016984 | 0.00015073 | 0.0025415
214 | 0:35 | 1.1144 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.4239 | 0.024239 | 0.024239 | 1.1144 | 0.00065474 | [13 empty] | 0.97318 | 1 | 0.97398 | 0.91218 | 0.82625 | 0.71716 | 0.57143 | 0.37123 | 0.13776 | -0.10315 | -0.28289 | -0.38721 | -0.43086 | -0.43621 | -0.42715 | -0.41506 | -0.41551 | -0.43422 | -0.47051 | -0.52653 | -0.59675 | -0.67312 | -0.74593 | -0.80133 | -0.82291 | -0.80617 | -0.74065 | -0.62997 | -0.503 | -0.37234 | -0.24292 | 0.001212 | -0.0048203 | -0.00024101 | -0.00024101 | 0 | 0 | 0.0025757 | 0.05 | -0.46676 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.53349 | 0.51822 | 0.52081 | 0.55026 | 0.60302 | 0.67711 | 0.7654 | 0.86264 | 0.95271 | 0.9625 | 0.88766 | 0.8223 | 0.76817 | 0.72812 | 0.696 | 0.67286 | 0.65594 | 0.64412 | 0.63502 | 0.62869 | 0.62554 | 0.62684 | 0.63381 | 0.64309 | 0.67226 | 0.72208 | 0.78205 | 0.84606 | 0.90879 | 0.97164 | 0.96923 | 0.97164 | 29 | Slope | 0.066667 | 0.51116 | 0.50607 | 0.49582 | 0.49453 | 0.50101 | 0.51459 | 0.53291 | 0.55421 | 0.57313 | 0.56528 | 0.52922 | 0.49632 | 0.46717 | 0.44271 | 0.42089 | 0.40206 | 0.38531 | 0.37026 | 0.35612 | 0.3429 | 0.33074 | 0.32006 | 0.31127 | 0.30325 | 0.30186 | 0.30736 | 0.31624 | 0.32646 | 0.33626 | 0.3461 | 0.33419 | 0.57313 | 8 | 0.95271 | Slope | 0.76667 | 0.024239 |  | 0.88002 | 0 | 0.95271 | Slope | 2 | 0.76667 | 0 | 20 | -20 | 0.00065474 | 0.00014288 | 0.0025757
215 | 0:36 | 2.4239 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 4.7727 | 0.047727 | 0.047727 | 2.4239 | 0.0011744 | [13 empty] | 0.97398 | 1 | 0.97639 | 0.91783 | 0.83155 | 0.70408 | 0.5149 | 0.27295 | 0.00081768 | -0.22311 | -0.36556 | -0.43756 | -0.45569 | -0.45188 | -0.43568 | -0.42113 | -0.42026 | -0.43745 | -0.47232 | -0.52737 | -0.59555 | -0.66854 | -0.73833 | -0.77503 | -0.77383 | -0.73228 | -0.65303 | -0.5506 | -0.43643 | -0.31585 | -0.1944 | 0.0023863 | -0.0047943 | -0.00023972 | -0.00023972 | 0 | 0 | 0.0025697 | 0.05 | -0.48203 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.51821 | 0.52081 | 0.55026 | 0.60302 | 0.67711 | 0.7654 | 0.86264 | 0.95271 | 0.9625 | 0.88766 | 0.8223 | 0.76817 | 0.72812 | 0.696 | 0.67286 | 0.65594 | 0.64412 | 0.63502 | 0.62869 | 0.62554 | 0.62684 | 0.63381 | 0.64309 | 0.67226 | 0.72208 | 0.78205 | 0.84606 | 0.90879 | 0.97164 | 0.96922 | 0.92101 | 0.97164 | 28 | Slope | 0.1 | 0.50607 | 0.50694 | 0.50564 | 0.51212 | 0.5257 | 0.54402 | 0.56532 | 0.58424 | 0.57639 | 0.54033 | 0.50743 | 0.47828 | 0.45382 | 0.432 | 0.41318 | 0.39643 | 0.38137 | 0.36723 | 0.35401 | 0.34185 | 0.33117 | 0.32238 | 0.31436 | 0.31298 | 0.31847 | 0.32735 | 0.33757 | 0.34737 | 0.35721 | 0.3453 | 0.31811 | 0.58424 | 7 | 0.95271 | Slope | 0.8 | 0.047727 |  | 0.76375 | 0 | 0.95271 | Slope | 2 | 0.8 | 0 | 20 | -20 | 0.0011744 | 0.00013422 | 0.0025697
216 | 0:36 | 4.7727 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 6.5059 | 0.065059 | 0.065059 | 4.7727 | 0.00086659 | [13 empty] | 0.97639 | 1 | 0.97657 | 0.91572 | 0.81197 | 0.64164 | 0.40706 | 0.12141 | -0.13448 | -0.31539 | -0.41741 | -0.45308 | -0.45697 | -0.44068 | -0.42158 | -0.40879 | -0.40718 | -0.42457 | -0.4637 | -0.52162 | -0.59124 | -0.6723 | -0.72204 | -0.73525 | -0.71477 | -0.6628 | -0.58806 | -0.4881 | -0.37318 | -0.25235 | -0.12474 | 0.0032529 | -0.0044998 | -0.00022499 | -0.00022499 | 0 | 0 | 0.0024926 | 0.05 | -0.47943 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.52079 | 0.55024 | 0.60301 | 0.67709 | 0.76538 | 0.86262 | 0.95269 | 0.96251 | 0.88768 | 0.82232 | 0.76818 | 0.72814 | 0.69601 | 0.67287 | 0.65596 | 0.64413 | 0.63504 | 0.62871 | 0.62556 | 0.62686 | 0.63383 | 0.64311 | 0.67227 | 0.72209 | 0.78206 | 0.84607 | 0.9088 | 0.97166 | 0.96921 | 0.92099 | 0.88139 | 0.97166 | 27 | Slope | 0.13333 | 0.50693 | 0.51675 | 0.52322 | 0.53681 | 0.55513 | 0.57643 | 0.59534 | 0.5875 | 0.55145 | 0.51855 | 0.48939 | 0.46493 | 0.44312 | 0.42429 | 0.40754 | 0.39249 | 0.37835 | 0.36512 | 0.35296 | 0.34229 | 0.3335 | 0.32548 | 0.32409 | 0.32959 | 0.33847 | 0.34869 | 0.35849 | 0.36833 | 0.3564 | 0.32922 | 0.30491 | 0.59534 | 6 | 0.95269 | Slope | 0.83333 | 0.065059 |  | 0.67796 | 0 | 0.95269 | Slope | 2 | 0.83333 | 0 | 20 | -20 | 0.00086659 | 0.00012523 | 0.0024926
217 | 0:36 | 6.5059 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 7.7753 | 0.077753 | 0.077753 | 6.5059 | 0.00063472 | [13 empty] | 0.97657 | 1 | 0.9746 | 0.89887 | 0.75515 | 0.53751 | 0.25463 | -0.019219 | -0.23143 | -0.36748 | -0.42486 | -0.44217 | -0.42868 | -0.40885 | -0.39409 | -0.3806 | -0.37981 | -0.40584 | -0.45213 | -0.51613 | -0.60503 | -0.66626 | -0.69336 | -0.69404 | -0.66769 | -0.61775 | -0.53628 | -0.42492 | -0.30088 | -0.16437 | -0.032148 | 0.0038876 | -0.0039722 | -0.00019861 | -0.00019861 | 0 | 0 | 0.0023421 | 0.05 | -0.44998 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.55021 | 0.60298 | 0.67706 | 0.76536 | 0.86259 | 0.95267 | 0.96254 | 0.8877 | 0.82234 | 0.76821 | 0.72816 | 0.69604 | 0.6729 | 0.65598 | 0.64416 | 0.63507 | 0.62873 | 0.62558 | 0.62688 | 0.63385 | 0.64313 | 0.6723 | 0.72212 | 0.78209 | 0.8461 | 0.90883 | 0.97168 | 0.96918 | 0.92096 | 0.88136 | 0.85377 | 0.97168 | 26 | Slope | 0.16667 | 0.51674 | 0.53433 | 0.54791 | 0.56623 | 0.58753 | 0.60644 | 0.59862 | 0.56257 | 0.52967 | 0.50051 | 0.47605 | 0.45424 | 0.43541 | 0.41866 | 0.40361 | 0.38947 | 0.37624 | 0.36408 | 0.35341 | 0.34462 | 0.3366 | 0.33521 | 0.34071 | 0.34959 | 0.35981 | 0.36961 | 0.37945 | 0.36751 | 0.34032 | 0.31601 | 0.2957 | 0.60644 | 5 | 0.95267 | Slope | 0.86667 | 0.077753 |  | 0.61512 | 0 | 0.95267 | Slope | 2 | 0.86667 | 0 | 20 | -20 | 0.00063472 | 0.00011682 | 0.0023421
218 | 0:36 | 7.7753 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 7.8521 | 0.078521 | 0.078521 | 7.7753 | 3.8424e-05 | [13 empty] | 0.9746 | 1 | 0.96628 | 0.85682 | 0.66674 | 0.39864 | 0.12224 | -0.11067 | -0.27704 | -0.36221 | -0.39821 | -0.39349 | -0.37592 | -0.36339 | -0.34805 | -0.33555 | -0.34742 | -0.38513 | -0.44249 | -0.53857 | -0.60941 | -0.65076 | -0.6745 | -0.67615 | -0.65053 | -0.58445 | -0.48008 | -0.34854 | -0.19645 | -0.046165 | 0.08373 | 0.0039261 | -0.0032313 | -0.00016157 | -0.00016157 | 0 | 0 | 0.0021178 | 0.05 | -0.39722 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.60294 | 0.67703 | 0.76532 | 0.86256 | 0.95263 | 0.96258 | 0.88774 | 0.82238 | 0.76824 | 0.7282 | 0.69608 | 0.67294 | 0.65602 | 0.6442 | 0.6351 | 0.62877 | 0.62562 | 0.62692 | 0.63389 | 0.64317 | 0.67234 | 0.72215 | 0.78213 | 0.84614 | 0.90887 | 0.97172 | 0.96915 | 0.92093 | 0.88133 | 0.85373 | 0.83858 | 0.97172 | 25 | Slope | 0.2 | 0.53431 | 0.55901 | 0.57733 | 0.59863 | 0.61754 | 0.60975 | 0.57369 | 0.54079 | 0.51164 | 0.48718 | 0.46536 | 0.44654 | 0.42978 | 0.41473 | 0.40059 | 0.38737 | 0.37521 | 0.36453 | 0.35574 | 0.34772 | 0.34633 | 0.35183 | 0.36071 | 0.37093 | 0.38073 | 0.39057 | 0.3786 | 0.35142 | 0.32711 | 0.3068 | 0.29064 | 0.61754 | 4 | 0.95263 | Slope | 0.9 | 0.078521 |  | 0.61132 | 0 | 0.95263 | Slope | 2 | 0.9 | 0 | 20 | -20 | 3.8424e-05 | 0.00010989 | 0.0021178
219 | 0:36 | 7.8521 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 7.2079 | 0.072079 | 0.072079 | 7.8521 | 0.00032213 | [13 empty] | 0.96628 | 1 | 0.95024 | 0.80284 | 0.56666 | 0.30095 | 0.061294 | -0.12789 | -0.24125 | -0.30481 | -0.31672 | -0.30908 | -0.30288 | -0.29079 | -0.27757 | -0.28176 | -0.30918 | -0.36295 | -0.46434 | -0.54707 | -0.60436 | -0.65417 | -0.68802 | -0.69101 | -0.64217 | -0.54317 | -0.40819 | -0.23542 | -0.057975 | 0.098162 | 0.21963 | 0.0036039 | -0.0023484 | -0.00011742 | -0.00011742 | 0 | 0 | 0.0018631 | 0.05 | -0.32313 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.67698 | 0.76528 | 0.86251 | 0.95259 | 0.96262 | 0.88779 | 0.82242 | 0.76829 | 0.72825 | 0.69612 | 0.67298 | 0.65606 | 0.64424 | 0.63515 | 0.62881 | 0.62566 | 0.62697 | 0.63393 | 0.64321 | 0.67238 | 0.7222 | 0.78217 | 0.84618 | 0.90891 | 0.97176 | 0.9691 | 0.92088 | 0.88128 | 0.85369 | 0.83853 | 0.83452 | 0.97176 | 24 | Slope | 0.23333 | 0.55899 | 0.58843 | 0.60973 | 0.62864 | 0.62087 | 0.58482 | 0.55192 | 0.52276 | 0.4983 | 0.47648 | 0.45766 | 0.44091 | 0.42586 | 0.41172 | 0.39849 | 0.38633 | 0.37566 | 0.36687 | 0.35885 | 0.35746 | 0.36296 | 0.37183 | 0.38206 | 0.39186 | 0.4017 | 0.3897 | 0.36252 | 0.33821 | 0.3179 | 0.30173 | 0.28928 | 0.62864 | 3 | 0.95259 | Slope | 0.93333 | 0.072079 |  | 0.64321 | 0 | 0.95259 | Slope | 2 | 0.93333 | 0 | 20 | -20 | 0.00032213 | 0.00010515 | 0.0018631
220 | 0:36 | 7.2079 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 5.6458 | 0.056458 | 0.056458 | 7.2079 | 0.00078106 | [13 empty] | 0.95024 | 1 | 0.93435 | 0.75536 | 0.52271 | 0.2918 | 0.094775 | -0.039888 | -0.13198 | -0.17121 | -0.18314 | -0.19271 | -0.18915 | -0.18158 | -0.19084 | -0.21526 | -0.26324 | -0.37238 | -0.46654 | -0.545 | -0.62461 | -0.69518 | -0.73204 | -0.70673 | -0.61697 | -0.47771 | -0.29063 | -0.080527 | 0.11246 | 0.26647 | 0.36446 | 0.0028229 | -0.001376 | -6.8802e-05 | -6.8802e-05 | 0 | 0 | 0.0016263 | 0.05 | -0.23484 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.76523 | 0.86246 | 0.95254 | 0.96267 | 0.88783 | 0.82247 | 0.76834 | 0.72829 | 0.69617 | 0.67303 | 0.65611 | 0.64429 | 0.6352 | 0.62886 | 0.62571 | 0.62701 | 0.63398 | 0.64326 | 0.67243 | 0.72225 | 0.78222 | 0.84623 | 0.90896 | 0.97181 | 0.96905 | 0.92083 | 0.88123 | 0.85364 | 0.83848 | 0.83447 | 0.84056 | 0.97181 | 23 | Slope | 0.26667 | 0.58841 | 0.62082 | 0.63973 | 0.632 | 0.59594 | 0.56305 | 0.53389 | 0.50943 | 0.48761 | 0.46879 | 0.45204 | 0.43699 | 0.42284 | 0.40962 | 0.39746 | 0.38678 | 0.37799 | 0.36998 | 0.36859 | 0.37408 | 0.38296 | 0.39319 | 0.40299 | 0.41283 | 0.4008 | 0.37361 | 0.3493 | 0.32899 | 0.31283 | 0.30038 | 0.2913 | 0.63973 | 2 | 0.95254 | Slope | 0.96667 | 0.056458 |  | 0.72053 | 0 | 0.95254 | Slope | 2 | 0.96667 | 0 | 20 | -20 | 0.00078106 | 0.00010281 | 0.0016263
221 | 0:37 | 5.6458 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.5371 | 0.035371 | 0.035371 | 5.6458 | 0.0010543 | [13 empty] | 0.93435 | 1 | 0.92032 | 0.74447 | 0.54397 | 0.35569 | 0.21444 | 0.10242 | 0.034848 | -0.0060008 | -0.037622 | -0.051931 | -0.054505 | -0.071655 | -0.10322 | -0.14916 | -0.25396 | -0.35881 | -0.45353 | -0.56143 | -0.66712 | -0.74303 | -0.75397 | -0.69046 | -0.56082 | -0.36834 | -0.1405 | 0.09103 | 0.28694 | 0.42059 | 0.47943 | 0.0017686 | -0.00047531 | -2.3765e-05 | -2.3765e-05 | 0 | 0 | 0.00144 | 0.05 | -0.1376 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.86242 | 0.95249 | 0.96271 | 0.88788 | 0.82252 | 0.76838 | 0.72834 | 0.69622 | 0.67308 | 0.65616 | 0.64434 | 0.63524 | 0.62891 | 0.62576 | 0.62706 | 0.63403 | 0.64331 | 0.67248 | 0.72229 | 0.78226 | 0.84627 | 0.909 | 0.97186 | 0.96901 | 0.92079 | 0.88119 | 0.85359 | 0.83844 | 0.83443 | 0.84051 | 0.85488 | 0.97186 | 22 | Slope | 0.3 | 0.62081 | 0.65083 | 0.64313 | 0.60707 | 0.57417 | 0.54502 | 0.52056 | 0.49874 | 0.47991 | 0.46316 | 0.44811 | 0.43397 | 0.42075 | 0.40859 | 0.39791 | 0.38912 | 0.3811 | 0.37971 | 0.38521 | 0.39409 | 0.40431 | 0.41411 | 0.42395 | 0.41189 | 0.38471 | 0.3604 | 0.34009 | 0.32392 | 0.31148 | 0.30239 | 0.29607 | 0.65083 | 1 | 0.95249 | Slope | 1 | 0.035371 |  | 0.82491 | 0 | 0.95249 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0010543 | 0.0001024 | 0.00144
222 | 0:37 | 3.5371 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.4285 | 0.014285 | 0.014285 | 3.5371 | 0.0010543 | [13 empty] | 0.92032 | 1 | 0.92696 | 0.78201 | 0.62525 | 0.49356 | 0.38 | 0.29502 | 0.22673 | 0.16533 | 0.12798 | 0.10548 | 0.076064 | 0.034908 | -0.01965 | -0.11947 | -0.22415 | -0.33698 | -0.46428 | -0.59597 | -0.7 | -0.7479 | -0.72396 | -0.62502 | -0.45115 | -0.22489 | 0.018642 | 0.24934 | 0.42299 | 0.51796 | 0.54629 | 0.00071424 | 0.00037262 | 1.8631e-05 | 1.8631e-05 | 0 | 0 | 0.0013762 | 0.05 | -0.047531 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.95245 | 0.96276 | 0.88792 | 0.82256 | 0.76842 | 0.72838 | 0.69626 | 0.67312 | 0.6562 | 0.64438 | 0.63528 | 0.62895 | 0.6258 | 0.6271 | 0.63407 | 0.64335 | 0.67252 | 0.72233 | 0.78231 | 0.84632 | 0.90905 | 0.9719 | 0.96897 | 0.92075 | 0.88115 | 0.85355 | 0.8384 | 0.83438 | 0.84047 | 0.85484 | 0.88122 | 0.9719 | 21 | Slope | 0.33333 | 0.65082 | 0.65425 | 0.6182 | 0.5853 | 0.55614 | 0.53168 | 0.50986 | 0.49104 | 0.47429 | 0.45924 | 0.44509 | 0.43187 | 0.41971 | 0.40903 | 0.40025 | 0.39223 | 0.39084 | 0.39633 | 0.40521 | 0.41544 | 0.42524 | 0.43508 | 0.42299 | 0.3958 | 0.37149 | 0.35118 | 0.33502 | 0.32257 | 0.31349 | 0.30717 | 0.30485 | 0.65425 | 1 | 0.96276 | Slope | 1 | 0.014285 |  | 0.92929 | 0 | 0.96276 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0010543 | 0.00010303 | 0.0013762
223 | 0:37 | 1.4285 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -0.29576 | -0.0029576 | -0.0029576 | 1.4285 | 0.00086212 | [13 empty] | 0.92696 | 1 | 0.94102 | 0.82986 | 0.72171 | 0.61946 | 0.53434 | 0.45368 | 0.37136 | 0.30767 | 0.26425 | 0.21845 | 0.16801 | 0.10666 | 0.0073622 | -0.096408 | -0.21299 | -0.35432 | -0.49654 | -0.61695 | -0.69112 | -0.70786 | -0.65368 | -0.52215 | -0.32375 | -0.088795 | 0.14762 | 0.3526 | 0.48801 | 0.55879 | 0.60364 | -0.00014788 | 0.001121 | 5.6049e-05 | 5.6049e-05 | 0 | 0 | 0.0014126 | 0.05 | 0.037262 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.96279 | 0.88796 | 0.8226 | 0.76846 | 0.72842 | 0.6963 | 0.67316 | 0.65624 | 0.64441 | 0.63532 | 0.62899 | 0.62584 | 0.62714 | 0.63411 | 0.64339 | 0.67256 | 0.72237 | 0.78234 | 0.84635 | 0.90908 | 0.97194 | 0.96893 | 0.92071 | 0.88111 | 0.85351 | 0.83836 | 0.83435 | 0.84044 | 0.8548 | 0.88118 | 0.91453 | 0.97194 | 20 | Slope | 0.36667 | 0.65426 | 0.62932 | 0.59642 | 0.56727 | 0.54281 | 0.52099 | 0.50216 | 0.48541 | 0.47036 | 0.45622 | 0.443 | 0.43083 | 0.42016 | 0.41137 | 0.40335 | 0.40196 | 0.40746 | 0.41634 | 0.42656 | 0.43636 | 0.4462 | 0.43409 | 0.4069 | 0.38259 | 0.36228 | 0.34612 | 0.33367 | 0.32459 | 0.31827 | 0.31595 | 0.31596 | 0.65426 | 0 | 0.96279 | Slope | 1 | 0.0029576 |  | 0.98536 | 0 | 0.96279 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00086212 | 0.00010391 | 0.0014126
224 | 0:37 | -0.29576 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -1.8954 | -0.018954 | -0.018954 | -0.29576 | 0.0007998 | [13 empty] | 0.94102 | 1 | 0.95422 | 0.87622 | 0.79325 | 0.71666 | 0.63888 | 0.55089 | 0.47051 | 0.40478 | 0.3439 | 0.28163 | 0.21459 | 0.11769 | 0.0099328 | -0.10967 | -0.25097 | -0.40015 | -0.52531 | -0.61617 | -0.66193 | -0.65022 | -0.56927 | -0.41575 | -0.20846 | 0.019957 | 0.23238 | 0.40133 | 0.5163 | 0.59853 | 0.63795 | -0.00094768 | 0.0017746 | 8.8729e-05 | 8.8729e-05 | 0 | 0 | 0.0015046 | 0.05 | 0.1121 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.88799 | 0.82263 | 0.7685 | 0.72845 | 0.69633 | 0.67319 | 0.65627 | 0.64445 | 0.63535 | 0.62902 | 0.62587 | 0.62717 | 0.63414 | 0.64342 | 0.67259 | 0.72241 | 0.78238 | 0.84639 | 0.90912 | 0.97197 | 0.9689 | 0.92068 | 0.88108 | 0.85348 | 0.83833 | 0.83431 | 0.8404 | 0.85477 | 0.88115 | 0.9145 | 0.95795 | 0.97197 | 19 | Slope | 0.4 | 0.62933 | 0.60754 | 0.57839 | 0.55393 | 0.53211 | 0.51329 | 0.49653 | 0.48148 | 0.46734 | 0.45412 | 0.44196 | 0.43128 | 0.42249 | 0.41447 | 0.41309 | 0.41858 | 0.42746 | 0.43768 | 0.44748 | 0.45732 | 0.44519 | 0.418 | 0.39369 | 0.37338 | 0.35722 | 0.34477 | 0.33569 | 0.32937 | 0.32705 | 0.32706 | 0.33043 | 0.62933 | 0 | 0.88799 | Slope | 1 | 0.018954 |  | 0.90618 | 0 | 0.88799 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0007998 | 0.0001045 | 0.0015046
225 | 0:37 | -1.8954 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -3.8847 | -0.038847 | -0.038847 | -1.8954 | 0.00099467 | [13 empty] | 0.95422 | 1 | 0.9671 | 0.90631 | 0.84285 | 0.77383 | 0.69276 | 0.60857 | 0.52911 | 0.45203 | 0.37924 | 0.30397 | 0.20972 | 0.099693 | -0.027444 | -0.16906 | -0.31476 | -0.44547 | -0.54566 | -0.61321 | -0.63294 | -0.59792 | -0.49344 | -0.32522 | -0.1174 | 0.094832 | 0.27875 | 0.43203 | 0.55273 | 0.62995 | 0.67155 | -0.0019423 | 0.0023159 | 0.0001158 | 0.0001158 | 0 | 0 | 0.0016142 | 0.05 | 0.17746 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.82266 | 0.76852 | 0.72848 | 0.69635 | 0.67322 | 0.6563 | 0.64447 | 0.63538 | 0.62905 | 0.6259 | 0.6272 | 0.63417 | 0.64345 | 0.67262 | 0.72243 | 0.7824 | 0.84641 | 0.90914 | 0.972 | 0.96887 | 0.92065 | 0.88105 | 0.85345 | 0.8383 | 0.83429 | 0.84038 | 0.85474 | 0.88112 | 0.91447 | 0.95792 | 0.99062 | 0.99062 | 30 | Slope | 0.033333 | 0.60755 | 0.58951 | 0.56505 | 0.54323 | 0.52441 | 0.50765 | 0.4926 | 0.47846 | 0.46524 | 0.45308 | 0.4424 | 0.43361 | 0.42559 | 0.42421 | 0.4297 | 0.43858 | 0.4488 | 0.4586 | 0.46844 | 0.45629 | 0.42911 | 0.40479 | 0.38448 | 0.36832 | 0.35587 | 0.34679 | 0.34047 | 0.33815 | 0.33816 | 0.34153 | 0.34132 | 0.60755 | 0 | 0.82266 | Slope | 1 | 0.038847 |  | 0.80771 | 0 | 0.82266 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00099467 | 0.00010456 | 0.0016142
226 | 0:37 | -3.8847 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.8762 | -0.048762 | -0.048762 | -3.8847 | 0.00049575 | [13 empty] | 0.9671 | 1 | 0.97244 | 0.92251 | 0.86466 | 0.79444 | 0.71683 | 0.63453 | 0.54853 | 0.46343 | 0.38031 | 0.28585 | 0.17166 | 0.036419 | -0.11097 | -0.25463 | -0.383 | -0.49535 | -0.57934 | -0.62392 | -0.62368 | -0.56221 | -0.43471 | -0.2553 | -0.05171 | 0.14318 | 0.3203 | 0.47575 | 0.59323 | 0.67016 | 0.71218 | -0.0024381 | 0.0027164 | 0.00013582 | 0.00013582 | 0 | 0 | 0.0017236 | 0.05 | 0.23159 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.76854 | 0.7285 | 0.69637 | 0.67324 | 0.65632 | 0.64449 | 0.6354 | 0.62907 | 0.62592 | 0.62722 | 0.63419 | 0.64347 | 0.67264 | 0.72245 | 0.78242 | 0.84643 | 0.90916 | 0.97202 | 0.96885 | 0.92063 | 0.88103 | 0.85343 | 0.83828 | 0.83427 | 0.84036 | 0.85472 | 0.8811 | 0.91445 | 0.9579 | 0.99064 | 0.93201 | 0.99064 | 29 | Slope | 0.066667 | 0.58951 | 0.57617 | 0.55435 | 0.53552 | 0.51877 | 0.50372 | 0.48958 | 0.47636 | 0.46419 | 0.45352 | 0.44473 | 0.43671 | 0.43532 | 0.44082 | 0.4497 | 0.45992 | 0.46972 | 0.47956 | 0.46739 | 0.44021 | 0.4159 | 0.39559 | 0.37943 | 0.36698 | 0.3579 | 0.35157 | 0.34926 | 0.34926 | 0.35263 | 0.35243 | 0.32178 | 0.58951 | 0 | 0.76854 | Slope | 1 | 0.048762 |  | 0.75863 | 0 | 0.76854 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00049575 | 0.00010411 | 0.0017236
227 | 0:38 | -4.8762 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.958 | -0.05958 | -0.05958 | -4.8762 | 0.00054091 | [13 empty] | 0.97244 | 1 | 0.9767 | 0.93084 | 0.87245 | 0.80471 | 0.72855 | 0.64163 | 0.54935 | 0.45541 | 0.357 | 0.23916 | 0.096692 | -0.058659 | -0.20766 | -0.33572 | -0.45034 | -0.55072 | -0.61428 | -0.64133 | -0.61342 | -0.52374 | -0.37732 | -0.19302 | 0.0013785 | 0.19533 | 0.37437 | 0.5275 | 0.64254 | 0.71673 | 0.75203 | -0.002979 | 0.0030376 | 0.00015188 | 0.00015188 | 0 | 0 | 0.0018206 | 0.05 | 0.27164 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.72851 | 0.69639 | 0.67325 | 0.65633 | 0.64451 | 0.63542 | 0.62908 | 0.62593 | 0.62724 | 0.6342 | 0.64348 | 0.67265 | 0.72247 | 0.78244 | 0.84645 | 0.90918 | 0.97203 | 0.96883 | 0.92061 | 0.88101 | 0.85342 | 0.83826 | 0.83425 | 0.84034 | 0.85471 | 0.88109 | 0.91444 | 0.95788 | 0.99065 | 0.93202 | 0.87384 | 0.99065 | 28 | Slope | 0.1 | 0.57617 | 0.56546 | 0.54664 | 0.52989 | 0.51484 | 0.50069 | 0.48747 | 0.47531 | 0.46463 | 0.45585 | 0.44783 | 0.44644 | 0.45193 | 0.46081 | 0.47104 | 0.48084 | 0.49068 | 0.4785 | 0.45132 | 0.427 | 0.4067 | 0.39053 | 0.37808 | 0.369 | 0.36268 | 0.36036 | 0.36037 | 0.36374 | 0.36355 | 0.3329 | 0.30239 | 0.57617 | 0 | 0.72851 | Slope | 1 | 0.05958 |  | 0.70508 | 0 | 0.72851 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00054091 | 0.00010333 | 0.0018206
228 | 0:38 | -5.958 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -6.2023 | -0.062023 | -0.062023 | -5.958 | 0.00012216 | [13 empty] | 0.9767 | 1 | 0.97799 | 0.93193 | 0.87489 | 0.80781 | 0.72812 | 0.63577 | 0.53531 | 0.42953 | 0.30385 | 0.15389 | -0.0093245 | -0.16628 | -0.30123 | -0.42053 | -0.52829 | -0.61122 | -0.66019 | -0.65893 | -0.59849 | -0.48291 | -0.32253 | -0.13838 | 0.062458 | 0.25977 | 0.4395 | 0.58989 | 0.70008 | 0.76497 | 0.78979 | -0.0031012 | 0.003269 | 0.00016345 | 0.00016345 | 0 | 0 | 0.0018979 | 0.05 | 0.30376 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.6964 | 0.67326 | 0.65634 | 0.64452 | 0.63543 | 0.6291 | 0.62594 | 0.62725 | 0.63421 | 0.6435 | 0.67266 | 0.72248 | 0.78245 | 0.84646 | 0.90919 | 0.97204 | 0.96882 | 0.9206 | 0.881 | 0.85341 | 0.83825 | 0.83424 | 0.84033 | 0.8547 | 0.88107 | 0.91443 | 0.95787 | 0.99066 | 0.93203 | 0.87386 | 0.82426 | 0.99066 | 27 | Slope | 0.13333 | 0.56547 | 0.55775 | 0.541 | 0.52595 | 0.51181 | 0.49859 | 0.48643 | 0.47575 | 0.46696 | 0.45894 | 0.45755 | 0.46305 | 0.47193 | 0.48215 | 0.49195 | 0.50179 | 0.48961 | 0.46242 | 0.43811 | 0.4178 | 0.40164 | 0.38919 | 0.38011 | 0.37379 | 0.37147 | 0.37148 | 0.37485 | 0.37467 | 0.34401 | 0.31351 | 0.28587 | 0.56547 | 0 | 0.6964 | Slope | 1 | 0.062023 |  | 0.69298 | 0 | 0.6964 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00012216 | 0.0001023 | 0.0018979
229 | 0:38 | -6.2023 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.8736 | -0.058736 | -0.058736 | -6.2023 | 0.00016436 | [13 empty] | 0.97799 | 1 | 0.97796 | 0.93271 | 0.87597 | 0.80618 | 0.7217 | 0.62185 | 0.51143 | 0.37837 | 0.22054 | 0.049732 | -0.11568 | -0.26036 | -0.38986 | -0.50633 | -0.60046 | -0.67238 | -0.69482 | -0.66033 | -0.57111 | -0.43659 | -0.27072 | -0.075771 | 0.13028 | 0.33009 | 0.50736 | 0.65155 | 0.7508 | 0.80571 | 0.81629 | -0.0029368 | 0.0034382 | 0.00017191 | 0.00017191 | 0 | 0 | 0.001953 | 0.05 | 0.3269 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.67327 | 0.65635 | 0.64453 | 0.63544 | 0.6291 | 0.62595 | 0.62726 | 0.63422 | 0.6435 | 0.67267 | 0.72249 | 0.78246 | 0.84647 | 0.9092 | 0.97205 | 0.96881 | 0.92059 | 0.88099 | 0.8534 | 0.83824 | 0.83423 | 0.84032 | 0.85469 | 0.88107 | 0.91442 | 0.95786 | 0.99067 | 0.93204 | 0.87386 | 0.82427 | 0.78956 | 0.99067 | 26 | Slope | 0.16667 | 0.55776 | 0.55212 | 0.53707 | 0.52292 | 0.5097 | 0.49754 | 0.48686 | 0.47807 | 0.47006 | 0.46867 | 0.47416 | 0.48304 | 0.49327 | 0.50307 | 0.51291 | 0.50072 | 0.47353 | 0.44922 | 0.42891 | 0.41275 | 0.4003 | 0.39122 | 0.3849 | 0.38258 | 0.38258 | 0.38595 | 0.38578 | 0.35512 | 0.32462 | 0.29698 | 0.2743 | 0.55776 | 0 | 0.67327 | Slope | 1 | 0.058736 |  | 0.70926 | 0 | 0.67327 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00016436 | 0.00010104 | 0.001953
230 | 0:38 | -5.8736 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.7332 | -0.057332 | -0.057332 | -5.8736 | 7.0202e-05 | [13 empty] | 0.97796 | 1 | 0.97846 | 0.93371 | 0.87541 | 0.802 | 0.71122 | 0.6028 | 0.46802 | 0.30577 | 0.12777 | -0.045988 | -0.20103 | -0.34256 | -0.47259 | -0.58001 | -0.66729 | -0.71659 | -0.70792 | -0.64476 | -0.53482 | -0.39187 | -0.21341 | -0.011673 | 0.19778 | 0.39542 | 0.56598 | 0.69869 | 0.78928 | 0.83398 | 0.83184 | -0.0028666 | 0.0035564 | 0.00017782 | 0.00017782 | 0 | 0 | 0.0019871 | 0.05 | 0.34382 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.65636 | 0.64454 | 0.63544 | 0.62911 | 0.62596 | 0.62726 | 0.63423 | 0.64351 | 0.67268 | 0.72249 | 0.78247 | 0.84647 | 0.90921 | 0.97206 | 0.96881 | 0.92059 | 0.88099 | 0.85339 | 0.83824 | 0.83422 | 0.84031 | 0.85468 | 0.88106 | 0.91441 | 0.95786 | 0.99068 | 0.93205 | 0.87387 | 0.82428 | 0.78957 | 0.76716 | 0.99068 | 25 | Slope | 0.2 | 0.55212 | 0.54818 | 0.53404 | 0.52081 | 0.50865 | 0.49798 | 0.48919 | 0.48117 | 0.47978 | 0.48528 | 0.49416 | 0.50438 | 0.51418 | 0.52402 | 0.51182 | 0.48464 | 0.46033 | 0.44002 | 0.42386 | 0.41141 | 0.40233 | 0.39601 | 0.39369 | 0.39369 | 0.39706 | 0.39689 | 0.36624 | 0.33573 | 0.30809 | 0.28541 | 0.26683 | 0.55212 | 0 | 0.65636 | Slope | 1 | 0.057332 |  | 0.71621 | 0 | 0.65636 | Slope | 2 | 1 | 0 | 20 | -20 | 7.0202e-05 | 9.9581e-05 | 0.0019871
231 | 0:38 | -5.7332 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.5138 | -0.055138 | -0.055138 | -5.7332 | 0.00010969 | [13 empty] | 0.97846 | 1 | 0.9787 | 0.93297 | 0.87165 | 0.79253 | 0.69377 | 0.5619 | 0.39866 | 0.21542 | 0.033443 | -0.13034 | -0.2823 | -0.42507 | -0.54788 | -0.65041 | -0.71692 | -0.7361 | -0.69836 | -0.6129 | -0.49252 | -0.33527 | -0.14805 | 0.058476 | 0.26678 | 0.45793 | 0.61598 | 0.73877 | 0.81952 | 0.85265 | 0.83961 | -0.0027569 | 0.0036474 | 0.00018237 | 0.00018237 | 0 | 0 | 0.0020124 | 0.05 | 0.35564 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.64454 | 0.63545 | 0.62911 | 0.62596 | 0.62727 | 0.63423 | 0.64351 | 0.67268 | 0.7225 | 0.78247 | 0.84648 | 0.90921 | 0.97206 | 0.9688 | 0.92058 | 0.88098 | 0.85339 | 0.83823 | 0.83422 | 0.84031 | 0.85468 | 0.88105 | 0.91441 | 0.95785 | 0.99068 | 0.93205 | 0.87387 | 0.82428 | 0.78957 | 0.76716 | 0.75299 | 0.99068 | 24 | Slope | 0.23333 | 0.54818 | 0.54515 | 0.53193 | 0.51977 | 0.50909 | 0.5003 | 0.49228 | 0.49089 | 0.49639 | 0.50527 | 0.51549 | 0.52529 | 0.53513 | 0.52293 | 0.49575 | 0.47144 | 0.45113 | 0.43497 | 0.42252 | 0.41344 | 0.40711 | 0.4048 | 0.4048 | 0.40817 | 0.40801 | 0.37735 | 0.34685 | 0.31921 | 0.29652 | 0.27794 | 0.26211 | 0.54818 | 0 | 0.64454 | Slope | 1 | 0.055138 |  | 0.72707 | 0 | 0.64454 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00010969 | 9.7952e-05 | 0.0020124
232 | 0:38 | -5.5138 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.8599 | -0.048599 | -0.048599 | -5.5138 | 0.00032697 | [13 empty] | 0.9787 | 1 | 0.97823 | 0.93021 | 0.86396 | 0.77759 | 0.65674 | 0.49765 | 0.31266 | 0.12424 | -0.048196 | -0.20874 | -0.36241 | -0.49987 | -0.61995 | -0.70407 | -0.74208 | -0.73268 | -0.67184 | -0.5745 | -0.43873 | -0.27113 | -0.077702 | 0.12914 | 0.33182 | 0.50992 | 0.65712 | 0.77044 | 0.84095 | 0.86402 | 0.84485 | -0.0024299 | 0.0037107 | 0.00018553 | 0.00018553 | 0 | 0 | 0.0020291 | 0.05 | 0.36474 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.63545 | 0.62912 | 0.62597 | 0.62727 | 0.63424 | 0.64352 | 0.67269 | 0.7225 | 0.78247 | 0.84648 | 0.90921 | 0.97207 | 0.9688 | 0.92058 | 0.88098 | 0.85339 | 0.83823 | 0.83422 | 0.84031 | 0.85467 | 0.88105 | 0.9144 | 0.95785 | 0.99069 | 0.93206 | 0.87388 | 0.82428 | 0.78958 | 0.76717 | 0.75299 | 0.74309 | 0.99069 | 23 | Slope | 0.26667 | 0.54515 | 0.54304 | 0.53088 | 0.5202 | 0.51141 | 0.50339 | 0.50201 | 0.5075 | 0.51638 | 0.52661 | 0.5364 | 0.54624 | 0.53404 | 0.50686 | 0.48255 | 0.46224 | 0.44608 | 0.43363 | 0.42455 | 0.41822 | 0.41591 | 0.41591 | 0.41928 | 0.41912 | 0.38846 | 0.35796 | 0.33032 | 0.30764 | 0.28906 | 0.27322 | 0.25881 | 0.54624 | 11 | 0.97207 | Slope | 0.66667 | 0.048599 |  | 0.75944 | 0 | 0.97207 | Slope | 2 | 0.66667 | 0 | 20 | -20 | 0.00032697 | 9.6158e-05 | 0.0020291
233 | 0:39 | -4.8599 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.4084 | -0.044084 | -0.044084 | -4.8599 | 0.00022572 | [13 empty] | 0.97823 | 1 | 0.9774 | 0.9262 | 0.85403 | 0.75001 | 0.60647 | 0.42632 | 0.23506 | 0.05521 | -0.11379 | -0.27675 | -0.42844 | -0.56659 | -0.67294 | -0.73274 | -0.7451 | -0.714 | -0.64144 | -0.52981 | -0.38353 | -0.2097 | -0.015098 | 0.18705 | 0.37728 | 0.54524 | 0.68551 | 0.79185 | 0.85464 | 0.87222 | 0.84937 | -0.0022042 | 0.0037422 | 0.00018711 | 0.00018711 | 0 | 0 | 0.002036 | 0.05 | 0.37107 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.62912 | 0.62597 | 0.62727 | 0.63424 | 0.64352 | 0.67269 | 0.7225 | 0.78247 | 0.84648 | 0.90922 | 0.97207 | 0.9688 | 0.92058 | 0.88098 | 0.85338 | 0.83823 | 0.83421 | 0.8403 | 0.85467 | 0.88105 | 0.9144 | 0.95785 | 0.99069 | 0.93206 | 0.87388 | 0.82429 | 0.78958 | 0.76717 | 0.75299 | 0.74309 | 0.73641 | 0.99069 | 22 | Slope | 0.3 | 0.54304 | 0.54199 | 0.53131 | 0.52252 | 0.51451 | 0.51312 | 0.51861 | 0.52749 | 0.53772 | 0.54752 | 0.55736 | 0.54515 | 0.51797 | 0.49366 | 0.47335 | 0.45719 | 0.44474 | 0.43566 | 0.42934 | 0.42702 | 0.42702 | 0.43039 | 0.43023 | 0.39957 | 0.36907 | 0.34143 | 0.31875 | 0.30017 | 0.28433 | 0.26992 | 0.25658 | 0.55736 | 10 | 0.97207 | Slope | 0.7 | 0.044084 |  | 0.78178 | 0 | 0.97207 | Slope | 2 | 0.7 | 0 | 20 | -20 | 0.00022572 | 9.4211e-05 | 0.002036
234 | 0:39 | -4.4084 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.1199 | -0.041199 | -0.041199 | -4.4084 | 0.00014426 | [13 empty] | 0.9774 | 1 | 0.9762 | 0.92105 | 0.83532 | 0.71292 | 0.54917 | 0.36163 | 0.17798 | 0.0017414 | -0.17033 | -0.33459 | -0.49051 | -0.61984 | -0.70637 | -0.74351 | -0.73556 | -0.69259 | -0.60654 | -0.48467 | -0.33204 | -0.15611 | 0.035129 | 0.2259 | 0.4067 | 0.57006 | 0.70673 | 0.80799 | 0.86619 | 0.88111 | 0.85556 | -0.00206 | 0.0037292 | 0.00018646 | 0.00018646 | 0 | 0 | 0.0020337 | 0.05 | 0.37422 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.62597 | 0.62727 | 0.63424 | 0.64352 | 0.67269 | 0.7225 | 0.78247 | 0.84648 | 0.90922 | 0.97207 | 0.9688 | 0.92058 | 0.88098 | 0.85338 | 0.83823 | 0.83422 | 0.8403 | 0.85467 | 0.88105 | 0.9144 | 0.95785 | 0.99069 | 0.93206 | 0.87388 | 0.82429 | 0.78958 | 0.76717 | 0.75299 | 0.74309 | 0.73641 | 0.73231 | 0.99069 | 21 | Slope | 0.33333 | 0.54199 | 0.54242 | 0.53363 | 0.52562 | 0.52423 | 0.52972 | 0.5386 | 0.54883 | 0.55863 | 0.56847 | 0.55627 | 0.52908 | 0.50477 | 0.48446 | 0.4683 | 0.45585 | 0.44677 | 0.44045 | 0.43813 | 0.43813 | 0.44151 | 0.44134 | 0.41069 | 0.38018 | 0.35254 | 0.32986 | 0.31128 | 0.29544 | 0.28103 | 0.26769 | 0.25521 | 0.56847 | 9 | 0.97207 | Slope | 0.73333 | 0.041199 |  | 0.79606 | 0 | 0.97207 | Slope | 2 | 0.73333 | 0 | 20 | -20 | 0.00014426 | 9.2079e-05 | 0.0020337
235 | 0:39 | -4.1199 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.9077 | -0.029077 | -0.029077 | -4.1199 | 0.00060611 | [13 empty] | 0.9762 | 1 | 0.97503 | 0.91035 | 0.81064 | 0.66953 | 0.49755 | 0.31668 | 0.13686 | -0.043003 | -0.21964 | -0.39171 | -0.54402 | -0.6584 | -0.72559 | -0.74383 | -0.72375 | -0.66796 | -0.57253 | -0.44427 | -0.28896 | -0.11518 | 0.065984 | 0.24826 | 0.42673 | 0.58997 | 0.72448 | 0.82227 | 0.87923 | 0.89233 | 0.86027 | -0.0014539 | 0.0036595 | 0.00018297 | 0.00018297 | 0 | 0 | 0.0020239 | 0.05 | 0.37292 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.62727 | 0.63423 | 0.64352 | 0.67268 | 0.7225 | 0.78247 | 0.84648 | 0.90921 | 0.97206 | 0.9688 | 0.92058 | 0.88098 | 0.85339 | 0.83823 | 0.83422 | 0.84031 | 0.85468 | 0.88105 | 0.91441 | 0.95785 | 0.99068 | 0.93205 | 0.87388 | 0.82428 | 0.78958 | 0.76717 | 0.75299 | 0.74308 | 0.73641 | 0.73231 | 0.73458 | 0.99068 | 20 | Slope | 0.36667 | 0.54242 | 0.54474 | 0.53673 | 0.53534 | 0.54083 | 0.54971 | 0.55994 | 0.56974 | 0.57958 | 0.56738 | 0.54019 | 0.51588 | 0.49557 | 0.47941 | 0.46696 | 0.45788 | 0.45156 | 0.44924 | 0.44925 | 0.45262 | 0.45245 | 0.4218 | 0.39129 | 0.36365 | 0.34097 | 0.32239 | 0.30655 | 0.29214 | 0.2788 | 0.26632 | 0.25597 | 0.57958 | 8 | 0.97206 | Slope | 0.76667 | 0.029077 |  | 0.85607 | 0 | 0.97206 | Slope | 2 | 0.76667 | 0 | 20 | -20 | 0.00060611 | 8.9666e-05 | 0.0020239
236 | 0:39 | -2.9077 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.4148 | -0.044148 | -0.044148 | -2.9077 | 0.00075356 | [13 empty] | 0.97503 | 1 | 0.9746 | 0.90567 | 0.79104 | 0.6417 | 0.47598 | 0.30188 | 0.12058 | -0.066713 | -0.25416 | -0.42945 | -0.5747 | -0.67642 | -0.72969 | -0.73896 | -0.71103 | -0.6484 | -0.54981 | -0.42051 | -0.26795 | -0.10308 | 0.071161 | 0.25411 | 0.43622 | 0.60057 | 0.73328 | 0.83137 | 0.88779 | 0.89693 | 0.85734 | -0.0022074 | 0.0035667 | 0.00017833 | 0.00017833 | 0 | 0 | 0.0020189 | 0.05 | 0.36595 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.63423 | 0.64351 | 0.67268 | 0.72249 | 0.78247 | 0.84648 | 0.90921 | 0.97206 | 0.96881 | 0.92059 | 0.88099 | 0.85339 | 0.83824 | 0.83422 | 0.84031 | 0.85468 | 0.88106 | 0.91441 | 0.95786 | 0.99068 | 0.93205 | 0.87387 | 0.82428 | 0.78957 | 0.76716 | 0.75298 | 0.74308 | 0.7364 | 0.7323 | 0.73457 | 0.74977 | 0.99068 | 19 | Slope | 0.4 | 0.54474 | 0.54784 | 0.54645 | 0.55194 | 0.56082 | 0.57105 | 0.58085 | 0.59069 | 0.57849 | 0.55131 | 0.527 | 0.50669 | 0.49052 | 0.47807 | 0.46899 | 0.46267 | 0.46035 | 0.46036 | 0.46373 | 0.46356 | 0.4329 | 0.4024 | 0.37476 | 0.35208 | 0.3335 | 0.31766 | 0.30325 | 0.28991 | 0.27743 | 0.26708 | 0.26103 | 0.59069 | 7 | 0.97206 | Slope | 0.8 | 0.044148 |  | 0.78147 | 0 | 0.97206 | Slope | 2 | 0.8 | 0 | 20 | -20 | 0.00075356 | 8.6929e-05 | 0.0020189
237 | 0:39 | -4.4148 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.7794 | -0.057794 | -0.057794 | -4.4148 | 0.0006823 | [13 empty] | 0.9746 | 1 | 0.97249 | 0.89334 | 0.77262 | 0.62769 | 0.4637 | 0.28246 | 0.087755 | -0.11713 | -0.31357 | -0.48556 | -0.61949 | -0.7049 | -0.74326 | -0.74035 | -0.70875 | -0.64027 | -0.53983 | -0.41234 | -0.2672 | -0.10638 | 0.073946 | 0.26703 | 0.45461 | 0.61753 | 0.75325 | 0.85253 | 0.90494 | 0.90858 | 0.86137 | -0.0028897 | 0.003275 | 0.00016375 | 0.00016375 | 0 | 0 | 0.0020036 | 0.05 | 0.35667 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.6435 | 0.67266 | 0.72248 | 0.78245 | 0.84646 | 0.90919 | 0.97204 | 0.96882 | 0.9206 | 0.881 | 0.85341 | 0.83825 | 0.83424 | 0.84033 | 0.8547 | 0.88107 | 0.91443 | 0.95787 | 0.99067 | 0.93203 | 0.87386 | 0.82426 | 0.78956 | 0.76715 | 0.75297 | 0.74307 | 0.73639 | 0.73229 | 0.73456 | 0.74975 | 0.77817 | 0.99067 | 18 | Slope | 0.43333 | 0.54783 | 0.55755 | 0.56305 | 0.57193 | 0.58215 | 0.59195 | 0.60179 | 0.58961 | 0.56242 | 0.53811 | 0.5178 | 0.50164 | 0.48919 | 0.48011 | 0.47379 | 0.47147 | 0.47148 | 0.47485 | 0.47467 | 0.44401 | 0.41351 | 0.38587 | 0.36319 | 0.3446 | 0.32877 | 0.31436 | 0.30102 | 0.28854 | 0.27819 | 0.27214 | 0.2705 | 0.60179 | 6 | 0.97204 | Slope | 0.83333 | 0.057794 |  | 0.71392 | 0 | 0.97204 | Slope | 2 | 0.83333 | 0 | 20 | -20 | 0.0006823 | 8.3771e-05 | 0.0020036
238 | 0:39 | -5.7794 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.6357 | -0.056357 | -0.056357 | -5.7794 | 7.1871e-05 | [13 empty] | 0.97249 | 1 | 0.96921 | 0.88752 | 0.7696 | 0.62136 | 0.44456 | 0.24363 | 0.024532 | -0.19563 | -0.39296 | -0.55547 | -0.67128 | -0.73625 | -0.75901 | -0.75681 | -0.71781 | -0.64785 | -0.54936 | -0.42805 | -0.28366 | -0.11053 | 0.086871 | 0.28987 | 0.47618 | 0.64484 | 0.78359 | 0.87935 | 0.9297 | 0.92793 | 0.87116 | -0.0028178 | 0.0027768 | 0.00013884 | 0.00013884 | 0 | 0 | 0.0019854 | 0.05 | 0.3275 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.67264 | 0.72246 | 0.78243 | 0.84644 | 0.90917 | 0.97202 | 0.96885 | 0.92063 | 0.88103 | 0.85343 | 0.83828 | 0.83426 | 0.84035 | 0.85472 | 0.8811 | 0.91445 | 0.9579 | 0.99064 | 0.93201 | 0.87383 | 0.82424 | 0.78953 | 0.76712 | 0.75294 | 0.74304 | 0.73636 | 0.73226 | 0.73453 | 0.74973 | 0.77815 | 0.82407 | 0.99064 | 17 | Slope | 0.46667 | 0.55755 | 0.57415 | 0.58303 | 0.59326 | 0.60306 | 0.6129 | 0.60073 | 0.57354 | 0.54923 | 0.52892 | 0.51276 | 0.50031 | 0.49123 | 0.48491 | 0.48259 | 0.48259 | 0.48597 | 0.48577 | 0.45511 | 0.42461 | 0.39697 | 0.37429 | 0.35571 | 0.33987 | 0.32546 | 0.31212 | 0.29964 | 0.28929 | 0.28324 | 0.2816 | 0.2858 | 0.6129 | 5 | 0.97202 | Slope | 0.86667 | 0.056357 |  | 0.72103 | 0 | 0.97202 | Slope | 2 | 0.86667 | 0 | 20 | -20 | 7.1871e-05 | 8.0738e-05 | 0.0019854
239 | 0:40 | -5.6357 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.2523 | -0.052523 | -0.052523 | -5.6357 | 0.00019168 | [13 empty] | 0.96921 | 1 | 0.96946 | 0.89045 | 0.77036 | 0.61097 | 0.41354 | 0.18735 | -0.05031 | -0.27501 | -0.46516 | -0.60995 | -0.70356 | -0.754 | -0.78106 | -0.77322 | -0.73492 | -0.66859 | -0.57613 | -0.45444 | -0.29527 | -0.10281 | 0.10497 | 0.30443 | 0.49538 | 0.66583 | 0.80087 | 0.89825 | 0.94685 | 0.93967 | 0.87886 | -0.0026262 | 0.0021771 | 0.00010886 | 0.00010886 | 0 | 0 | 0.0020017 | 0.05 | 0.27768 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.72243 | 0.7824 | 0.84641 | 0.90914 | 0.97199 | 0.96888 | 0.92066 | 0.88106 | 0.85346 | 0.83831 | 0.83429 | 0.84038 | 0.85475 | 0.88113 | 0.91448 | 0.95793 | 0.99061 | 0.93198 | 0.8738 | 0.82421 | 0.7895 | 0.76709 | 0.75291 | 0.74301 | 0.73633 | 0.73223 | 0.7345 | 0.7497 | 0.77812 | 0.82404 | 0.88864 | 0.99061 | 16 | Slope | 0.5 | 0.57414 | 0.59413 | 0.60436 | 0.61416 | 0.624 | 0.61185 | 0.58466 | 0.56035 | 0.54004 | 0.52388 | 0.51143 | 0.50235 | 0.49603 | 0.49371 | 0.49372 | 0.49709 | 0.49687 | 0.46622 | 0.43571 | 0.40807 | 0.38539 | 0.36681 | 0.35097 | 0.33656 | 0.32322 | 0.31074 | 0.30039 | 0.29434 | 0.29271 | 0.2969 | 0.30733 | 0.624 | 4 | 0.97199 | Slope | 0.9 | 0.052523 |  | 0.74001 | 0 | 0.97199 | Slope | 2 | 0.9 | 0 | 20 | -20 | 0.00019168 | 7.8661e-05 | 0.0020017
240 | 0:40 | -5.2523 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.4105 | -0.054105 | -0.054105 | -5.2523 | 7.9073e-05 | [13 empty] | 0.96946 | 1 | 0.97057 | 0.8912 | 0.76377 | 0.58562 | 0.36501 | 0.11894 | -0.1258 | -0.34509 | -0.51806 | -0.63977 | -0.71967 | -0.77536 | -0.79746 | -0.7906 | -0.75568 | -0.69421 | -0.60091 | -0.46458 | -0.28649 | -0.084631 | 0.11744 | 0.31932 | 0.50971 | 0.67519 | 0.81302 | 0.90979 | 0.95464 | 0.94492 | 0.88521 | -0.0027052 | 0.001537 | 7.6851e-05 | 7.6851e-05 | 0 | 0 | 0.0020507 | 0.05 | 0.21771 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.78236 | 0.84637 | 0.90911 | 0.97196 | 0.96891 | 0.92069 | 0.88109 | 0.85349 | 0.83834 | 0.83433 | 0.84041 | 0.85478 | 0.88116 | 0.91451 | 0.95796 | 0.99058 | 0.93195 | 0.87377 | 0.82418 | 0.78947 | 0.76706 | 0.75288 | 0.74298 | 0.7363 | 0.7322 | 0.73447 | 0.74966 | 0.77809 | 0.82401 | 0.88861 | 0.97167 | 0.99058 | 15 | Slope | 0.53333 | 0.59412 | 0.61546 | 0.62526 | 0.6351 | 0.62297 | 0.59579 | 0.57147 | 0.55116 | 0.535 | 0.52255 | 0.51347 | 0.50715 | 0.50483 | 0.50484 | 0.50821 | 0.50797 | 0.47732 | 0.44681 | 0.41917 | 0.39649 | 0.37791 | 0.36207 | 0.34766 | 0.33432 | 0.32184 | 0.31149 | 0.30544 | 0.30381 | 0.308 | 0.31843 | 0.335 | 0.6351 | 3 | 0.97196 | Slope | 0.93333 | 0.054105 |  | 0.73218 | 0 | 0.97196 | Slope | 2 | 0.93333 | 0 | 20 | -20 | 7.9073e-05 | 7.8336e-05 | 0.0020507
241 | 0:40 | -5.4105 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -6.6718 | -0.066718 | -0.066718 | -5.4105 | 0.00063067 | [13 empty] | 0.97057 | 1 | 0.97086 | 0.88745 | 0.74406 | 0.54461 | 0.30245 | 0.045766 | -0.19663 | -0.4005 | -0.55091 | -0.65832 | -0.7421 | -0.79118 | -0.81194 | -0.80547 | -0.77354 | -0.71211 | -0.60718 | -0.4537 | -0.26609 | -0.068624 | 0.13648 | 0.33843 | 0.52442 | 0.69247 | 0.82879 | 0.9197 | 0.9586 | 0.94623 | 0.88992 | -0.0033359 | 0.00090971 | 4.5486e-05 | 4.5486e-05 | 0 | 0 | 0.0020899 | 0.05 | 0.1537 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.84634 | 0.90907 | 0.97193 | 0.96894 | 0.92072 | 0.88112 | 0.85353 | 0.83837 | 0.83436 | 0.84045 | 0.85481 | 0.88119 | 0.91454 | 0.95799 | 0.99055 | 0.93192 | 0.87374 | 0.82414 | 0.78944 | 0.76703 | 0.75285 | 0.74295 | 0.73627 | 0.73217 | 0.73444 | 0.74963 | 0.77805 | 0.82398 | 0.88858 | 0.97164 | 0.93337 | 0.99055 | 14 | Slope | 0.56667 | 0.61545 | 0.63636 | 0.6462 | 0.63409 | 0.60691 | 0.5826 | 0.56229 | 0.54612 | 0.53367 | 0.52459 | 0.51827 | 0.51595 | 0.51596 | 0.51933 | 0.51907 | 0.48842 | 0.45791 | 0.43027 | 0.40759 | 0.38901 | 0.37317 | 0.35876 | 0.34542 | 0.33295 | 0.32259 | 0.31654 | 0.31491 | 0.3191 | 0.32953 | 0.3461 | 0.32224 | 0.6462 | 2 | 0.97193 | Slope | 0.96667 | 0.066718 |  | 0.66974 | 0 | 0.97193 | Slope | 2 | 0.96667 | 0 | 20 | -20 | 0.00063067 | 8.0434e-05 | 0.0020899
242 | 0:40 | -6.6718 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.7054 | -0.077054 | -0.077054 | -6.6718 | 0.00051677 | [13 empty] | 0.97086 | 1 | 0.96862 | 0.87273 | 0.70913 | 0.48651 | 0.22985 | -0.028565 | -0.2582 | -0.4402 | -0.57394 | -0.68471 | -0.75883 | -0.80379 | -0.82177 | -0.81766 | -0.78843 | -0.72031 | -0.60058 | -0.43653 | -0.24983 | -0.045616 | 0.16362 | 0.36389 | 0.55276 | 0.71879 | 0.846 | 0.92557 | 0.95498 | 0.94097 | 0.886 | -0.0038527 | 0.0002812 | 1.406e-05 | 1.406e-05 | 0 | 0 | 0.0020795 | 0.05 | 0.090971 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.90904 | 0.97189 | 0.96897 | 0.92075 | 0.88115 | 0.85356 | 0.8384 | 0.83439 | 0.84048 | 0.85485 | 0.88122 | 0.91458 | 0.95802 | 0.99052 | 0.93188 | 0.87371 | 0.82411 | 0.78941 | 0.767 | 0.75282 | 0.74292 | 0.73624 | 0.73214 | 0.73441 | 0.7496 | 0.77802 | 0.82395 | 0.88855 | 0.97161 | 0.93341 | 0.83204 | 0.99052 | 13 | Slope | 0.6 | 0.63635 | 0.6573 | 0.64521 | 0.61803 | 0.59372 | 0.57341 | 0.55724 | 0.5448 | 0.53571 | 0.52939 | 0.52707 | 0.52708 | 0.53045 | 0.53017 | 0.49952 | 0.46901 | 0.44137 | 0.41869 | 0.40011 | 0.38427 | 0.36986 | 0.35652 | 0.34405 | 0.33369 | 0.32764 | 0.32601 | 0.33021 | 0.34063 | 0.3572 | 0.33336 | 0.28846 | 0.6573 | 1 | 0.97189 | Slope | 1 | 0.077054 |  | 0.61858 | 0 | 0.97189 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00051677 | 8.5202e-05 | 0.0020795
243 | 0:40 | -7.7054 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.6238 | -0.076238 | -0.076238 | -7.7054 | 4.0788e-05 | [13 empty] | 0.96862 | 1 | 0.96314 | 0.85154 | 0.66609 | 0.42649 | 0.16367 | -0.086182 | -0.29678 | -0.46124 | -0.59882 | -0.69803 | -0.76631 | -0.80648 | -0.82774 | -0.83093 | -0.80259 | -0.72477 | -0.59543 | -0.42954 | -0.23266 | -0.019915 | 0.19102 | 0.39488 | 0.58216 | 0.73723 | 0.84949 | 0.9146 | 0.93897 | 0.92438 | 0.87002 | -0.0038119 | -0.00031016 | -1.5508e-05 | -1.5508e-05 | 0 | 0 | 0.002016 | 0.05 | 0.02812 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.97186 | 0.969 | 0.92078 | 0.88118 | 0.85359 | 0.83843 | 0.83442 | 0.84051 | 0.85488 | 0.88125 | 0.91461 | 0.95805 | 0.99049 | 0.93185 | 0.87368 | 0.82408 | 0.78938 | 0.76697 | 0.75279 | 0.74289 | 0.73621 | 0.73211 | 0.73438 | 0.74957 | 0.77799 | 0.82392 | 0.88852 | 0.97158 | 0.93344 | 0.83207 | 0.73263 | 0.99049 | 12 | Slope | 0.63333 | 0.65729 | 0.65633 | 0.62915 | 0.60484 | 0.58453 | 0.56837 | 0.55592 | 0.54684 | 0.54051 | 0.5382 | 0.5382 | 0.54157 | 0.54127 | 0.51062 | 0.48011 | 0.45247 | 0.42979 | 0.41121 | 0.39537 | 0.38096 | 0.36763 | 0.35515 | 0.34479 | 0.33875 | 0.33711 | 0.34131 | 0.35173 | 0.3683 | 0.34448 | 0.29958 | 0.25532 | 0.65729 | 0 | 0.97186 | Slope | 1 | 0.076238 |  | 0.62262 | 0 | 0.97186 | Slope | 2 | 1 | 0 | 20 | -20 | 4.0788e-05 | 9.2361e-05 | 0.002016
244 | 0:40 | -7.6238 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.4973 | -0.074973 | -0.074973 | -7.6238 | 6.3265e-05 | [13 empty] | 0.96314 | 1 | 0.95738 | 0.83049 | 0.62959 | 0.38195 | 0.12408 | -0.11049 | -0.30434 | -0.47214 | -0.59747 | -0.68965 | -0.75166 | -0.79628 | -0.83014 | -0.84365 | -0.81405 | -0.73132 | -0.60046 | -0.42484 | -0.21842 | -0.0026017 | 0.21093 | 0.41257 | 0.58749 | 0.72561 | 0.82103 | 0.88038 | 0.90475 | 0.89189 | 0.84271 | -0.0037486 | -0.00079234 | -3.9617e-05 | -3.9617e-05 | 0 | 0 | 0.001932 | 0.05 | -0.031016 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.96902 | 0.92081 | 0.88121 | 0.85361 | 0.83845 | 0.83444 | 0.84053 | 0.8549 | 0.88128 | 0.91463 | 0.95808 | 0.99046 | 0.93183 | 0.87365 | 0.82406 | 0.78935 | 0.76694 | 0.75276 | 0.74286 | 0.73619 | 0.73208 | 0.73435 | 0.74955 | 0.77797 | 0.8239 | 0.88849 | 0.97155 | 0.93346 | 0.8321 | 0.73266 | 0.64149 | 0.99046 | 11 | Slope | 0.66667 | 0.65634 | 0.64027 | 0.61596 | 0.59565 | 0.57948 | 0.56704 | 0.55795 | 0.55163 | 0.54931 | 0.54932 | 0.55269 | 0.55238 | 0.52172 | 0.49122 | 0.46358 | 0.4409 | 0.42231 | 0.40648 | 0.39207 | 0.37873 | 0.36625 | 0.3559 | 0.34985 | 0.34821 | 0.35241 | 0.36283 | 0.37941 | 0.3556 | 0.3107 | 0.26644 | 0.22494 | 0.65634 | 0 | 0.96902 | Slope | 1 | 0.074973 |  | 0.62888 | 0 | 0.96902 | Slope | 2 | 1 | 0 | 20 | -20 | 6.3265e-05 | 0.00010123 | 0.001932
245 | 0:41 | -7.4973 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -6.5151 | -0.065151 | -0.065151 | -7.4973 | 0.00049109 | [13 empty] | 0.95738 | 1 | 0.95187 | 0.81466 | 0.60665 | 0.36228 | 0.11737 | -0.10077 | -0.29839 | -0.45352 | -0.57131 | -0.65655 | -0.72417 | -0.78556 | -0.83762 | -0.85791 | -0.82905 | -0.74708 | -0.60866 | -0.42412 | -0.21455 | 0.0024525 | 0.21294 | 0.40095 | 0.55732 | 0.6765 | 0.76489 | 0.82447 | 0.85257 | 0.84725 | 0.81193 | -0.0032575 | -0.0011883 | -5.9417e-05 | -5.9417e-05 | 0 | 0 | 0.0018387 | 0.05 | -0.079234 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.92083 | 0.88123 | 0.85363 | 0.83847 | 0.83446 | 0.84055 | 0.85492 | 0.8813 | 0.91465 | 0.9581 | 0.99044 | 0.93181 | 0.87363 | 0.82404 | 0.78933 | 0.76692 | 0.75274 | 0.74284 | 0.73617 | 0.73206 | 0.73434 | 0.74953 | 0.77795 | 0.82388 | 0.88847 | 0.97153 | 0.93348 | 0.83212 | 0.73267 | 0.64151 | 0.5627 | 0.99044 | 10 | Slope | 0.7 | 0.64028 | 0.62708 | 0.60677 | 0.5906 | 0.57815 | 0.56907 | 0.56275 | 0.56043 | 0.56044 | 0.56381 | 0.56348 | 0.53283 | 0.50232 | 0.47468 | 0.452 | 0.43342 | 0.41758 | 0.40317 | 0.38983 | 0.37735 | 0.367 | 0.36095 | 0.35932 | 0.36351 | 0.37394 | 0.39051 | 0.36672 | 0.32182 | 0.27756 | 0.23606 | 0.19868 | 0.64028 | 0 | 0.92083 | Slope | 1 | 0.065151 |  | 0.6775 | 0 | 0.92083 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00049109 | 0.00011106 | 0.0018387
246 | 0:41 | -6.5151 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.1758 | -0.051758 | -0.051758 | -6.5151 | 0.00066967 | [13 empty] | 0.95187 | 1 | 0.94881 | 0.80806 | 0.6038 | 0.37174 | 0.14363 | -0.076111 | -0.26016 | -0.40646 | -0.51596 | -0.6062 | -0.69228 | -0.77717 | -0.84264 | -0.86915 | -0.84409 | -0.75938 | -0.61612 | -0.43129 | -0.22427 | -0.012943 | 0.1821 | 0.35007 | 0.48609 | 0.59701 | 0.6854 | 0.74957 | 0.78605 | 0.79479 | 0.77915 | -0.0025879 | -0.0014643 | -7.3215e-05 | -7.3215e-05 | 0 | 0 | 0.0017666 | 0.05 | -0.11883 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.88124 | 0.85364 | 0.83849 | 0.83448 | 0.84056 | 0.85493 | 0.88131 | 0.91466 | 0.95811 | 0.99043 | 0.9318 | 0.87362 | 0.82403 | 0.78932 | 0.76691 | 0.75273 | 0.74283 | 0.73615 | 0.73205 | 0.73432 | 0.74951 | 0.77794 | 0.82386 | 0.88846 | 0.97152 | 0.93349 | 0.83213 | 0.73269 | 0.64153 | 0.56271 | 0.49816 | 0.99043 | 9 | Slope | 0.73333 | 0.62708 | 0.61788 | 0.60172 | 0.58927 | 0.58019 | 0.57387 | 0.57155 | 0.57155 | 0.57493 | 0.57459 | 0.54393 | 0.51343 | 0.48579 | 0.46311 | 0.44453 | 0.42869 | 0.41428 | 0.40094 | 0.38846 | 0.37811 | 0.37206 | 0.37042 | 0.37462 | 0.38504 | 0.40162 | 0.37783 | 0.33293 | 0.28867 | 0.24718 | 0.20979 | 0.17717 | 0.62708 | 0 | 0.88124 | Slope | 1 | 0.051758 |  | 0.7438 | 0 | 0.88124 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00066967 | 0.00012129 | 0.0017666
247 | 0:41 | -5.1758 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -3.8328 | -0.038328 | -0.038328 | -5.1758 | 0.00067148 | [13 empty] | 0.94881 | 1 | 0.9483 | 0.81156 | 0.61906 | 0.40431 | 0.17827 | -0.026343 | -0.19944 | -0.33534 | -0.44738 | -0.55486 | -0.6662 | -0.76809 | -0.8428 | -0.8744 | -0.8507 | -0.76552 | -0.62537 | -0.44729 | -0.24903 | -0.054699 | 0.11931 | 0.26595 | 0.39195 | 0.50139 | 0.59341 | 0.66463 | 0.71287 | 0.73853 | 0.74131 | -0.0019164 | -0.0016158 | -8.0792e-05 | -8.0792e-05 | 0 | 0 | 0.0017272 | 0.05 | -0.14643 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.85365 | 0.8385 | 0.83448 | 0.84057 | 0.85494 | 0.88132 | 0.91467 | 0.95812 | 0.99042 | 0.93179 | 0.87361 | 0.82402 | 0.78931 | 0.7669 | 0.75272 | 0.74282 | 0.73614 | 0.73204 | 0.73431 | 0.74951 | 0.77793 | 0.82385 | 0.88845 | 0.97151 | 0.9335 | 0.83214 | 0.7327 | 0.64153 | 0.56272 | 0.49817 | 0.44671 | 0.99042 | 8 | Slope | 0.76667 | 0.61788 | 0.61283 | 0.60038 | 0.5913 | 0.58498 | 0.58266 | 0.58267 | 0.58604 | 0.5857 | 0.55504 | 0.52454 | 0.4969 | 0.47421 | 0.45563 | 0.4398 | 0.42538 | 0.41205 | 0.39957 | 0.38922 | 0.38317 | 0.38153 | 0.38573 | 0.39615 | 0.41273 | 0.38894 | 0.34405 | 0.29979 | 0.25829 | 0.22091 | 0.18828 | 0.16001 | 0.61788 | 0 | 0.85365 | Slope | 1 | 0.038328 |  | 0.81028 | 0 | 0.85365 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00067148 | 0.00013151 | 0.0017272
248 | 0:41 | -3.8328 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.3516 | -0.023516 | -0.023516 | -3.8328 | 0.00074059 | [13 empty] | 0.9483 | 1 | 0.95059 | 0.82326 | 0.64708 | 0.43726 | 0.22742 | 0.035739 | -0.12476 | -0.2596 | -0.38556 | -0.51725 | -0.64662 | -0.75846 | -0.83743 | -0.8722 | -0.85034 | -0.76995 | -0.63913 | -0.47158 | -0.29053 | -0.11708 | 0.035388 | 0.1701 | 0.29242 | 0.40358 | 0.50018 | 0.57944 | 0.64 | 0.68005 | 0.69811 | -0.0011758 | -0.001656 | -8.2799e-05 | -8.2799e-05 | 0 | 0 | 0.0017173 | 0.05 | -0.16158 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.8385 | 0.83448 | 0.84057 | 0.85494 | 0.88132 | 0.91467 | 0.95812 | 0.99042 | 0.93179 | 0.87361 | 0.82402 | 0.78931 | 0.7669 | 0.75272 | 0.74282 | 0.73614 | 0.73204 | 0.73431 | 0.7495 | 0.77793 | 0.82385 | 0.88845 | 0.97151 | 0.9335 | 0.83214 | 0.7327 | 0.64154 | 0.56272 | 0.49817 | 0.44671 | 0.40737 | 0.99042 | 7 | Slope | 0.8 | 0.61283 | 0.61149 | 0.60241 | 0.59609 | 0.59377 | 0.59378 | 0.59715 | 0.59681 | 0.56615 | 0.53565 | 0.50801 | 0.48533 | 0.46674 | 0.45091 | 0.4365 | 0.42316 | 0.41068 | 0.40033 | 0.39428 | 0.39264 | 0.39684 | 0.40726 | 0.42384 | 0.40006 | 0.35516 | 0.3109 | 0.2694 | 0.23202 | 0.19939 | 0.17113 | 0.1469 | 0.61283 | 0 | 0.8385 | Slope | 1 | 0.023516 |  | 0.88359 | 0 | 0.8385 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00074059 | 0.00014146 | 0.0017173
249 | 0:41 | -2.3516 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -0.75958 | -0.0075958 | -0.0075958 | -2.3516 | 0.00079602 | [13 empty] | 0.95059 | 1 | 0.95443 | 0.83895 | 0.668 | 0.47304 | 0.27644 | 0.098501 | -0.056793 | -0.20032 | -0.34685 | -0.49543 | -0.63373 | -0.7476 | -0.82961 | -0.86635 | -0.84838 | -0.77677 | -0.65532 | -0.50219 | -0.33918 | -0.18538 | -0.04568 | 0.083567 | 0.20543 | 0.31796 | 0.41773 | 0.50313 | 0.57216 | 0.62239 | 0.65129 | -0.00037979 | -0.0015951 | -7.9754e-05 | -7.9754e-05 | 0 | 0 | 0.00173 | 0.05 | -0.1656 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.83448 | 0.84057 | 0.85494 | 0.88132 | 0.91467 | 0.95812 | 0.99042 | 0.93179 | 0.87361 | 0.82402 | 0.78931 | 0.7669 | 0.75272 | 0.74282 | 0.73615 | 0.73204 | 0.73431 | 0.74951 | 0.77793 | 0.82386 | 0.88845 | 0.97151 | 0.9335 | 0.83214 | 0.7327 | 0.64153 | 0.56272 | 0.49817 | 0.44671 | 0.40737 | 0.37889 | 0.99042 | 6 | Slope | 0.83333 | 0.61149 | 0.61352 | 0.6072 | 0.60488 | 0.60489 | 0.60826 | 0.60792 | 0.57726 | 0.54676 | 0.51912 | 0.49644 | 0.47786 | 0.46202 | 0.44761 | 0.43427 | 0.42179 | 0.41144 | 0.40539 | 0.40375 | 0.40795 | 0.41837 | 0.43495 | 0.41117 | 0.36627 | 0.32201 | 0.28051 | 0.24313 | 0.2105 | 0.18224 | 0.15801 | 0.13741 | 0.61352 | 1 | 0.84057 | Slope | 1 | 0.0075958 |  | 0.9624 | 0 | 0.84057 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00079602 | 0.00015095 | 0.00173
250 | 0:41 | -0.75958 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 0.83246 | 0.0083246 | 0.0083246 | -0.75958 | 0.00079602 | [13 empty] | 0.95443 | 1 | 0.95842 | 0.84504 | 0.68391 | 0.49921 | 0.31485 | 0.14537 | -0.012489 | -0.17101 | -0.33189 | -0.48781 | -0.62601 | -0.74219 | -0.82531 | -0.86334 | -0.85064 | -0.78399 | -0.67047 | -0.52888 | -0.38052 | -0.23841 | -0.10464 | 0.022672 | 0.14293 | 0.25372 | 0.35321 | 0.44064 | 0.51387 | 0.56986 | 0.60553 | 0.00041623 | -0.0014514 | -7.257e-05 | -7.257e-05 | 0 | 0 | 0.001751 | 0.05 | -0.15951 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.84056 | 0.85493 | 0.88131 | 0.91466 | 0.95811 | 0.99043 | 0.9318 | 0.87362 | 0.82403 | 0.78932 | 0.76691 | 0.75273 | 0.74283 | 0.73615 | 0.73205 | 0.73432 | 0.74951 | 0.77794 | 0.82386 | 0.88846 | 0.97152 | 0.93349 | 0.83213 | 0.73269 | 0.64153 | 0.56271 | 0.49816 | 0.4467 | 0.40736 | 0.37888 | 0.36019 | 0.99043 | 5 | Slope | 0.86667 | 0.61352 | 0.61831 | 0.61599 | 0.616 | 0.61937 | 0.61903 | 0.58838 | 0.55787 | 0.53023 | 0.50755 | 0.48897 | 0.47313 | 0.45872 | 0.44538 | 0.43291 | 0.42255 | 0.4165 | 0.41487 | 0.41907 | 0.42949 | 0.44606 | 0.42228 | 0.37738 | 0.33312 | 0.29162 | 0.25424 | 0.22161 | 0.19334 | 0.16912 | 0.14851 | 0.13118 | 0.61937 | 4 | 0.95811 | Slope | 0.9 | 0.0083246 |  | 0.95879 | 0 | 0.95811 | Slope | 2 | 0.9 | 0 | 20 | -20 | 0.00079602 | 0.00015984 | 0.001751
251 | 0:42 | 0.83246 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 0.8893 | 0.008893 | 0.008893 | 0.83246 | 2.8421e-05 | [13 empty] | 0.95842 | 1 | 0.95868 | 0.84971 | 0.69587 | 0.52178 | 0.348 | 0.17988 | 0.0095443 | -0.16338 | -0.3315 | -0.48546 | -0.62588 | -0.74266 | -0.82482 | -0.86615 | -0.85543 | -0.79159 | -0.68408 | -0.5524 | -0.41386 | -0.27748 | -0.14684 | -0.02379 | 0.090436 | 0.19533 | 0.29124 | 0.37755 | 0.45185 | 0.51063 | 0.55007 | 0.00044465 | -0.0011876 | -5.9381e-05 | -5.9381e-05 | 0 | 0 | 0.0017785 | 0.05 | -0.14514 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.85492 | 0.8813 | 0.91465 | 0.9581 | 0.99044 | 0.93181 | 0.87363 | 0.82404 | 0.78933 | 0.76692 | 0.75274 | 0.74284 | 0.73617 | 0.73206 | 0.73434 | 0.74953 | 0.77795 | 0.82388 | 0.88847 | 0.97153 | 0.93348 | 0.83212 | 0.73267 | 0.64151 | 0.5627 | 0.49815 | 0.44669 | 0.40734 | 0.37886 | 0.36018 | 0.34938 | 0.99044 | 4 | Slope | 0.9 | 0.61831 | 0.6271 | 0.62711 | 0.63048 | 0.63015 | 0.59949 | 0.56899 | 0.54135 | 0.51867 | 0.50009 | 0.48425 | 0.46984 | 0.4565 | 0.44402 | 0.43367 | 0.42762 | 0.42598 | 0.43018 | 0.4406 | 0.45718 | 0.43338 | 0.38848 | 0.34422 | 0.30273 | 0.26534 | 0.23272 | 0.20445 | 0.18023 | 0.15962 | 0.14228 | 0.12757 | 0.63048 | 3 | 0.9581 | Slope | 0.93333 | 0.008893 |  | 0.95598 | 0 | 0.9581 | Slope | 2 | 0.93333 | 0 | 20 | -20 | 2.8421e-05 | 0.00016809 | 0.0017785
252 | 0:42 | 0.8893 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.9482 | 0.019482 | 0.019482 | 0.8893 | 0.00052947 | [13 empty] | 0.95868 | 1 | 0.96166 | 0.85936 | 0.71608 | 0.55377 | 0.38356 | 0.20357 | 0.017949 | -0.16263 | -0.3275 | -0.48298 | -0.62299 | -0.73823 | -0.82547 | -0.87002 | -0.86317 | -0.80607 | -0.70982 | -0.59064 | -0.46085 | -0.32856 | -0.20166 | -0.08388 | 0.024574 | 0.12516 | 0.21872 | 0.30464 | 0.38027 | 0.44163 | 0.48417 | 0.00097412 | -0.0008541 | -4.2705e-05 | -4.2705e-05 | 0 | 0 | 0.0018276 | 0.05 | -0.11876 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.88128 | 0.91463 | 0.95808 | 0.99046 | 0.93183 | 0.87365 | 0.82406 | 0.78935 | 0.76694 | 0.75276 | 0.74286 | 0.73618 | 0.73208 | 0.73435 | 0.74954 | 0.77797 | 0.82389 | 0.88849 | 0.97155 | 0.93346 | 0.8321 | 0.73266 | 0.6415 | 0.56268 | 0.49813 | 0.44667 | 0.40733 | 0.37885 | 0.36016 | 0.34936 | 0.34353 | 0.99046 | 3 | Slope | 0.93333 | 0.62709 | 0.63821 | 0.64158 | 0.64126 | 0.61061 | 0.58011 | 0.55246 | 0.52978 | 0.5112 | 0.49536 | 0.48095 | 0.46762 | 0.45514 | 0.44478 | 0.43874 | 0.4371 | 0.4413 | 0.45172 | 0.46829 | 0.44449 | 0.39959 | 0.35533 | 0.31383 | 0.27645 | 0.24382 | 0.21556 | 0.19133 | 0.17073 | 0.15339 | 0.13868 | 0.12562 | 0.64158 | 2 | 0.95808 | Slope | 0.96667 | 0.019482 |  | 0.90356 | 0 | 0.95808 | Slope | 2 | 0.96667 | 0 | 20 | -20 | 0.00052947 | 0.00017551 | 0.0018276
253 | 0:42 | 1.9482 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.4453 | 0.024453 | 0.024453 | 1.9482 | 0.00024854 | [13 empty] | 0.96166 | 1 | 0.96383 | 0.86834 | 0.7358 | 0.57893 | 0.39881 | 0.20364 | 0.010418 | -0.16547 | -0.33166 | -0.48615 | -0.6231 | -0.7428 | -0.83169 | -0.87681 | -0.87225 | -0.82167 | -0.73537 | -0.62455 | -0.49923 | -0.37171 | -0.25209 | -0.14304 | -0.042145 | 0.052791 | 0.1428 | 0.22704 | 0.30274 | 0.36556 | 0.41037 | 0.0012227 | -0.00041964 | -2.0982e-05 | -2.0982e-05 | 0 | 0 | 0.0018858 | 0.05 | -0.08541 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.91461 | 0.95806 | 0.99048 | 0.93185 | 0.87367 | 0.82408 | 0.78937 | 0.76696 | 0.75278 | 0.74288 | 0.7362 | 0.7321 | 0.73437 | 0.74957 | 0.77799 | 0.82391 | 0.88851 | 0.97157 | 0.93344 | 0.83208 | 0.73264 | 0.64147 | 0.56266 | 0.49811 | 0.44665 | 0.40731 | 0.37883 | 0.36014 | 0.34934 | 0.34351 | 0.34598 | 0.99048 | 2 | Slope | 0.96667 | 0.6382 | 0.65269 | 0.65238 | 0.62173 | 0.59122 | 0.56358 | 0.5409 | 0.52232 | 0.50648 | 0.49207 | 0.47873 | 0.46626 | 0.4559 | 0.44986 | 0.44822 | 0.45242 | 0.46284 | 0.47941 | 0.45559 | 0.41069 | 0.36643 | 0.32494 | 0.28755 | 0.25493 | 0.22666 | 0.20244 | 0.18183 | 0.16449 | 0.14978 | 0.13673 | 0.12644 | 0.65269 | 1 | 0.95806 | Slope | 1 | 0.024453 |  | 0.87896 | 0 | 0.95806 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00024854 | 0.00018107 | 0.0018858
254 | 0:42 | 2.4453 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.786 | 0.02786 | 0.02786 | 2.4453 | 0.00017033 | [13 empty] | 0.96383 | 1 | 0.96645 | 0.87893 | 0.75167 | 0.58572 | 0.39058 | 0.18823 | 0.0013445 | -0.17497 | -0.33909 | -0.48939 | -0.63118 | -0.75233 | -0.84066 | -0.88575 | -0.88462 | -0.8418 | -0.76349 | -0.65693 | -0.53607 | -0.41612 | -0.30632 | -0.2064 | -0.11298 | -0.02353 | 0.062785 | 0.14521 | 0.22087 | 0.28392 | 0.37958 | 0.001393 | 9.4987e-05 | 4.7494e-06 | 4.7494e-06 | 0 | 0 | 0.001962 | 0.05 | -0.041964 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.95803 | 0.99051 | 0.93187 | 0.8737 | 0.8241 | 0.7894 | 0.76699 | 0.75281 | 0.74291 | 0.73623 | 0.73213 | 0.7344 | 0.74959 | 0.77801 | 0.82394 | 0.88854 | 0.9716 | 0.93342 | 0.83205 | 0.73261 | 0.64145 | 0.56263 | 0.49808 | 0.44662 | 0.40728 | 0.3788 | 0.36012 | 0.34932 | 0.34349 | 0.34595 | 0.39389 | 0.99051 | 1 | Slope | 1 | 0.65268 | 0.6635 | 0.63285 | 0.60234 | 0.5747 | 0.55202 | 0.53344 | 0.5176 | 0.50319 | 0.48985 | 0.47738 | 0.46702 | 0.46098 | 0.45934 | 0.46354 | 0.47396 | 0.49053 | 0.46669 | 0.4218 | 0.37754 | 0.33604 | 0.29866 | 0.26603 | 0.23776 | 0.21354 | 0.19293 | 0.17559 | 0.16088 | 0.14783 | 0.13754 | 0.14241 | 0.6635 | 1 | 0.99051 | Slope | 1 | 0.02786 |  | 0.86209 | 0 | 0.99051 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00017033 | 0.00018486 | 0.001962
255 | 0:42 | 2.786 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.8415 | 0.028415 | 0.028415 | 2.786 | 2.7742e-05 | [13 empty] | 0.96645 | 1 | 0.96942 | 0.88475 | 0.74789 | 0.56678 | 0.36491 | 0.17056 | -0.01543 | -0.18829 | -0.34718 | -0.50281 | -0.6461 | -0.76616 | -0.85265 | -0.89803 | -0.90145 | -0.86497 | -0.78958 | -0.68608 | -0.5721 | -0.46241 | -0.36286 | -0.27176 | -0.18526 | -0.10105 | -0.018089 | 0.062948 | 0.13689 | 0.25073 | 0.34179 | 0.0014207 | 0.0006813 | 3.4065e-05 | 3.4065e-05 | 0 | 0 | 0.00206 | 0.05 | 0.0094987 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.99054 | 0.9319 | 0.87373 | 0.82413 | 0.78943 | 0.76702 | 0.75284 | 0.74294 | 0.73626 | 0.73216 | 0.73443 | 0.74962 | 0.77804 | 0.82397 | 0.88857 | 0.97163 | 0.93339 | 0.83202 | 0.73258 | 0.64142 | 0.56261 | 0.49806 | 0.44659 | 0.40725 | 0.37877 | 0.36009 | 0.34929 | 0.34346 | 0.34592 | 0.39386 | 0.44729 | 0.99054 | 0 | Slope | 1 | 0.66351 | 0.64397 | 0.61346 | 0.58582 | 0.56314 | 0.54456 | 0.52872 | 0.51431 | 0.50098 | 0.4885 | 0.47814 | 0.4721 | 0.47046 | 0.47466 | 0.48508 | 0.50165 | 0.4778 | 0.4329 | 0.38864 | 0.34714 | 0.30976 | 0.27713 | 0.24886 | 0.22464 | 0.20403 | 0.1867 | 0.17198 | 0.15893 | 0.14864 | 0.15351 | 0.16021 | 0.66351 | 0 | 0.99054 | Slope | 1 | 0.028415 |  | 0.85935 | 0 | 0.99054 | Slope | 2 | 1 | 0 | 20 | -20 | 2.7742e-05 | 0.00018701 | 0.00206
256 | 0:42 | 2.8415 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.9495 | 0.029495 | 0.029495 | 2.8415 | 5.4009e-05 | [13 empty] | 0.96942 | 1 | 0.9694 | 0.87579 | 0.72442 | 0.53613 | 0.3412 | 0.1477 | -0.03494 | -0.20309 | -0.36777 | -0.52523 | -0.66721 | -0.78398 | -0.86789 | -0.91483 | -0.92236 | -0.88593 | -0.81 | -0.71023 | -0.60479 | -0.50501 | -0.41443 | -0.33055 | -0.24971 | -0.16931 | -0.088163 | -0.0097602 | 0.10951 | 0.21792 | 0.29462 | 0.0014747 | 0.0012631 | 6.3154e-05 | 6.3154e-05 | 0 | 0 | 0.0021555 | 0.05 | 0.06813 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.93193 | 0.87376 | 0.82416 | 0.78946 | 0.76705 | 0.75287 | 0.74296 | 0.73629 | 0.73219 | 0.73446 | 0.74965 | 0.77807 | 0.824 | 0.8886 | 0.97166 | 0.93336 | 0.83199 | 0.73255 | 0.64139 | 0.56258 | 0.49803 | 0.44656 | 0.40722 | 0.37874 | 0.36006 | 0.34926 | 0.34343 | 0.34589 | 0.39384 | 0.44727 | 0.50105 | 0.97166 | 14 | Slope | 0.56667 | 0.64398 | 0.62459 | 0.59694 | 0.57426 | 0.55568 | 0.53984 | 0.52543 | 0.5121 | 0.49962 | 0.48926 | 0.48322 | 0.48158 | 0.48578 | 0.4962 | 0.51277 | 0.4889 | 0.444 | 0.39974 | 0.35824 | 0.32086 | 0.28823 | 0.25997 | 0.23574 | 0.21514 | 0.1978 | 0.18309 | 0.17003 | 0.15974 | 0.16461 | 0.17131 | 0.17813 | 0.64398 | 0 | 0.93193 | Slope | 1 | 0.029495 |  | 0.854 | 0 | 0.93193 | Slope | 2 | 1 | 0 | 20 | -20 | 5.4009e-05 | 0.00018743 | 0.0021555
257 | 0:43 | 2.9495 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.1533 | 0.031533 | 0.031533 | 2.9495 | 0.00010189 | [13 empty] | 0.9694 | 1 | 0.96478 | 0.85976 | 0.70063 | 0.5155 | 0.3194 | 0.12697 | -0.05314 | -0.22698 | -0.39365 | -0.54936 | -0.68667 | -0.79864 | -0.88251 | -0.93227 | -0.93767 | -0.89725 | -0.82138 | -0.72763 | -0.63106 | -0.54004 | -0.45673 | -0.37855 | -0.30148 | -0.22264 | -0.14424 | -0.03299 | 0.082129 | 0.17924 | 0.25194 | 0.0015766 | 0.001759 | 8.795e-05 | 8.795e-05 | 0 | 0 | 0.0022144 | 0.05 | 0.12631 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.87378 | 0.82419 | 0.78948 | 0.76707 | 0.75289 | 0.74299 | 0.73631 | 0.73221 | 0.73448 | 0.74968 | 0.7781 | 0.82402 | 0.88862 | 0.97168 | 0.93333 | 0.83197 | 0.73253 | 0.64137 | 0.56255 | 0.498 | 0.44654 | 0.4072 | 0.37872 | 0.36003 | 0.34923 | 0.3434 | 0.34587 | 0.39381 | 0.44724 | 0.50103 | 0.56028 | 0.97168 | 13 | Slope | 0.6 | 0.62459 | 0.60806 | 0.58538 | 0.5668 | 0.55096 | 0.53655 | 0.52322 | 0.51074 | 0.50038 | 0.49434 | 0.4927 | 0.4969 | 0.50732 | 0.52389 | 0.5 | 0.4551 | 0.41084 | 0.36934 | 0.33196 | 0.29933 | 0.27107 | 0.24684 | 0.22624 | 0.2089 | 0.19419 | 0.18113 | 0.17084 | 0.17571 | 0.18241 | 0.18923 | 0.19787 | 0.62459 | 0 | 0.87378 | Slope | 1 | 0.031533 |  | 0.84391 | 0 | 0.87378 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00010189 | 0.00018611 | 0.0022144
258 | 0:43 | 3.1533 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.357 | 0.03357 | 0.03357 | 3.1533 | 0.00010189 | [13 empty] | 0.96478 | 1 | 0.96093 | 0.85029 | 0.69095 | 0.50292 | 0.30535 | 0.11324 | -0.070798 | -0.24528 | -0.40826 | -0.55703 | -0.68728 | -0.79877 | -0.88562 | -0.93322 | -0.93359 | -0.89149 | -0.82028 | -0.73502 | -0.64757 | -0.56452 | -0.4876 | -0.41368 | -0.33827 | -0.26262 | -0.17031 | -0.061781 | 0.046824 | 0.14228 | 0.22241 | 0.0016785 | 0.0021061 | 0.0001053 | 0.0001053 | 0 | 0 | 0.0022276 | 0.05 | 0.1759 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.8242 | 0.7895 | 0.76709 | 0.75291 | 0.74301 | 0.73633 | 0.73223 | 0.7345 | 0.74969 | 0.77811 | 0.82404 | 0.88864 | 0.9717 | 0.93331 | 0.83195 | 0.73251 | 0.64135 | 0.56253 | 0.49798 | 0.44652 | 0.40718 | 0.3787 | 0.36002 | 0.34922 | 0.34339 | 0.34585 | 0.39379 | 0.44722 | 0.50101 | 0.56026 | 0.62604 | 0.9717 | 12 | Slope | 0.63333 | 0.60807 | 0.5965 | 0.57792 | 0.56208 | 0.54767 | 0.53433 | 0.52185 | 0.5115 | 0.50545 | 0.50382 | 0.50801 | 0.51844 | 0.53501 | 0.5111 | 0.46621 | 0.42195 | 0.38045 | 0.34307 | 0.31044 | 0.28217 | 0.25795 | 0.23734 | 0.22001 | 0.20529 | 0.19224 | 0.18195 | 0.18682 | 0.19352 | 0.20034 | 0.20898 | 0.21979 | 0.60807 | 0 | 0.8242 | Slope | 1 | 0.03357 |  | 0.83383 | 0 | 0.8242 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00010189 | 0.00018323 | 0.0022276
259 | 0:43 | 3.357 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.2102 | 0.032102 | 0.032102 | 3.357 | 7.343e-05 | [13 empty] | 0.96093 | 1 | 0.95938 | 0.848 | 0.68617 | 0.49612 | 0.29837 | 0.1049 | -0.077591 | -0.24576 | -0.39921 | -0.53839 | -0.66682 | -0.7809 | -0.86637 | -0.90968 | -0.90855 | -0.87119 | -0.80905 | -0.73404 | -0.65598 | -0.58077 | -0.50936 | -0.43797 | -0.367 | -0.29468 | -0.20582 | -0.10188 | 0.0049512 | 0.10613 | 0.19418 | 0.0016051 | 0.0023302 | 0.00011651 | 0.00011651 | 0 | 0 | 0.0022202 | 0.05 | 0.21061 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.78951 | 0.7671 | 0.75292 | 0.74302 | 0.73634 | 0.73224 | 0.73451 | 0.7497 | 0.77813 | 0.82405 | 0.88865 | 0.97171 | 0.9333 | 0.83194 | 0.7325 | 0.64134 | 0.56252 | 0.49797 | 0.44651 | 0.40717 | 0.37869 | 0.36001 | 0.34921 | 0.34338 | 0.34584 | 0.39378 | 0.44721 | 0.501 | 0.56025 | 0.62603 | 0.68543 | 0.97171 | 11 | Slope | 0.66667 | 0.5965 | 0.58903 | 0.5732 | 0.55878 | 0.54545 | 0.53297 | 0.52261 | 0.51657 | 0.51493 | 0.51913 | 0.52955 | 0.54613 | 0.52221 | 0.47731 | 0.43306 | 0.39156 | 0.35417 | 0.32155 | 0.29328 | 0.26906 | 0.24845 | 0.23111 | 0.2164 | 0.20335 | 0.19306 | 0.19793 | 0.20463 | 0.21144 | 0.22008 | 0.2309 | 0.23959 | 0.5965 | 0 | 0.78951 | Slope | 1 | 0.032102 |  | 0.8411 | 0 | 0.78951 | Slope | 2 | 1 | 0 | 20 | -20 | 7.343e-05 | 0.00017914 | 0.0022202
260 | 0:43 | 3.2102 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.6445 | 0.026445 | 0.026445 | 3.2102 | 0.00028284 | [13 empty] | 0.95938 | 1 | 0.95927 | 0.8467 | 0.68347 | 0.4934 | 0.29571 | 0.1048 | -0.070417 | -0.22811 | -0.37072 | -0.50639 | -0.63618 | -0.74913 | -0.83082 | -0.87239 | -0.87528 | -0.84659 | -0.79494 | -0.73007 | -0.66084 | -0.59215 | -0.52413 | -0.45822 | -0.40122 | -0.33373 | -0.25013 | -0.15051 | -0.041216 | 0.070378 | 0.16883 | 0.0013223 | 0.002472 | 0.0001236 | 0.0001236 | 0 | 0 | 0.0022107 | 0.05 | 0.23302 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.76711 | 0.75293 | 0.74303 | 0.73635 | 0.73225 | 0.73452 | 0.74971 | 0.77813 | 0.82406 | 0.88866 | 0.97172 | 0.9333 | 0.83193 | 0.73249 | 0.64133 | 0.56252 | 0.49797 | 0.4465 | 0.40716 | 0.37868 | 0.36 | 0.3492 | 0.34337 | 0.34583 | 0.39377 | 0.44721 | 0.50099 | 0.56024 | 0.62602 | 0.68542 | 0.72697 | 0.97172 | 10 | Slope | 0.7 | 0.58904 | 0.58431 | 0.5699 | 0.55656 | 0.54408 | 0.53373 | 0.52768 | 0.52604 | 0.53024 | 0.54066 | 0.55724 | 0.53332 | 0.48842 | 0.44416 | 0.40267 | 0.36528 | 0.33266 | 0.30439 | 0.28017 | 0.25956 | 0.24222 | 0.22751 | 0.21446 | 0.20417 | 0.20904 | 0.21574 | 0.22255 | 0.23119 | 0.24201 | 0.2507 | 0.25343 | 0.58904 | 0 | 0.76711 | Slope | 1 | 0.026445 |  | 0.8691 | 0 | 0.76711 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00028284 | 0.00017408 | 0.0022107
261 | 0:43 | 2.6445 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.6115 | 0.026115 | 0.026115 | 2.6445 | 1.6486e-05 | [13 empty] | 0.95927 | 1 | 0.95881 | 0.84532 | 0.68168 | 0.49069 | 0.29415 | 0.10857 | -0.057965 | -0.20574 | -0.34374 | -0.47941 | -0.60773 | -0.71648 | -0.79487 | -0.83798 | -0.84721 | -0.82739 | -0.78506 | -0.72881 | -0.66621 | -0.60121 | -0.53888 | -0.48963 | -0.43827 | -0.37759 | -0.30186 | -0.20411 | -0.084693 | 0.043038 | 0.15062 | 0.0013058 | 0.002571 | 0.00012855 | 0.00012855 | 0 | 0 | 0.0022049 | 0.05 | 0.2472 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.75293 | 0.74303 | 0.73635 | 0.73225 | 0.73452 | 0.74972 | 0.77814 | 0.82406 | 0.88866 | 0.97172 | 0.93329 | 0.83193 | 0.73249 | 0.64133 | 0.56251 | 0.49796 | 0.4465 | 0.40716 | 0.37868 | 0.35999 | 0.34919 | 0.34336 | 0.34583 | 0.39377 | 0.4472 | 0.50099 | 0.56024 | 0.62602 | 0.68542 | 0.72697 | 0.7529 | 0.97172 | 9 | Slope | 0.73333 | 0.58431 | 0.58101 | 0.56767 | 0.5552 | 0.54484 | 0.53879 | 0.53716 | 0.54135 | 0.55178 | 0.56835 | 0.54443 | 0.49953 | 0.45527 | 0.41378 | 0.37639 | 0.34376 | 0.3155 | 0.29127 | 0.27067 | 0.25333 | 0.23862 | 0.22557 | 0.21528 | 0.22015 | 0.22684 | 0.23366 | 0.2423 | 0.25312 | 0.26181 | 0.26454 | 0.26208 | 0.58431 | 0 | 0.75293 | Slope | 1 | 0.026115 |  | 0.87073 | 0 | 0.75293 | Slope | 2 | 1 | 0 | 20 | -20 | 1.6486e-05 | 0.00016818 | 0.0022049
262 | 0:43 | 2.6115 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.4773 | 0.024773 | 0.024773 | 2.6115 | 6.7146e-05 | [13 empty] | 0.95881 | 1 | 0.95853 | 0.84493 | 0.68066 | 0.49058 | 0.29904 | 0.12212 | -0.033604 | -0.17459 | -0.31082 | -0.44534 | -0.57073 | -0.6769 | -0.75644 | -0.80496 | -0.82237 | -0.81169 | -0.7783 | -0.72927 | -0.67093 | -0.61243 | -0.57272 | -0.53022 | -0.48716 | -0.43871 | -0.37204 | -0.26718 | -0.12527 | 0.020156 | 0.13575 | 0.0012386 | 0.0026378 | 0.00013189 | 0.00013189 | 0 | 0 | 0.0021998 | 0.05 | 0.2571 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.74303 | 0.73636 | 0.73226 | 0.73453 | 0.74972 | 0.77814 | 0.82407 | 0.88867 | 0.97172 | 0.93329 | 0.83193 | 0.73248 | 0.64132 | 0.56251 | 0.49796 | 0.44649 | 0.40715 | 0.37867 | 0.35999 | 0.34919 | 0.34336 | 0.34582 | 0.39377 | 0.4472 | 0.50098 | 0.56023 | 0.62601 | 0.68541 | 0.72696 | 0.75289 | 0.77446 | 0.97172 | 8 | Slope | 0.76667 | 0.58101 | 0.57879 | 0.56631 | 0.55595 | 0.54991 | 0.54827 | 0.55247 | 0.56289 | 0.57946 | 0.55554 | 0.51064 | 0.46638 | 0.42489 | 0.3875 | 0.35487 | 0.32661 | 0.30238 | 0.28178 | 0.26444 | 0.24973 | 0.23668 | 0.22639 | 0.23126 | 0.23795 | 0.24477 | 0.25341 | 0.26423 | 0.27292 | 0.27565 | 0.27319 | 0.26927 | 0.58101 | 0 | 0.74303 | Slope | 1 | 0.024773 |  | 0.87738 | 0 | 0.74303 | Slope | 2 | 1 | 0 | 20 | -20 | 6.7146e-05 | 0.00016149 | 0.0021998
263 | 0:44 | 2.4773 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.7866 | 0.017866 | 0.017866 | 2.4773 | 0.00034534 | [13 empty] | 0.95853 | 1 | 0.95866 | 0.8444 | 0.68027 | 0.49409 | 0.31049 | 0.14487 | -0.0018553 | -0.13924 | -0.27457 | -0.40742 | -0.53102 | -0.6379 | -0.72154 | -0.77693 | -0.80264 | -0.80061 | -0.77462 | -0.73021 | -0.67897 | -0.64742 | -0.61549 | -0.58239 | -0.55503 | -0.52235 | -0.45403 | -0.3232 | -0.15589 | 0.0014233 | 0.12312 | 0.00089329 | 0.0026788 | 0.00013394 | 0.00013394 | 0 | 0 | 0.0021963 | 0.05 | 0.26378 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.73636 | 0.73226 | 0.73453 | 0.74972 | 0.77814 | 0.82407 | 0.88867 | 0.97173 | 0.93329 | 0.83192 | 0.73248 | 0.64132 | 0.56251 | 0.49796 | 0.44649 | 0.40715 | 0.37867 | 0.35999 | 0.34919 | 0.34336 | 0.34582 | 0.39376 | 0.44719 | 0.50098 | 0.56023 | 0.62601 | 0.68541 | 0.72696 | 0.75289 | 0.77446 | 0.80053 | 0.97173 | 7 | Slope | 0.8 | 0.57879 | 0.57742 | 0.56707 | 0.56102 | 0.55938 | 0.56358 | 0.574 | 0.59058 | 0.56665 | 0.52175 | 0.47749 | 0.436 | 0.39861 | 0.36599 | 0.33772 | 0.31349 | 0.29289 | 0.27555 | 0.26084 | 0.24779 | 0.2375 | 0.24237 | 0.24906 | 0.25588 | 0.26452 | 0.27534 | 0.28403 | 0.28676 | 0.2843 | 0.28038 | 0.27795 | 0.59058 | 7 | 0.97173 | Slope | 0.8 | 0.017866 |  | 0.91156 | 0 | 0.97173 | Slope | 2 | 0.8 | 0 | 20 | -20 | 0.00034534 | 0.00015411 | 0.0021963
264 | 0:44 | 1.7866 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.0116 | 0.010116 | 0.010116 | 1.7866 | 0.00038747 | [13 empty] | 0.95866 | 1 | 0.95775 | 0.84248 | 0.6802 | 0.50013 | 0.32721 | 0.17193 | 0.030152 | -0.10603 | -0.23975 | -0.37014 | -0.4925 | -0.60083 | -0.68865 | -0.75015 | -0.78304 | -0.78773 | -0.76634 | -0.72898 | -0.70802 | -0.68414 | -0.66119 | -0.64447 | -0.63661 | -0.60702 | -0.51294 | -0.3521 | -0.17058 | -0.0070108 | 0.12333 | 0.00050581 | 0.0026561 | 0.0001328 | 0.0001328 | 0 | 0 | 0.0021981 | 0.05 | 0.26788 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.73226 | 0.73453 | 0.74972 | 0.77814 | 0.82407 | 0.88867 | 0.97172 | 0.93329 | 0.83193 | 0.73248 | 0.64132 | 0.56251 | 0.49796 | 0.44649 | 0.40715 | 0.37867 | 0.35999 | 0.34919 | 0.34336 | 0.34582 | 0.39377 | 0.4472 | 0.50098 | 0.56023 | 0.62601 | 0.68541 | 0.72696 | 0.75289 | 0.77446 | 0.80053 | 0.82938 | 0.97172 | 6 | Slope | 0.83333 | 0.57742 | 0.57818 | 0.57213 | 0.57049 | 0.57469 | 0.58511 | 0.60169 | 0.57776 | 0.53286 | 0.48861 | 0.44711 | 0.40972 | 0.3771 | 0.34883 | 0.32461 | 0.304 | 0.28666 | 0.27195 | 0.2589 | 0.24861 | 0.25348 | 0.26018 | 0.26699 | 0.27563 | 0.28645 | 0.29514 | 0.29788 | 0.29541 | 0.29149 | 0.28906 | 0.28757 | 0.60169 | 6 | 0.97172 | Slope | 0.83333 | 0.010116 |  | 0.94992 | 0 | 0.97172 | Slope | 2 | 0.83333 | 0 | 20 | -20 | 0.00038747 | 0.00014619 | 0.0021981
265 | 0:44 | 1.0116 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 0.12877 | 0.0012877 | 0.0012877 | 1.0116 | 0.00044143 | [13 empty] | 0.95775 | 1 | 0.95772 | 0.84451 | 0.68856 | 0.52006 | 0.35928 | 0.21062 | 0.070724 | -0.063588 | -0.19416 | -0.32163 | -0.44304 | -0.55289 | -0.64445 | -0.71139 | -0.75014 | -0.7595 | -0.74522 | -0.74726 | -0.73336 | -0.7157 | -0.70789 | -0.71244 | -0.70961 | -0.65352 | -0.52621 | -0.35122 | -0.1665 | 0.0050468 | 0.13966 | 6.4384e-05 | 0.0025041 | 0.00012521 | 0.00012521 | 0 | 0 | 0.0022135 | 0.05 | 0.26561 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.73452 | 0.74971 | 0.77813 | 0.82406 | 0.88866 | 0.97172 | 0.93329 | 0.83193 | 0.73249 | 0.64133 | 0.56251 | 0.49796 | 0.4465 | 0.40716 | 0.37868 | 0.36 | 0.3492 | 0.34337 | 0.34583 | 0.39377 | 0.4472 | 0.50099 | 0.56024 | 0.62602 | 0.68542 | 0.72697 | 0.7529 | 0.77447 | 0.80053 | 0.82939 | 0.86684 | 0.97172 | 5 | Slope | 0.86667 | 0.57817 | 0.58324 | 0.5816 | 0.5858 | 0.59622 | 0.61279 | 0.58888 | 0.54398 | 0.49972 | 0.45822 | 0.42084 | 0.38821 | 0.35994 | 0.33572 | 0.31512 | 0.29778 | 0.28307 | 0.27001 | 0.25972 | 0.26459 | 0.27129 | 0.27811 | 0.28675 | 0.29756 | 0.30625 | 0.30899 | 0.30652 | 0.3026 | 0.30018 | 0.29868 | 0.30006 | 0.61279 | 5 | 0.97172 | Slope | 0.86667 | 0.0012877 |  | 0.99363 | 0 | 0.97172 | Slope | 2 | 0.86667 | 0 | 20 | -20 | 0.00044143 | 0.00013823 | 0.0022135
266 | 0:44 | 0.12877 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -1.2638 | -0.012638 | -0.012638 | 0.12877 | 0.00069626 | [13 empty] | 0.95772 | 1 | 0.95895 | 0.85113 | 0.70661 | 0.55177 | 0.39956 | 0.2539 | 0.11662 | -0.013429 | -0.13913 | -0.26302 | -0.38293 | -0.49353 | -0.58789 | -0.65886 | -0.70154 | -0.71721 | -0.74954 | -0.75771 | -0.74687 | -0.74195 | -0.75578 | -0.76515 | -0.73489 | -0.64418 | -0.50477 | -0.33161 | -0.14211 | 0.028685 | 0.14396 | -0.00063188 | 0.0022199 | 0.000111 | 0.000111 | 0 | 0 | 0.002247 | 0.05 | 0.25041 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.7497 | 0.77812 | 0.82405 | 0.88865 | 0.9717 | 0.93331 | 0.83195 | 0.7325 | 0.64134 | 0.56253 | 0.49798 | 0.44652 | 0.40717 | 0.37869 | 0.36001 | 0.34921 | 0.34338 | 0.34585 | 0.39379 | 0.44722 | 0.501 | 0.56025 | 0.62604 | 0.68544 | 0.72698 | 0.75291 | 0.77448 | 0.80055 | 0.8294 | 0.86686 | 0.9203 | 0.9717 | 4 | Slope | 0.9 | 0.58323 | 0.59271 | 0.5969 | 0.60733 | 0.6239 | 0.59999 | 0.55509 | 0.51083 | 0.46934 | 0.43195 | 0.39933 | 0.37106 | 0.34684 | 0.32623 | 0.30889 | 0.29418 | 0.28113 | 0.27084 | 0.27571 | 0.28241 | 0.28922 | 0.29786 | 0.30868 | 0.31737 | 0.32011 | 0.31764 | 0.31372 | 0.31129 | 0.3098 | 0.31118 | 0.31788 | 0.6239 | 4 | 0.9717 | Slope | 0.9 | 0.012638 |  | 0.93744 | 0 | 0.9717 | Slope | 2 | 0.9 | 0 | 20 | -20 | 0.00069626 | 0.00013127 | 0.002247
267 | 0:44 | -1.2638 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.8343 | -0.028343 | -0.028343 | -1.2638 | 0.00078526 | [13 empty] | 0.95895 | 1 | 0.96131 | 0.86238 | 0.73097 | 0.58585 | 0.43824 | 0.29716 | 0.16681 | 0.045036 | -0.0735 | -0.19207 | -0.30889 | -0.41859 | -0.51401 | -0.5872 | -0.63395 | -0.70133 | -0.73725 | -0.74362 | -0.74077 | -0.75499 | -0.77173 | -0.75253 | -0.68761 | -0.58756 | -0.4549 | -0.28234 | -0.10162 | 0.039318 | 0.067385 | -0.0014171 | 0.0017607 | 8.8033e-05 | 8.8033e-05 | 0 | 0 | 0.0023038 | 0.05 | 0.22199 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.7781 | 0.82402 | 0.88862 | 0.97168 | 0.93333 | 0.83197 | 0.73253 | 0.64137 | 0.56255 | 0.498 | 0.44654 | 0.4072 | 0.37872 | 0.36003 | 0.34923 | 0.3434 | 0.34587 | 0.39381 | 0.44724 | 0.50103 | 0.56028 | 0.62606 | 0.68546 | 0.72701 | 0.75294 | 0.77451 | 0.80057 | 0.82942 | 0.86688 | 0.92033 | 0.98859 | 0.98859 | 30 | Slope | 0.033333 | 0.5927 | 0.60801 | 0.61843 | 0.635 | 0.61111 | 0.56621 | 0.52195 | 0.48046 | 0.44307 | 0.41044 | 0.38218 | 0.35795 | 0.33735 | 0.32001 | 0.3053 | 0.29225 | 0.28196 | 0.28683 | 0.29352 | 0.30034 | 0.30898 | 0.3198 | 0.32849 | 0.33122 | 0.32876 | 0.32484 | 0.32241 | 0.32092 | 0.32229 | 0.329 | 0.34064 | 0.635 | 3 | 0.97168 | Slope | 0.93333 | 0.028343 |  | 0.8597 | 0 | 0.97168 | Slope | 2 | 0.93333 | 0 | 20 | -20 | 0.00078526 | 0.00012664 | 0.0023038
268 | 0:44 | -2.8343 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.6873 | -0.046873 | -0.046873 | -2.8343 | 0.00092654 | [13 empty] | 0.96131 | 1 | 0.96507 | 0.87612 | 0.75408 | 0.61466 | 0.47361 | 0.34243 | 0.224 | 0.11294 | 0.0032266 | -0.10871 | -0.22102 | -0.32858 | -0.42399 | -0.49806 | -0.59874 | -0.66597 | -0.69413 | -0.70279 | -0.71512 | -0.72894 | -0.71693 | -0.664 | -0.59211 | -0.50137 | -0.37463 | -0.2202 | -0.082027 | -0.034492 | -0.083707 | -0.0023437 | 0.0011147 | 5.5733e-05 | 5.5733e-05 | 0 | 0 | 0.0023835 | 0.05 | 0.17607 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.82399 | 0.88859 | 0.97165 | 0.93336 | 0.832 | 0.73256 | 0.6414 | 0.56258 | 0.49803 | 0.44657 | 0.40723 | 0.37875 | 0.36007 | 0.34927 | 0.34344 | 0.3459 | 0.39384 | 0.44727 | 0.50106 | 0.56031 | 0.62609 | 0.68549 | 0.72704 | 0.75297 | 0.77454 | 0.8006 | 0.82946 | 0.86691 | 0.92036 | 0.98862 | 0.93305 | 0.98862 | 29 | Slope | 0.066667 | 0.608 | 0.62953 | 0.6461 | 0.62223 | 0.57733 | 0.53308 | 0.49158 | 0.45419 | 0.42157 | 0.3933 | 0.36908 | 0.34847 | 0.33113 | 0.31642 | 0.30337 | 0.29308 | 0.29795 | 0.30465 | 0.31146 | 0.3201 | 0.33092 | 0.33961 | 0.34235 | 0.33988 | 0.33596 | 0.33353 | 0.33204 | 0.33342 | 0.34012 | 0.35176 | 0.32213 | 0.6461 | 2 | 0.97165 | Slope | 0.96667 | 0.046873 |  | 0.76798 | 0 | 0.97165 | Slope | 2 | 0.96667 | 0 | 20 | -20 | 0.00092654 | 0.00012584 | 0.0023835
269 | 0:45 | -4.6873 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -6.4468 | -0.064468 | -0.064468 | -4.6873 | 0.00087973 | [13 empty] | 0.96507 | 1 | 0.96861 | 0.88599 | 0.76915 | 0.63734 | 0.50873 | 0.39303 | 0.28872 | 0.18958 | 0.089288 | -0.015339 | -0.12298 | -0.22883 | -0.32179 | -0.44792 | -0.54411 | -0.59719 | -0.62069 | -0.6394 | -0.64771 | -0.63397 | -0.59143 | -0.53351 | -0.47004 | -0.38739 | -0.28489 | -0.18327 | -0.14052 | -0.17082 | -0.24313 | -0.0032234 | 0.00028408 | 1.4204e-05 | 1.4204e-05 | 0 | 0 | 0.0024714 | 0.05 | 0.11147 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.88855 | 0.97161 | 0.93341 | 0.83204 | 0.7326 | 0.64144 | 0.56263 | 0.49808 | 0.44661 | 0.40727 | 0.37879 | 0.36011 | 0.34931 | 0.34348 | 0.34594 | 0.39388 | 0.44731 | 0.5011 | 0.56035 | 0.62613 | 0.68553 | 0.72708 | 0.75301 | 0.77458 | 0.80065 | 0.8295 | 0.86696 | 0.9204 | 0.98866 | 0.933 | 0.84906 | 0.98866 | 28 | Slope | 0.1 | 0.62952 | 0.6572 | 0.63336 | 0.58846 | 0.5442 | 0.5027 | 0.46532 | 0.43269 | 0.40443 | 0.3802 | 0.3596 | 0.34226 | 0.32755 | 0.31449 | 0.3042 | 0.30907 | 0.31577 | 0.32259 | 0.33123 | 0.34204 | 0.35073 | 0.35347 | 0.351 | 0.34708 | 0.34466 | 0.34317 | 0.34454 | 0.35124 | 0.36289 | 0.33322 | 0.29413 | 0.6572 | 1 | 0.97161 | Slope | 1 | 0.064468 |  | 0.68088 | 0 | 0.97161 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00087973 | 0.00012959 | 0.0024714
270 | 0:45 | -6.4468 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.5774 | -0.075774 | -0.075774 | -6.4468 | 0.0005653 | [13 empty] | 0.96861 | 1 | 0.97033 | 0.8906 | 0.78032 | 0.66144 | 0.55025 | 0.45092 | 0.36058 | 0.27252 | 0.18094 | 0.081975 | -0.023749 | -0.12517 | -0.26351 | -0.38246 | -0.4604 | -0.50285 | -0.53079 | -0.54343 | -0.52778 | -0.48871 | -0.44283 | -0.38973 | -0.33293 | -0.27379 | -0.22619 | -0.21518 | -0.24267 | -0.3041 | -0.37499 | -0.0037887 | -0.0006658 | -3.329e-05 | -3.329e-05 | 0 | 0 | 0.0025333 | 0.05 | 0.028408 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.97156 | 0.93345 | 0.83209 | 0.73265 | 0.64149 | 0.56267 | 0.49812 | 0.44666 | 0.40732 | 0.37884 | 0.36016 | 0.34935 | 0.34353 | 0.34599 | 0.39393 | 0.44736 | 0.50115 | 0.5604 | 0.62618 | 0.68558 | 0.72713 | 0.75306 | 0.77463 | 0.80069 | 0.82955 | 0.867 | 0.92045 | 0.98871 | 0.93296 | 0.84901 | 0.77082 | 0.98871 | 27 | Slope | 0.13333 | 0.65719 | 0.64448 | 0.59959 | 0.55533 | 0.51383 | 0.47645 | 0.44382 | 0.41555 | 0.39133 | 0.37072 | 0.35339 | 0.33867 | 0.32562 | 0.31533 | 0.3202 | 0.3269 | 0.33372 | 0.34235 | 0.35317 | 0.36186 | 0.3646 | 0.36213 | 0.35821 | 0.35579 | 0.35429 | 0.35567 | 0.36237 | 0.37401 | 0.34432 | 0.30523 | 0.26805 | 0.65719 | 0 | 0.97156 | Slope | 1 | 0.075774 |  | 0.62492 | 0 | 0.97156 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0005653 | 0.00013762 | 0.0025333
271 | 0:45 | -7.5774 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.3524 | -0.073524 | -0.073524 | -7.5774 | 0.00011247 | [13 empty] | 0.97033 | 1 | 0.97125 | 0.89647 | 0.79823 | 0.69715 | 0.60345 | 0.51943 | 0.44136 | 0.363 | 0.27769 | 0.18057 | 0.080491 | -0.059395 | -0.18877 | -0.28672 | -0.34939 | -0.39162 | -0.41232 | -0.40579 | -0.37003 | -0.32904 | -0.28467 | -0.23592 | -0.19963 | -0.19543 | -0.24034 | -0.29191 | -0.3526 | -0.42261 | -0.49549 | -0.0036762 | -0.0016794 | -8.3971e-05 | -8.3971e-05 | 0 | 0 | 0.0025684 | 0.05 | -0.06658 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.9335 | 0.83214 | 0.7327 | 0.64154 | 0.56272 | 0.49817 | 0.44671 | 0.40737 | 0.37889 | 0.36021 | 0.34941 | 0.34358 | 0.34604 | 0.39398 | 0.44741 | 0.5012 | 0.56045 | 0.62623 | 0.68563 | 0.72718 | 0.75311 | 0.77468 | 0.80074 | 0.8296 | 0.86705 | 0.9205 | 0.98876 | 0.93291 | 0.84896 | 0.77077 | 0.70123 | 0.98876 | 26 | Slope | 0.16667 | 0.6445 | 0.61071 | 0.56646 | 0.52496 | 0.48757 | 0.45495 | 0.42668 | 0.40246 | 0.38185 | 0.36451 | 0.3498 | 0.33675 | 0.32646 | 0.33133 | 0.33803 | 0.34484 | 0.35348 | 0.3643 | 0.37299 | 0.37573 | 0.37326 | 0.36934 | 0.36691 | 0.36542 | 0.3668 | 0.3735 | 0.38514 | 0.35541 | 0.31632 | 0.27915 | 0.24486 | 0.6445 | 0 | 0.9335 | Slope | 1 | 0.073524 |  | 0.63605 | 0 | 0.9335 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00011247 | 0.00014862 | 0.0025684
272 | 0:45 | -7.3524 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -6.1563 | -0.061563 | -0.061563 | -7.3524 | 0.00059809 | [13 empty] | 0.97125 | 1 | 0.9735 | 0.90781 | 0.82532 | 0.74101 | 0.66269 | 0.59132 | 0.52345 | 0.45192 | 0.36898 | 0.27855 | 0.1457 | 0.016535 | -0.089825 | -0.16971 | -0.22952 | -0.26466 | -0.2702 | -0.24798 | -0.2114 | -0.17039 | -0.12954 | -0.098839 | -0.11771 | -0.2131 | -0.31281 | -0.38796 | -0.45794 | -0.53141 | -0.59627 | -0.0030781 | -0.0026738 | -0.00013369 | -0.00013369 | 0 | 0 | 0.0026084 | 0.05 | -0.16794 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.83219 | 0.73275 | 0.64159 | 0.56277 | 0.49822 | 0.44676 | 0.40742 | 0.37894 | 0.36026 | 0.34946 | 0.34363 | 0.34609 | 0.39403 | 0.44746 | 0.50125 | 0.5605 | 0.62628 | 0.68568 | 0.72723 | 0.75316 | 0.77473 | 0.80079 | 0.82965 | 0.8671 | 0.92055 | 0.98881 | 0.93286 | 0.84891 | 0.77072 | 0.70118 | 0.64303 | 0.98881 | 25 | Slope | 0.2 | 0.61073 | 0.57758 | 0.53608 | 0.4987 | 0.46607 | 0.43781 | 0.41358 | 0.39298 | 0.37564 | 0.36093 | 0.34788 | 0.33759 | 0.34246 | 0.34915 | 0.35597 | 0.36461 | 0.37543 | 0.38412 | 0.38685 | 0.38439 | 0.38047 | 0.37804 | 0.37655 | 0.37792 | 0.38463 | 0.39627 | 0.36651 | 0.32742 | 0.29024 | 0.25595 | 0.22545 | 0.61073 | 0 | 0.83219 | Slope | 1 | 0.061563 |  | 0.69527 | 0 | 0.83219 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00059809 | 0.00016114 | 0.0026084
273 | 0:45 | -6.1563 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.4052 | -0.044052 | -0.044052 | -6.1563 | 0.00087554 | [13 empty] | 0.9735 | 1 | 0.97717 | 0.92254 | 0.85405 | 0.78369 | 0.71739 | 0.65597 | 0.595 | 0.52635 | 0.45049 | 0.33186 | 0.21095 | 0.10584 | 0.019201 | -0.056169 | -0.10981 | -0.13342 | -0.12653 | -0.10453 | -0.067906 | -0.030184 | -0.0064402 | -0.030057 | -0.15419 | -0.29758 | -0.40215 | -0.47878 | -0.55006 | -0.61592 | -0.67356 | -0.0022026 | -0.0035855 | -0.00017927 | -0.00017927 | 0 | 0 | 0.0026722 | 0.05 | -0.26738 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.73279 | 0.64163 | 0.56282 | 0.49827 | 0.44681 | 0.40746 | 0.37898 | 0.3603 | 0.3495 | 0.34367 | 0.34614 | 0.39408 | 0.44751 | 0.50129 | 0.56054 | 0.62633 | 0.68573 | 0.72727 | 0.7532 | 0.77478 | 0.80084 | 0.82969 | 0.86715 | 0.9206 | 0.98886 | 0.93281 | 0.84887 | 0.77068 | 0.70114 | 0.64298 | 0.59274 | 0.98886 | 24 | Slope | 0.23333 | 0.5776 | 0.54721 | 0.50983 | 0.4772 | 0.44894 | 0.42471 | 0.40411 | 0.38677 | 0.37206 | 0.359 | 0.34871 | 0.35358 | 0.36028 | 0.3671 | 0.37574 | 0.38655 | 0.39524 | 0.39798 | 0.39551 | 0.39159 | 0.38917 | 0.38767 | 0.38905 | 0.39575 | 0.4074 | 0.3776 | 0.33851 | 0.30134 | 0.26705 | 0.23655 | 0.20869 | 0.5776 | 0 | 0.73279 | Slope | 1 | 0.044052 |  | 0.78194 | 0 | 0.73279 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00087554 | 0.00017404 | 0.0026722
274 | 0:45 | -4.4052 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.4671 | -0.024671 | -0.024671 | -4.4052 | 0.00096902 | [13 empty] | 0.97717 | 1 | 0.98115 | 0.93566 | 0.87807 | 0.81796 | 0.76052 | 0.70545 | 0.64742 | 0.58525 | 0.48426 | 0.37748 | 0.28007 | 0.19482 | 0.11388 | 0.04356 | -0.0018604 | -0.015585 | -0.009323 | 0.011632 | 0.044626 | 0.065663 | 0.035344 | -0.09444 | -0.26037 | -0.38895 | -0.48059 | -0.55324 | -0.61689 | -0.67536 | -0.72894 | -0.0012336 | -0.0043736 | -0.00021868 | -0.00021868 | 0 | 0 | 0.0027598 | 0.05 | -0.35855 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.64167 | 0.56286 | 0.49831 | 0.44685 | 0.4075 | 0.37902 | 0.36034 | 0.34954 | 0.34371 | 0.34617 | 0.39412 | 0.44755 | 0.50133 | 0.56058 | 0.62637 | 0.68576 | 0.72731 | 0.75324 | 0.77481 | 0.80088 | 0.82973 | 0.86719 | 0.92063 | 0.9889 | 0.93277 | 0.84883 | 0.77064 | 0.7011 | 0.64294 | 0.5927 | 0.5436 | 0.9889 | 23 | Slope | 0.26667 | 0.54722 | 0.52095 | 0.48833 | 0.46006 | 0.43583 | 0.41523 | 0.39789 | 0.38318 | 0.37013 | 0.35984 | 0.36471 | 0.3714 | 0.37822 | 0.38686 | 0.39768 | 0.40637 | 0.4091 | 0.40664 | 0.40272 | 0.40029 | 0.3988 | 0.40017 | 0.40688 | 0.41852 | 0.3887 | 0.34961 | 0.31243 | 0.27814 | 0.24765 | 0.21979 | 0.19231 | 0.54722 | 0 | 0.64167 | Slope | 1 | 0.024671 |  | 0.87788 | 0 | 0.64167 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00096902 | 0.00018685 | 0.0027598
275 | 0:46 | -2.4671 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -0.83342 | -0.0083342 | -0.0083342 | -2.4671 | 0.00081686 | [13 empty] | 0.98115 | 1 | 0.98405 | 0.94513 | 0.89504 | 0.84201 | 0.7899 | 0.73748 | 0.68468 | 0.59915 | 0.50858 | 0.42325 | 0.34441 | 0.26524 | 0.18851 | 0.12332 | 0.085432 | 0.07092 | 0.074917 | 0.091254 | 0.10725 | 0.0748 | -0.058461 | -0.22348 | -0.35956 | -0.46102 | -0.54106 | -0.6053 | -0.66176 | -0.71546 | -0.76443 | -0.00041671 | -0.0050191 | -0.00025096 | -0.00025096 | 0 | 0 | 0.0028591 | 0.05 | -0.43736 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.56289 | 0.49834 | 0.44688 | 0.40754 | 0.37906 | 0.36037 | 0.34957 | 0.34374 | 0.34621 | 0.39415 | 0.44758 | 0.50137 | 0.56061 | 0.6264 | 0.6858 | 0.72735 | 0.75328 | 0.77485 | 0.80091 | 0.82976 | 0.86722 | 0.92067 | 0.98893 | 0.93274 | 0.8488 | 0.7706 | 0.70107 | 0.64291 | 0.59267 | 0.54357 | 0.48348 | 0.98893 | 22 | Slope | 0.3 | 0.52096 | 0.49945 | 0.47118 | 0.44696 | 0.42635 | 0.40901 | 0.3943 | 0.38125 | 0.37096 | 0.37583 | 0.38253 | 0.38934 | 0.39798 | 0.4088 | 0.41749 | 0.42023 | 0.41776 | 0.41384 | 0.41141 | 0.40992 | 0.4113 | 0.418 | 0.42964 | 0.3998 | 0.36071 | 0.32353 | 0.28924 | 0.25875 | 0.23089 | 0.20341 | 0.17227 | 0.52096 | 0 | 0.56289 | Slope | 1 | 0.0083342 |  | 0.95875 | 0 | 0.56289 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00081686 | 0.00019949 | 0.0028591
276 | 0:46 | -0.83342 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 0.54802 | 0.0054802 | 0.0054802 | -0.83342 | 0.00069072 | [13 empty] | 0.98405 | 1 | 0.98612 | 0.95167 | 0.90667 | 0.85785 | 0.80799 | 0.75958 | 0.68491 | 0.60801 | 0.53647 | 0.46817 | 0.3957 | 0.3202 | 0.24574 | 0.18512 | 0.14591 | 0.12805 | 0.12659 | 0.12484 | 0.087921 | -0.041509 | -0.20244 | -0.32964 | -0.42992 | -0.51376 | -0.58372 | -0.64087 | -0.69248 | -0.74078 | -0.78129 | 0.00027401 | -0.0055337 | -0.00027669 | -0.00027669 | 0 | 0 | 0.002955 | 0.05 | -0.50191 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.49837 | 0.4469 | 0.40756 | 0.37908 | 0.3604 | 0.3496 | 0.34377 | 0.34623 | 0.39418 | 0.44761 | 0.50139 | 0.56064 | 0.62642 | 0.68582 | 0.72737 | 0.7533 | 0.77487 | 0.80094 | 0.82979 | 0.86725 | 0.92069 | 0.98895 | 0.93271 | 0.84877 | 0.77058 | 0.70104 | 0.64288 | 0.59265 | 0.54354 | 0.48346 | 0.40815 | 0.98895 | 21 | Slope | 0.33333 | 0.49946 | 0.4823 | 0.45808 | 0.43747 | 0.42013 | 0.40542 | 0.39237 | 0.38208 | 0.38695 | 0.39365 | 0.40046 | 0.4091 | 0.41992 | 0.42861 | 0.43135 | 0.42888 | 0.42496 | 0.42253 | 0.42104 | 0.42242 | 0.42912 | 0.44076 | 0.4109 | 0.37181 | 0.33464 | 0.30035 | 0.26985 | 0.24199 | 0.21451 | 0.18338 | 0.14716 | 0.49946 | 0 | 0.49837 | Slope | 1 | 0.0054802 |  | 0.97287 | 0 | 0.49837 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00069072 | 0.00021173 | 0.002955
277 | 0:46 | 0.54802 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.6469 | 0.016469 | 0.016469 | 0.54802 | 0.00054944 | [13 empty] | 0.98612 | 1 | 0.9875 | 0.95603 | 0.91399 | 0.86693 | 0.82002 | 0.75117 | 0.68334 | 0.62302 | 0.56693 | 0.50533 | 0.43627 | 0.36056 | 0.28763 | 0.2247 | 0.18103 | 0.1566 | 0.1359 | 0.080419 | -0.045548 | -0.19435 | -0.31112 | -0.39924 | -0.47867 | -0.55114 | -0.61353 | -0.66567 | -0.71162 | -0.75118 | -0.78756 | 0.00082345 | -0.0059271 | -0.00029636 | -0.00029636 | 0 | 0 | 0.0030383 | 0.05 | -0.55337 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.44692 | 0.40758 | 0.3791 | 0.36042 | 0.34962 | 0.34379 | 0.34625 | 0.39419 | 0.44763 | 0.50141 | 0.56066 | 0.62644 | 0.68584 | 0.72739 | 0.75332 | 0.77489 | 0.80096 | 0.82981 | 0.86727 | 0.92071 | 0.98897 | 0.93269 | 0.84875 | 0.77056 | 0.70102 | 0.64286 | 0.59263 | 0.54352 | 0.48344 | 0.40813 | 0.3275 | 0.98897 | 20 | Slope | 0.36667 | 0.48231 | 0.46919 | 0.44859 | 0.43125 | 0.41654 | 0.40349 | 0.3932 | 0.39806 | 0.40476 | 0.41158 | 0.42022 | 0.43104 | 0.43973 | 0.44246 | 0.44 | 0.43608 | 0.43365 | 0.43216 | 0.43353 | 0.44024 | 0.45188 | 0.42201 | 0.38292 | 0.34574 | 0.31145 | 0.28095 | 0.2531 | 0.22562 | 0.19448 | 0.15827 | 0.12028 | 0.48231 | 0 | 0.44692 | Slope | 1 | 0.016469 |  | 0.91848 | 0 | 0.44692 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00054944 | 0.00022341 | 0.0030383
278 | 0:46 | 1.6469 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.5115 | 0.025115 | 0.025115 | 1.6469 | 0.00043229 | [13 empty] | 0.9875 | 1 | 0.98841 | 0.95864 | 0.91781 | 0.87278 | 0.8069 | 0.74332 | 0.68987 | 0.64354 | 0.59458 | 0.53658 | 0.46532 | 0.38825 | 0.31192 | 0.24356 | 0.19192 | 0.14674 | 0.071336 | -0.065695 | -0.20127 | -0.30193 | -0.37821 | -0.44514 | -0.51312 | -0.57782 | -0.63477 | -0.68098 | -0.71828 | -0.75377 | -0.78779 | 0.0012557 | -0.0062119 | -0.0003106 | -0.0003106 | 0 | 0 | 0.003104 | 0.05 | -0.59271 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.4076 | 0.37912 | 0.36043 | 0.34963 | 0.3438 | 0.34627 | 0.39421 | 0.44764 | 0.50143 | 0.56067 | 0.62646 | 0.68586 | 0.72741 | 0.75334 | 0.77491 | 0.80097 | 0.82982 | 0.86728 | 0.92073 | 0.98899 | 0.93268 | 0.84874 | 0.77054 | 0.70101 | 0.64285 | 0.59261 | 0.54351 | 0.48342 | 0.40812 | 0.32748 | 0.24413 | 0.98899 | 19 | Slope | 0.4 | 0.4692 | 0.45971 | 0.44237 | 0.42766 | 0.4146 | 0.40431 | 0.40918 | 0.41588 | 0.4227 | 0.43134 | 0.44215 | 0.45084 | 0.45358 | 0.45111 | 0.44719 | 0.44477 | 0.44327 | 0.44465 | 0.45135 | 0.463 | 0.43312 | 0.39402 | 0.35685 | 0.32256 | 0.29206 | 0.2642 | 0.23673 | 0.20559 | 0.16937 | 0.13138 | 0.092489 | 0.4692 | 0 | 0.4076 | Slope | 1 | 0.025115 |  | 0.87568 | 0 | 0.4076 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00043229 | 0.00023416 | 0.003104
279 | 0:46 | 2.5115 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.0248 | 0.030248 | 0.030248 | 2.5115 | 0.00025664 | [13 empty] | 0.98841 | 1 | 0.98889 | 0.95974 | 0.92009 | 0.85759 | 0.79564 | 0.74444 | 0.70355 | 0.66462 | 0.61978 | 0.5583 | 0.48319 | 0.40172 | 0.31954 | 0.24181 | 0.16771 | 0.066116 | -0.084669 | -0.22022 | -0.30404 | -0.36511 | -0.42053 | -0.47727 | -0.53794 | -0.59708 | -0.64767 | -0.6852 | -0.71868 | -0.75187 | -0.78753 | 0.0015124 | -0.0063988 | -0.00031994 | -0.00031994 | 0 | 0 | 0.0031498 | 0.05 | -0.62119 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.37913 | 0.36044 | 0.34964 | 0.34381 | 0.34628 | 0.39422 | 0.44765 | 0.50143 | 0.56068 | 0.62647 | 0.68587 | 0.72741 | 0.75335 | 0.77492 | 0.80098 | 0.82983 | 0.86729 | 0.92074 | 0.989 | 0.93267 | 0.84873 | 0.77053 | 0.701 | 0.64284 | 0.5926 | 0.5435 | 0.48342 | 0.40811 | 0.32747 | 0.24412 | 0.16852 | 0.989 | 18 | Slope | 0.43333 | 0.45971 | 0.45348 | 0.43877 | 0.42572 | 0.41543 | 0.4203 | 0.42699 | 0.43381 | 0.44245 | 0.45327 | 0.46196 | 0.46469 | 0.46223 | 0.45831 | 0.45588 | 0.45439 | 0.45576 | 0.46247 | 0.47411 | 0.44422 | 0.40513 | 0.36796 | 0.33367 | 0.30317 | 0.27531 | 0.24783 | 0.21669 | 0.18048 | 0.14249 | 0.1036 | 0.067283 | 0.47411 | 18 | 0.989 | Slope | 0.43333 | 0.030248 |  | 0.85027 | 0 | 0.989 | Slope | 2 | 0.43333 | 0 | 20 | -20 | 0.00025664 | 0.00024341 | 0.0031498
280 | 0:46 | 3.0248 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.0538 | 0.030538 | 0.030538 | 3.0248 | 1.4529e-05 | [13 empty] | 0.98889 | 1 | 0.98902 | 0.96044 | 0.90508 | 0.84562 | 0.79457 | 0.75491 | 0.72174 | 0.68748 | 0.63841 | 0.57109 | 0.49078 | 0.40378 | 0.31175 | 0.21055 | 0.078122 | -0.095721 | -0.23609 | -0.3148 | -0.36135 | -0.40333 | -0.45002 | -0.50056 | -0.55604 | -0.60884 | -0.65051 | -0.68421 | -0.71556 | -0.75037 | -0.78859 | 0.0015269 | -0.0065068 | -0.00032534 | -0.00032534 | 0 | 0 | 0.0031772 | 0.05 | -0.63988 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.36045 | 0.34965 | 0.34382 | 0.34628 | 0.39422 | 0.44765 | 0.50144 | 0.56069 | 0.62647 | 0.68587 | 0.72742 | 0.75335 | 0.77492 | 0.80099 | 0.82984 | 0.86729 | 0.92074 | 0.989 | 0.93266 | 0.84872 | 0.77053 | 0.70099 | 0.64283 | 0.5926 | 0.54349 | 0.48341 | 0.4081 | 0.32747 | 0.24412 | 0.16851 | 0.10913 | 0.989 | 17 | Slope | 0.46667 | 0.45348 | 0.44988 | 0.43683 | 0.42654 | 0.43141 | 0.43811 | 0.44492 | 0.45356 | 0.46438 | 0.47307 | 0.47581 | 0.47334 | 0.46942 | 0.467 | 0.4655 | 0.46688 | 0.47358 | 0.48522 | 0.45533 | 0.41624 | 0.37907 | 0.34477 | 0.31428 | 0.28642 | 0.25894 | 0.2278 | 0.19159 | 0.1536 | 0.11471 | 0.078393 | 0.047487 | 0.48522 | 17 | 0.989 | Slope | 0.46667 | 0.030538 |  | 0.84884 | 0 | 0.989 | Slope | 2 | 0.46667 | 0 | 20 | -20 | 1.4529e-05 | 0.0002506 | 0.0031772
281 | 0:47 | 3.0538 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.5954 | 0.035954 | 0.035954 | 3.0538 | 0.0002708 | [13 empty] | 0.98902 | 1 | 0.98934 | 0.94731 | 0.89487 | 0.84579 | 0.80626 | 0.77517 | 0.74723 | 0.70784 | 0.65116 | 0.57816 | 0.49361 | 0.39743 | 0.28321 | 0.12307 | -0.08345 | -0.2418 | -0.32175 | -0.36448 | -0.39464 | -0.42998 | -0.47155 | -0.51769 | -0.56733 | -0.61133 | -0.64878 | -0.68032 | -0.71334 | -0.75066 | -0.79033 | 0.0017977 | -0.0065651 | -0.00032825 | -0.00032825 | 0 | 0 | 0.0031919 | 0.05 | -0.65068 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.34965 | 0.34382 | 0.34628 | 0.39423 | 0.44766 | 0.50144 | 0.56069 | 0.62647 | 0.68587 | 0.72742 | 0.75335 | 0.77492 | 0.80099 | 0.82984 | 0.8673 | 0.92074 | 0.98901 | 0.93266 | 0.84872 | 0.77053 | 0.70099 | 0.64283 | 0.59259 | 0.54349 | 0.48341 | 0.4081 | 0.32747 | 0.24411 | 0.16851 | 0.10913 | 0.06998 | 0.98901 | 16 | Slope | 0.5 | 0.44988 | 0.44794 | 0.43765 | 0.44252 | 0.44922 | 0.45604 | 0.46468 | 0.47549 | 0.48418 | 0.48692 | 0.48445 | 0.48053 | 0.47811 | 0.47661 | 0.47799 | 0.48469 | 0.49634 | 0.46644 | 0.42735 | 0.39018 | 0.35589 | 0.32539 | 0.29753 | 0.27005 | 0.23891 | 0.2027 | 0.16471 | 0.12582 | 0.089503 | 0.058598 | 0.034438 | 0.49634 | 16 | 0.98901 | Slope | 0.5 | 0.035954 |  | 0.82203 | 0 | 0.98901 | Slope | 2 | 0.5 | 0 | 20 | -20 | 0.0002708 | 0.00025536 | 0.0031919
282 | 0:47 | 3.5954 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 4.8722 | 0.048722 | 0.048722 | 3.5954 | 0.00063839 | [13 empty] | 0.98934 | 1 | 0.97699 | 0.93716 | 0.89375 | 0.85494 | 0.82349 | 0.7972 | 0.76354 | 0.71568 | 0.65336 | 0.57692 | 0.48384 | 0.367 | 0.19408 | -0.045622 | -0.23348 | -0.324 | -0.36595 | -0.39215 | -0.4175 | -0.44892 | -0.48672 | -0.52781 | -0.56931 | -0.6089 | -0.6438 | -0.67681 | -0.71228 | -0.75099 | -0.79059 | 0.0024361 | -0.0065404 | -0.00032702 | -0.00032702 | 0 | 0 | 0.0031854 | 0.05 | -0.65651 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.34382 | 0.34628 | 0.39423 | 0.44766 | 0.50144 | 0.56069 | 0.62647 | 0.68587 | 0.72742 | 0.75335 | 0.77492 | 0.80099 | 0.82984 | 0.8673 | 0.92074 | 0.989 | 0.93266 | 0.84872 | 0.77053 | 0.70099 | 0.64283 | 0.5926 | 0.54349 | 0.48341 | 0.4081 | 0.32747 | 0.24412 | 0.16851 | 0.10913 | 0.069981 | 0.047878 | 0.989 | 15 | Slope | 0.53333 | 0.44794 | 0.44876 | 0.45363 | 0.46033 | 0.46715 | 0.47579 | 0.4866 | 0.49529 | 0.49803 | 0.49556 | 0.49164 | 0.48922 | 0.48772 | 0.4891 | 0.4958 | 0.50745 | 0.47755 | 0.43846 | 0.40129 | 0.367 | 0.3365 | 0.30864 | 0.28116 | 0.25002 | 0.21381 | 0.17582 | 0.13693 | 0.10061 | 0.069709 | 0.045549 | 0.02707 | 0.50745 | 15 | 0.989 | Slope | 0.53333 | 0.048722 |  | 0.75883 | 0 | 0.989 | Slope | 2 | 0.53333 | 0 | 20 | -20 | 0.00063839 | 0.00025741 | 0.0031854
283 | 0:47 | 4.8722 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 5.677 | 0.05677 | 0.05677 | 4.8722 | 0.00040241 | [13 empty] | 0.97699 | 1 | 0.97627 | 0.93552 | 0.89436 | 0.86137 | 0.82873 | 0.78744 | 0.73702 | 0.68267 | 0.61839 | 0.53653 | 0.43537 | 0.29197 | 0.079938 | -0.11885 | -0.22571 | -0.28227 | -0.31551 | -0.35065 | -0.38203 | -0.41269 | -0.44024 | -0.46791 | -0.50627 | -0.54532 | -0.58757 | -0.63146 | -0.67734 | -0.72279 | -0.7675 | 0.0028385 | -0.006061 | -0.00030305 | -0.00030305 | 0 | 0 | 0.0030981 | 0.05 | -0.65404 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.34626 | 0.3942 | 0.44763 | 0.50142 | 0.56067 | 0.62645 | 0.68585 | 0.7274 | 0.75333 | 0.7749 | 0.80096 | 0.82982 | 0.86727 | 0.92072 | 0.98898 | 0.93269 | 0.84875 | 0.77055 | 0.70101 | 0.64286 | 0.59262 | 0.54352 | 0.48343 | 0.40813 | 0.32749 | 0.24414 | 0.16853 | 0.10915 | 0.070005 | 0.047902 | 0.041008 | 0.98898 | 14 | Slope | 0.56667 | 0.44875 | 0.46473 | 0.47143 | 0.47825 | 0.48689 | 0.49771 | 0.50639 | 0.50913 | 0.50667 | 0.50274 | 0.50032 | 0.49883 | 0.5002 | 0.50691 | 0.51855 | 0.48867 | 0.44958 | 0.41241 | 0.37812 | 0.34762 | 0.31976 | 0.29228 | 0.26114 | 0.22493 | 0.18694 | 0.14805 | 0.11173 | 0.080828 | 0.056668 | 0.03819 | 0.02478 | 0.51855 | 14 | 0.98898 | Slope | 0.56667 | 0.05677 |  | 0.71899 | 0 | 0.98898 | Slope | 2 | 0.56667 | 0 | 20 | -20 | 0.00040241 | 0.00025654 | 0.0030981
284 | 0:47 | 5.677 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 6.7207 | 0.067207 | 0.067207 | 5.677 | 0.00052183 | [13 empty] | 0.97627 | 1 | 0.97471 | 0.9341 | 0.89635 | 0.86092 | 0.81293 | 0.75505 | 0.698 | 0.64067 | 0.57105 | 0.48075 | 0.35204 | 0.16076 | -0.026638 | -0.14482 | -0.20607 | -0.24493 | -0.28149 | -0.31989 | -0.34994 | -0.37199 | -0.38879 | -0.41403 | -0.45133 | -0.49551 | -0.54598 | -0.59817 | -0.64957 | -0.69929 | -0.74855 | 0.0033603 | -0.0055267 | -0.00027634 | -0.00027634 | 0 | 0 | 0.002982 | 0.05 | -0.6061 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.39417 | 0.44761 | 0.50139 | 0.56064 | 0.62642 | 0.68582 | 0.72737 | 0.7533 | 0.77487 | 0.80094 | 0.82979 | 0.86725 | 0.92069 | 0.98895 | 0.93271 | 0.84877 | 0.77058 | 0.70104 | 0.64288 | 0.59265 | 0.54354 | 0.48346 | 0.40815 | 0.32752 | 0.24417 | 0.16856 | 0.10918 | 0.070031 | 0.047929 | 0.041034 | 0.050787 | 0.98895 | 13 | Slope | 0.6 | 0.46472 | 0.48254 | 0.48935 | 0.49799 | 0.50881 | 0.5175 | 0.52023 | 0.51777 | 0.51385 | 0.51142 | 0.50993 | 0.5113 | 0.51801 | 0.52965 | 0.49979 | 0.4607 | 0.42353 | 0.38924 | 0.35874 | 0.33088 | 0.3034 | 0.27226 | 0.23605 | 0.19806 | 0.15917 | 0.12285 | 0.091948 | 0.067788 | 0.04931 | 0.0359 | 0.02804 | 0.52965 | 13 | 0.98895 | Slope | 0.6 | 0.067207 |  | 0.66733 | 0 | 0.98895 | Slope | 2 | 0.6 | 0 | 20 | -20 | 0.00052183 | 0.00025456 | 0.002982
285 | 0:47 | 6.7207 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 7.8276 | 0.078276 | 0.078276 | 6.7207 | 0.00055347 | [13 empty] | 0.97471 | 1 | 0.97372 | 0.9329 | 0.89104 | 0.84284 | 0.78081 | 0.71566 | 0.65167 | 0.58657 | 0.50339 | 0.37336 | 0.17972 | 0.00070843 | -0.10657 | -0.16536 | -0.19851 | -0.23225 | -0.26774 | -0.30367 | -0.32786 | -0.34259 | -0.35717 | -0.38104 | -0.42031 | -0.46844 | -0.52318 | -0.57828 | -0.63202 | -0.68425 | -0.75834 | 0.0039138 | -0.0049888 | -0.00024944 | -0.00024944 | 0 | 0 | 0.0028256 | 0.05 | -0.55267 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.44758 | 0.50136 | 0.56061 | 0.6264 | 0.6858 | 0.72734 | 0.75327 | 0.77485 | 0.80091 | 0.82976 | 0.86722 | 0.92067 | 0.98893 | 0.93274 | 0.8488 | 0.77061 | 0.70107 | 0.64291 | 0.59267 | 0.54357 | 0.48349 | 0.40818 | 0.32754 | 0.24419 | 0.16859 | 0.1092 | 0.070058 | 0.047956 | 0.041061 | 0.050814 | 0.040998 | 0.98893 | 12 | Slope | 0.63333 | 0.48253 | 0.50045 | 0.50909 | 0.51991 | 0.5286 | 0.53134 | 0.52887 | 0.52495 | 0.52253 | 0.52103 | 0.52241 | 0.52911 | 0.54075 | 0.51091 | 0.47182 | 0.43465 | 0.40036 | 0.36986 | 0.342 | 0.31452 | 0.28338 | 0.24717 | 0.20918 | 0.17029 | 0.13397 | 0.10307 | 0.078908 | 0.06043 | 0.04702 | 0.03916 | 0.024777 | 0.54075 | 12 | 0.98893 | Slope | 0.63333 | 0.078276 |  | 0.61253 | 0 | 0.98893 | Slope | 2 | 0.63333 | 0 | 20 | -20 | 0.00055347 | 0.00025133 | 0.0028256
286 | 0:47 | 7.8276 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 8.0295 | 0.080295 | 0.080295 | 7.8276 | 0.00010094 | [13 empty] | 0.97372 | 1 | 0.97061 | 0.9227 | 0.86902 | 0.80956 | 0.73936 | 0.66133 | 0.5843 | 0.49861 | 0.36385 | 0.15949 | -0.020734 | -0.11293 | -0.15206 | -0.17489 | -0.19781 | -0.22787 | -0.26043 | -0.29257 | -0.31152 | -0.32379 | -0.33664 | -0.36066 | -0.40115 | -0.4509 | -0.50707 | -0.56357 | -0.6188 | -0.70451 | -0.77876 | 0.0040148 | -0.0043964 | -0.00021982 | -0.00021982 | 0 | 0 | 0.0026091 | 0.05 | -0.49888 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.50133 | 0.56058 | 0.62637 | 0.68577 | 0.72731 | 0.75325 | 0.77482 | 0.80088 | 0.82973 | 0.86719 | 0.92064 | 0.9889 | 0.93277 | 0.84883 | 0.77063 | 0.7011 | 0.64294 | 0.5927 | 0.5436 | 0.48352 | 0.40821 | 0.32757 | 0.24422 | 0.16862 | 0.10923 | 0.070088 | 0.047985 | 0.041091 | 0.050844 | 0.041027 | 0.048278 | 0.9889 | 11 | Slope | 0.66667 | 0.50044 | 0.52019 | 0.53101 | 0.5397 | 0.54244 | 0.53997 | 0.53605 | 0.53363 | 0.53213 | 0.53351 | 0.54021 | 0.55185 | 0.52203 | 0.48294 | 0.44577 | 0.41148 | 0.38098 | 0.35312 | 0.32564 | 0.29451 | 0.25829 | 0.2203 | 0.18141 | 0.14509 | 0.11419 | 0.090029 | 0.071551 | 0.058141 | 0.050281 | 0.035898 | 0.027204 | 0.55185 | 11 | 0.9889 | Slope | 0.66667 | 0.080295 |  | 0.60254 | 0 | 0.9889 | Slope | 2 | 0.66667 | 0 | 20 | -20 | 0.00010094 | 0.00024657 | 0.0026091
287 | 0:48 | 8.0295 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 6.8408 | 0.068408 | 0.068408 | 8.0295 | 0.00059436 | [13 empty] | 0.97061 | 1 | 0.96315 | 0.90155 | 0.83582 | 0.76766 | 0.67942 | 0.58188 | 0.47614 | 0.33154 | 0.12554 | -0.055553 | -0.13912 | -0.15952 | -0.16019 | -0.17166 | -0.1904 | -0.2175 | -0.24711 | -0.27495 | -0.29138 | -0.30169 | -0.31404 | -0.33812 | -0.37938 | -0.43027 | -0.48825 | -0.54682 | -0.64504 | -0.73311 | -0.80023 | 0.0034204 | -0.0037385 | -0.00018693 | -0.00018693 | 0 | 0 | 0.0023392 | 0.05 | -0.43964 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.56055 | 0.62633 | 0.68573 | 0.72728 | 0.75321 | 0.77478 | 0.80085 | 0.8297 | 0.86716 | 0.9206 | 0.98886 | 0.9328 | 0.84886 | 0.77067 | 0.70113 | 0.64297 | 0.59274 | 0.54363 | 0.48355 | 0.40824 | 0.32761 | 0.24426 | 0.16865 | 0.10927 | 0.070121 | 0.048018 | 0.041124 | 0.050877 | 0.04106 | 0.048311 | 0.076982 | 0.98886 | 10 | Slope | 0.7 | 0.52018 | 0.54211 | 0.5508 | 0.55354 | 0.55107 | 0.54715 | 0.54473 | 0.54323 | 0.54461 | 0.55131 | 0.56295 | 0.53316 | 0.49406 | 0.45689 | 0.4226 | 0.3921 | 0.36425 | 0.33677 | 0.30563 | 0.26941 | 0.23142 | 0.19253 | 0.15622 | 0.12531 | 0.10115 | 0.082673 | 0.069263 | 0.061403 | 0.04702 | 0.038326 | 0.036772 | 0.56295 | 10 | 0.98886 | Slope | 0.7 | 0.068408 |  | 0.66138 | 0 | 0.98886 | Slope | 2 | 0.7 | 0 | 20 | -20 | 0.00059436 | 0.00024019 | 0.0023392
288 | 0:48 | 6.8408 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 4.4218 | 0.044218 | 0.044218 | 6.8408 | 0.0012095 | [13 empty] | 0.96315 | 1 | 0.95306 | 0.87828 | 0.80217 | 0.71443 | 0.60225 | 0.46618 | 0.28635 | 0.065395 | -0.11189 | -0.19061 | -0.19997 | -0.18014 | -0.16671 | -0.17153 | -0.18619 | -0.2119 | -0.23935 | -0.26471 | -0.27873 | -0.28674 | -0.29611 | -0.31712 | -0.35687 | -0.40764 | -0.46647 | -0.57211 | -0.67355 | -0.75491 | -0.81521 | 0.0022109 | -0.0031445 | -0.00015723 | -0.00015723 | 0 | 0 | 0.0020728 | 0.05 | -0.37385 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.6263 | 0.6857 | 0.72725 | 0.75318 | 0.77475 | 0.80082 | 0.82967 | 0.86713 | 0.92057 | 0.98883 | 0.93283 | 0.84889 | 0.7707 | 0.70116 | 0.643 | 0.59277 | 0.54366 | 0.48358 | 0.40827 | 0.32764 | 0.24429 | 0.16868 | 0.1093 | 0.070151 | 0.048048 | 0.041153 | 0.050906 | 0.04109 | 0.048341 | 0.077012 | 0.13445 | 0.98883 | 9 | Slope | 0.73333 | 0.5421 | 0.5619 | 0.56464 | 0.56217 | 0.55825 | 0.55583 | 0.55433 | 0.55571 | 0.56241 | 0.57406 | 0.54428 | 0.50519 | 0.46801 | 0.43372 | 0.40322 | 0.37537 | 0.34789 | 0.31675 | 0.28054 | 0.24255 | 0.20365 | 0.16734 | 0.13643 | 0.11227 | 0.093794 | 0.080384 | 0.072524 | 0.058141 | 0.049447 | 0.047893 | 0.055929 | 0.57406 | 9 | 0.98883 | Slope | 0.73333 | 0.044218 |  | 0.78112 | 0 | 0.98883 | Slope | 2 | 0.73333 | 0 | 20 | -20 | 0.0012095 | 0.00023241 | 0.0020728
289 | 0:48 | 4.4218 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.2558 | 0.022558 | 0.022558 | 4.4218 | 0.001083 | [13 empty] | 0.95306 | 1 | 0.94432 | 0.8584 | 0.76422 | 0.65495 | 0.50139 | 0.27599 | 0.00015483 | -0.1929 | -0.26852 | -0.27523 | -0.24616 | -0.21034 | -0.18698 | -0.18634 | -0.20165 | -0.22799 | -0.2523 | -0.2743 | -0.28342 | -0.28463 | -0.28582 | -0.29996 | -0.33507 | -0.38203 | -0.482 | -0.58732 | -0.68084 | -0.75271 | -0.80461 | 0.0011279 | -0.0027291 | -0.00013645 | -0.00013645 | 0 | 0 | 0.0018796 | 0.05 | -0.31445 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.68568 | 0.72723 | 0.75316 | 0.77473 | 0.8008 | 0.82965 | 0.86711 | 0.92055 | 0.98881 | 0.93285 | 0.84891 | 0.77072 | 0.70118 | 0.64302 | 0.59279 | 0.54368 | 0.4836 | 0.40829 | 0.32766 | 0.24431 | 0.1687 | 0.10932 | 0.070171 | 0.048069 | 0.041174 | 0.050927 | 0.041111 | 0.048361 | 0.077032 | 0.13447 | 0.21538 | 0.98881 | 8 | Slope | 0.76667 | 0.56189 | 0.57574 | 0.57328 | 0.56936 | 0.56693 | 0.56544 | 0.56681 | 0.57352 | 0.58516 | 0.5554 | 0.5163 | 0.47913 | 0.44484 | 0.41434 | 0.38648 | 0.35901 | 0.32787 | 0.29165 | 0.25366 | 0.21477 | 0.17846 | 0.14755 | 0.12339 | 0.10491 | 0.091502 | 0.083642 | 0.069259 | 0.060565 | 0.059011 | 0.067047 | 0.082906 | 0.58516 | 8 | 0.98881 | Slope | 0.76667 | 0.022558 |  | 0.88834 | 0 | 0.98881 | Slope | 2 | 0.76667 | 0 | 20 | -20 | 0.001083 | 0.00022338 | 0.0018796
290 | 0:48 | 2.2558 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 0.97832 | 0.0097832 | 0.0097832 | 2.2558 | 0.00063872 | [13 empty] | 0.94432 | 1 | 0.93712 | 0.83654 | 0.72352 | 0.57716 | 0.32807 | -0.017292 | -0.26863 | -0.3591 | -0.36739 | -0.33974 | -0.29598 | -0.25001 | -0.22098 | -0.22303 | -0.24124 | -0.26381 | -0.28369 | -0.29843 | -0.29802 | -0.28789 | -0.27868 | -0.28373 | -0.31034 | -0.38984 | -0.48415 | -0.57858 | -0.65874 | -0.7184 | -0.74894 | 0.00048916 | -0.0024697 | -0.00012349 | -0.00012349 | 0 | 0 | 0.0017579 | 0.05 | -0.27291 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.72722 | 0.75315 | 0.77472 | 0.80078 | 0.82964 | 0.86709 | 0.92054 | 0.9888 | 0.93287 | 0.84892 | 0.77073 | 0.70119 | 0.64304 | 0.5928 | 0.5437 | 0.48361 | 0.40831 | 0.32767 | 0.24432 | 0.16871 | 0.10933 | 0.070184 | 0.048082 | 0.041187 | 0.05094 | 0.041124 | 0.048374 | 0.077045 | 0.13449 | 0.2154 | 0.32365 | 0.9888 | 7 | Slope | 0.8 | 0.57574 | 0.58438 | 0.58046 | 0.57804 | 0.57655 | 0.57792 | 0.58462 | 0.59627 | 0.56651 | 0.52742 | 0.49024 | 0.45595 | 0.42546 | 0.3976 | 0.37012 | 0.33898 | 0.30277 | 0.26478 | 0.22588 | 0.18957 | 0.15867 | 0.13451 | 0.11603 | 0.10262 | 0.094758 | 0.080375 | 0.07168 | 0.070126 | 0.078163 | 0.094021 | 0.11899 | 0.59627 | 7 | 0.9888 | Slope | 0.8 | 0.0097832 |  | 0.95157 | 0 | 0.9888 | Slope | 2 | 0.8 | 0 | 20 | -20 | 0.00063872 | 0.00021329 | 0.0017579
291 | 0:48 | 0.97832 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 0.72553 | 0.0072553 | 0.0072553 | 0.97832 | 0.0001264 | [13 empty] | 0.93712 | 1 | 0.92852 | 0.81076 | 0.66443 | 0.42824 | 0.045177 | -0.27961 | -0.41957 | -0.44556 | -0.42475 | -0.38727 | -0.33624 | -0.2856 | -0.25916 | -0.26412 | -0.27883 | -0.29699 | -0.30967 | -0.31505 | -0.30357 | -0.28279 | -0.26323 | -0.25741 | -0.31339 | -0.38478 | -0.46639 | -0.54609 | -0.61384 | -0.65255 | -0.66397 | 0.00036277 | -0.002254 | -0.0001127 | -0.0001127 | 0 | 0 | 0.0016591 | 0.05 | -0.24697 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.75314 | 0.77471 | 0.80077 | 0.82962 | 0.86708 | 0.92053 | 0.98879 | 0.93288 | 0.84894 | 0.77074 | 0.7012 | 0.64305 | 0.59281 | 0.54371 | 0.48362 | 0.40832 | 0.32768 | 0.24433 | 0.16872 | 0.10934 | 0.070195 | 0.048092 | 0.041198 | 0.050951 | 0.041134 | 0.048385 | 0.077056 | 0.1345 | 0.21541 | 0.32366 | 0.45283 | 0.98879 | 6 | Slope | 0.83333 | 0.58438 | 0.59157 | 0.58915 | 0.58765 | 0.58903 | 0.59573 | 0.60737 | 0.57763 | 0.53853 | 0.50136 | 0.46707 | 0.43657 | 0.40871 | 0.38124 | 0.3501 | 0.31388 | 0.27589 | 0.237 | 0.20069 | 0.16978 | 0.14562 | 0.12714 | 0.11373 | 0.10587 | 0.091489 | 0.082795 | 0.081241 | 0.089277 | 0.10514 | 0.13011 | 0.16205 | 0.60737 | 6 | 0.98879 | Slope | 0.83333 | 0.0072553 |  | 0.96409 | 0 | 0.98879 | Slope | 2 | 0.83333 | 0 | 20 | -20 | 0.0001264 | 0.00020273 | 0.0016591
292 | 0:48 | 0.72553 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 0.099662 | 0.00099662 | 0.00099662 | 0.72553 | 0.00031294 | [13 empty] | 0.92852 | 1 | 0.91528 | 0.76409 | 0.52893 | 0.14986 | -0.22425 | -0.42688 | -0.49518 | -0.49227 | -0.46575 | -0.4233 | -0.36717 | -0.31611 | -0.29082 | -0.29277 | -0.30371 | -0.31575 | -0.32028 | -0.31577 | -0.29392 | -0.26204 | -0.22979 | -0.25578 | -0.30284 | -0.35944 | -0.42575 | -0.49498 | -0.54388 | -0.56358 | -0.56248 | 4.9831e-05 | -0.0019934 | -9.967e-05 | -9.967e-05 | 0 | 0 | 0.0015367 | 0.05 | -0.2254 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.7747 | 0.80076 | 0.82961 | 0.86707 | 0.92052 | 0.98878 | 0.93289 | 0.84895 | 0.77075 | 0.70122 | 0.64306 | 0.59282 | 0.54372 | 0.48364 | 0.40833 | 0.32769 | 0.24434 | 0.16874 | 0.10935 | 0.070208 | 0.048105 | 0.041211 | 0.050964 | 0.041147 | 0.048398 | 0.077069 | 0.13451 | 0.21542 | 0.32367 | 0.45284 | 0.59227 | 0.98878 | 5 | Slope | 0.86667 | 0.59157 | 0.60025 | 0.59876 | 0.60013 | 0.60684 | 0.61848 | 0.58874 | 0.54965 | 0.51247 | 0.47818 | 0.44769 | 0.41983 | 0.39235 | 0.36121 | 0.325 | 0.28701 | 0.24811 | 0.2118 | 0.1809 | 0.15674 | 0.13826 | 0.12485 | 0.11699 | 0.1026 | 0.093911 | 0.092356 | 0.10039 | 0.11625 | 0.14122 | 0.17317 | 0.20853 | 0.61848 | 5 | 0.98878 | Slope | 0.86667 | 0.00099662 |  | 0.99507 | 0 | 0.98878 | Slope | 2 | 0.86667 | 0 | 20 | -20 | 0.00031294 | 0.00019278 | 0.0015367
293 | 0:49 | 0.099662 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -0.35035 | -0.0035035 | -0.0035035 | 0.099662 | 0.00022501 | [13 empty] | 0.91528 | 1 | 0.89191 | 0.65584 | 0.26846 | -0.11795 | -0.36899 | -0.49191 | -0.52978 | -0.52528 | -0.49677 | -0.44939 | -0.38919 | -0.33594 | -0.30797 | -0.30669 | -0.3128 | -0.31831 | -0.31443 | -0.30088 | -0.26826 | -0.22293 | -0.22312 | -0.23842 | -0.2683 | -0.30794 | -0.36461 | -0.41733 | -0.4486 | -0.45517 | -0.4431 | -0.00017517 | -0.0017049 | -8.5244e-05 | -8.5244e-05 | 0 | 0 | 0.0014025 | 0.05 | -0.19934 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.80075 | 0.8296 | 0.86705 | 0.9205 | 0.98876 | 0.9329 | 0.84896 | 0.77077 | 0.70123 | 0.64307 | 0.59284 | 0.54373 | 0.48365 | 0.40834 | 0.32771 | 0.24436 | 0.16875 | 0.10937 | 0.070223 | 0.04812 | 0.041225 | 0.050978 | 0.041162 | 0.048413 | 0.077084 | 0.13453 | 0.21544 | 0.32369 | 0.45286 | 0.59228 | 0.73613 | 0.98876 | 4 | Slope | 0.9 | 0.60025 | 0.60987 | 0.61124 | 0.61794 | 0.62959 | 0.59986 | 0.56077 | 0.52359 | 0.4893 | 0.4588 | 0.43095 | 0.40347 | 0.37233 | 0.33611 | 0.29813 | 0.25923 | 0.22292 | 0.19201 | 0.16785 | 0.14937 | 0.13596 | 0.1281 | 0.11372 | 0.10503 | 0.10347 | 0.11151 | 0.12737 | 0.15234 | 0.18429 | 0.21965 | 0.25649 | 0.62959 | 4 | 0.98876 | Slope | 0.9 | 0.0035035 |  | 0.98266 | 0 | 0.98876 | Slope | 2 | 0.9 | 0 | 20 | -20 | 0.00022501 | 0.000185 | 0.0014025
294 | 0:49 | -0.35035 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -0.85568 | -0.0085568 | -0.0085568 | -0.35035 | 0.00025267 | [13 empty] | 0.89191 | 1 | 0.83436 | 0.44744 | 0.038076 | -0.23171 | -0.4004 | -0.49311 | -0.53716 | -0.53691 | -0.50416 | -0.44583 | -0.37537 | -0.31804 | -0.28691 | -0.28391 | -0.2879 | -0.28975 | -0.27989 | -0.25823 | -0.21359 | -0.20531 | -0.19428 | -0.18915 | -0.20281 | -0.23581 | -0.281 | -0.31925 | -0.33754 | -0.33362 | -0.31028 | -0.00042784 | -0.0013303 | -6.6515e-05 | -6.6515e-05 | 0 | 0 | 0.0012403 | 0.05 | -0.17049 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.82958 | 0.86704 | 0.92048 | 0.98874 | 0.93292 | 0.84898 | 0.77079 | 0.70125 | 0.64309 | 0.59286 | 0.54375 | 0.48367 | 0.40836 | 0.32773 | 0.24438 | 0.16877 | 0.10939 | 0.070241 | 0.048139 | 0.041244 | 0.050997 | 0.041181 | 0.048431 | 0.077102 | 0.13454 | 0.21545 | 0.32371 | 0.45288 | 0.5923 | 0.73615 | 0.88166 | 0.98874 | 3 | Slope | 0.93333 | 0.60986 | 0.62235 | 0.62905 | 0.64069 | 0.61097 | 0.57188 | 0.53471 | 0.50042 | 0.46992 | 0.44206 | 0.41458 | 0.38345 | 0.34723 | 0.30924 | 0.27035 | 0.23403 | 0.20313 | 0.17897 | 0.16049 | 0.14708 | 0.13922 | 0.12484 | 0.11614 | 0.11459 | 0.12263 | 0.13848 | 0.16346 | 0.1954 | 0.23077 | 0.26761 | 0.305 | 0.64069 | 3 | 0.98874 | Slope | 0.93333 | 0.0085568 |  | 0.95764 | 0 | 0.98874 | Slope | 2 | 0.93333 | 0 | 20 | -20 | 0.00025267 | 0.00018097 | 0.0012403
295 | 0:49 | -0.85568 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.3416 | -0.023416 | -0.023416 | -0.85568 | 0.00074296 | [13 empty] | 0.83436 | 1 | 0.74855 | 0.33992 | 0.043716 | -0.14866 | -0.29324 | -0.40903 | -0.47244 | -0.47234 | -0.418 | -0.33629 | -0.26005 | -0.19962 | -0.17284 | -0.17801 | -0.18978 | -0.19466 | -0.18349 | -0.15802 | -0.16205 | -0.14765 | -0.11478 | -0.098662 | -0.11565 | -0.14813 | -0.18484 | -0.21069 | -0.22166 | -0.20961 | -0.17494 | -0.0011708 | -0.00079584 | -3.9792e-05 | -3.9792e-05 | 0 | 0 | 0.0010717 | 0.05 | -0.13303 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.86701 | 0.92046 | 0.98872 | 0.93295 | 0.84901 | 0.77081 | 0.70128 | 0.64312 | 0.59288 | 0.54378 | 0.4837 | 0.40839 | 0.32775 | 0.2444 | 0.1688 | 0.10941 | 0.070268 | 0.048165 | 0.041271 | 0.051024 | 0.041207 | 0.048458 | 0.077129 | 0.13457 | 0.21548 | 0.32373 | 0.4529 | 0.59233 | 0.73618 | 0.88168 | 0.97219 | 0.98872 | 2 | Slope | 0.96667 | 0.62234 | 0.64015 | 0.65179 | 0.62209 | 0.583 | 0.54583 | 0.51154 | 0.48104 | 0.45318 | 0.4257 | 0.39457 | 0.35835 | 0.32036 | 0.28147 | 0.24515 | 0.21425 | 0.19009 | 0.17161 | 0.1582 | 0.15034 | 0.13596 | 0.12726 | 0.12571 | 0.13375 | 0.1496 | 0.17458 | 0.20652 | 0.24189 | 0.27873 | 0.31612 | 0.33518 | 0.65179 | 2 | 0.98872 | Slope | 0.96667 | 0.023416 |  | 0.88409 | 0 | 0.98872 | Slope | 2 | 0.96667 | 0 | 20 | -20 | 0.00074296 | 0.00018208 | 0.0010717
296 | 0:49 | -2.3416 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -3.8107 | -0.038107 | -0.038107 | -2.3416 | 0.00073456 | [13 empty] | 0.74855 | 1 | 0.77627 | 0.49998 | 0.29527 | 0.13581 | -0.030918 | -0.1686 | -0.23315 | -0.20366 | -0.12163 | -0.045737 | 0.020884 | 0.059759 | 0.06163 | 0.032831 | 0.0055228 | -0.01047 | -0.011049 | -0.042018 | -0.05368 | -0.030743 | -0.0087205 | -0.015316 | -0.051494 | -0.085037 | -0.10985 | -0.13199 | -0.14239 | -0.12972 | -0.1027 | -0.0019054 | -0.00011323 | -5.6613e-06 | -5.6613e-06 | 0 | 0 | 0.0010584 | 0.05 | -0.079584 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.92042 | 0.98868 | 0.93298 | 0.84904 | 0.77085 | 0.70131 | 0.64315 | 0.59292 | 0.54381 | 0.48373 | 0.40842 | 0.32779 | 0.24444 | 0.16883 | 0.10945 | 0.070302 | 0.048199 | 0.041305 | 0.051058 | 0.041241 | 0.048492 | 0.077163 | 0.13461 | 0.21551 | 0.32377 | 0.45294 | 0.59236 | 0.73621 | 0.88172 | 0.97216 | 0.831 | 0.98868 | 1 | Slope | 1 | 0.64014 | 0.66289 | 0.63322 | 0.59413 | 0.55695 | 0.52266 | 0.49216 | 0.46431 | 0.43683 | 0.40569 | 0.36947 | 0.33148 | 0.29259 | 0.25628 | 0.22537 | 0.20121 | 0.18273 | 0.16932 | 0.16146 | 0.14708 | 0.13839 | 0.13683 | 0.14487 | 0.16073 | 0.1857 | 0.21765 | 0.25301 | 0.28985 | 0.32724 | 0.34628 | 0.28811 | 0.66289 | 1 | 0.98868 | Slope | 1 | 0.038107 |  | 0.81137 | 0 | 0.98868 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00073456 | 0.00018895 | 0.0010584
297 | 0:49 | -3.8107 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.4819 | -0.054819 | -0.054819 | -3.8107 | 0.00083556 | [13 empty] | 0.77627 | 1 | 0.86543 | 0.6956 | 0.54803 | 0.39316 | 0.23352 | 0.11887 | 0.097686 | 0.15273 | 0.21521 | 0.26827 | 0.29908 | 0.30105 | 0.27252 | 0.22738 | 0.18796 | 0.1561 | 0.10936 | 0.067953 | 0.055724 | 0.049156 | 0.032316 | -0.0075691 | -0.051897 | -0.075878 | -0.098575 | -0.12204 | -0.13651 | -0.13629 | -0.13326 | -0.0027409 | 0.0006701 | 3.3505e-05 | 3.3505e-05 | 0 | 0 | 0.0012555 | 0.05 | -0.011323 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.98864 | 0.93302 | 0.84908 | 0.77089 | 0.70135 | 0.64319 | 0.59296 | 0.54385 | 0.48377 | 0.40846 | 0.32783 | 0.24448 | 0.16887 | 0.10949 | 0.070341 | 0.048239 | 0.041344 | 0.051097 | 0.041281 | 0.048531 | 0.077202 | 0.13464 | 0.21555 | 0.32381 | 0.45298 | 0.5924 | 0.73625 | 0.88176 | 0.97212 | 0.83096 | 0.70424 | 0.98864 | 0 | Slope | 1 | 0.66288 | 0.64434 | 0.60525 | 0.56807 | 0.53378 | 0.50329 | 0.47543 | 0.44795 | 0.41681 | 0.3806 | 0.34261 | 0.30371 | 0.2674 | 0.2365 | 0.21234 | 0.19386 | 0.18045 | 0.17259 | 0.1582 | 0.14951 | 0.14796 | 0.15599 | 0.17185 | 0.19682 | 0.22877 | 0.26413 | 0.30097 | 0.33836 | 0.35737 | 0.29921 | 0.24586 | 0.66288 | 0 | 0.98864 | Slope | 1 | 0.054819 |  | 0.72865 | 0 | 0.98864 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00083556 | 0.00020085 | 0.0012555
298 | 0:49 | -5.4819 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.1753 | -0.071753 | -0.071753 | -5.4819 | 0.00084673 | [13 empty] | 0.86543 | 1 | 0.9181 | 0.80196 | 0.6722 | 0.53585 | 0.41337 | 0.35442 | 0.36639 | 0.40451 | 0.44365 | 0.46217 | 0.45716 | 0.42903 | 0.38529 | 0.3326 | 0.28182 | 0.22424 | 0.16939 | 0.12768 | 0.085508 | 0.040742 | -0.013007 | -0.065578 | -0.1032 | -0.12807 | -0.1538 | -0.18128 | -0.20303 | -0.21367 | -0.22129 | -0.0035877 | 0.0015095 | 7.5476e-05 | 7.5476e-05 | 0 | 0 | 0.0016088 | 0.05 | 0.06701 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.93307 | 0.84912 | 0.77093 | 0.70139 | 0.64324 | 0.593 | 0.5439 | 0.48381 | 0.4085 | 0.32787 | 0.24452 | 0.16891 | 0.10953 | 0.070383 | 0.048281 | 0.041386 | 0.051139 | 0.041323 | 0.048573 | 0.077244 | 0.13469 | 0.2156 | 0.32385 | 0.45302 | 0.59244 | 0.73629 | 0.8818 | 0.97208 | 0.83092 | 0.7042 | 0.59979 | 0.97208 | 27 | Slope | 0.13333 | 0.64436 | 0.61637 | 0.5792 | 0.54491 | 0.51441 | 0.48655 | 0.45908 | 0.42794 | 0.39172 | 0.35373 | 0.31484 | 0.27853 | 0.24762 | 0.22346 | 0.20498 | 0.19157 | 0.18371 | 0.16933 | 0.16064 | 0.15908 | 0.16712 | 0.18298 | 0.20795 | 0.23989 | 0.27526 | 0.3121 | 0.34949 | 0.36847 | 0.31031 | 0.25695 | 0.21104 | 0.64436 | 0 | 0.93307 | Slope | 1 | 0.071753 |  | 0.64482 | 0 | 0.93307 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00084673 | 0.00021632 | 0.0016088
299 | 0:50 | -7.1753 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -8.5399 | -0.085399 | -0.085399 | -7.1753 | 0.00068229 | [13 empty] | 0.9181 | 1 | 0.94193 | 0.84263 | 0.72807 | 0.61902 | 0.54267 | 0.51765 | 0.52562 | 0.54976 | 0.56397 | 0.55612 | 0.52764 | 0.48621 | 0.43495 | 0.37376 | 0.31099 | 0.24614 | 0.18909 | 0.12241 | 0.050234 | -0.026308 | -0.094206 | -0.14491 | -0.18466 | -0.21443 | -0.24574 | -0.27706 | -0.298 | -0.30361 | -0.30476 | -0.0042699 | 0.0022915 | 0.00011457 | 0.00011457 | 0 | 0 | 0.0019645 | 0.05 | 0.15095 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.84916 | 0.77097 | 0.70143 | 0.64327 | 0.59304 | 0.54393 | 0.48385 | 0.40854 | 0.32791 | 0.24456 | 0.16895 | 0.10957 | 0.070422 | 0.04832 | 0.041425 | 0.051178 | 0.041362 | 0.048612 | 0.077283 | 0.13473 | 0.21563 | 0.32389 | 0.45306 | 0.59248 | 0.73633 | 0.88184 | 0.97204 | 0.83088 | 0.70416 | 0.59975 | 0.51617 | 0.97204 | 26 | Slope | 0.16667 | 0.61639 | 0.59032 | 0.55603 | 0.52554 | 0.49768 | 0.4702 | 0.43906 | 0.40285 | 0.36486 | 0.32596 | 0.28965 | 0.25875 | 0.23459 | 0.21611 | 0.2027 | 0.19484 | 0.18045 | 0.17176 | 0.17021 | 0.17824 | 0.1941 | 0.21907 | 0.25102 | 0.28638 | 0.32322 | 0.36061 | 0.37957 | 0.32141 | 0.26805 | 0.22214 | 0.18317 | 0.61639 | 0 | 0.84916 | Slope | 1 | 0.085399 |  | 0.57728 | 0 | 0.84916 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00068229 | 0.00023369 | 0.0019645
300 | 0:50 | -8.5399 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -8.8924 | -0.088924 | -0.088924 | -8.5399 | 0.00017625 | [13 empty] | 0.94193 | 1 | 0.95026 | 0.86168 | 0.766 | 0.68949 | 0.64163 | 0.62126 | 0.62427 | 0.63198 | 0.6264 | 0.60017 | 0.56036 | 0.51141 | 0.45146 | 0.38522 | 0.31476 | 0.24574 | 0.16566 | 0.073229 | -0.027065 | -0.11788 | -0.18719 | -0.24162 | -0.28652 | -0.32296 | -0.35704 | -0.38134 | -0.3872 | -0.37954 | -0.36887 | -0.0044462 | 0.0029868 | 0.00014934 | 0.00014934 | 0 | 0 | 0.002279 | 0.05 | 0.22915 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.771 | 0.70147 | 0.64331 | 0.59307 | 0.54397 | 0.48388 | 0.40858 | 0.32794 | 0.24459 | 0.16899 | 0.1096 | 0.070457 | 0.048354 | 0.04146 | 0.051213 | 0.041396 | 0.048647 | 0.077318 | 0.13476 | 0.21567 | 0.32392 | 0.45309 | 0.59252 | 0.73637 | 0.88187 | 0.97201 | 0.83085 | 0.70412 | 0.59971 | 0.51614 | 0.45334 | 0.97201 | 25 | Slope | 0.2 | 0.59033 | 0.56716 | 0.53666 | 0.5088 | 0.48132 | 0.45018 | 0.41397 | 0.37598 | 0.33709 | 0.30077 | 0.26987 | 0.24571 | 0.22723 | 0.21382 | 0.20596 | 0.19158 | 0.18288 | 0.18133 | 0.18936 | 0.20522 | 0.2302 | 0.26214 | 0.29751 | 0.33434 | 0.37174 | 0.39067 | 0.33251 | 0.27915 | 0.23324 | 0.19427 | 0.16222 | 0.59033 | 0 | 0.771 | Slope | 1 | 0.088924 |  | 0.55983 | 0 | 0.771 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00017625 | 0.00025169 | 0.002279
301 | 0:50 | -8.8924 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -8.9033 | -0.089033 | -0.089033 | -8.8924 | 5.4824e-06 | [13 empty] | 0.95026 | 1 | 0.956 | 0.87925 | 0.80337 | 0.74521 | 0.70541 | 0.68684 | 0.68269 | 0.67836 | 0.65993 | 0.62517 | 0.57914 | 0.5225 | 0.45852 | 0.38489 | 0.30934 | 0.22022 | 0.11741 | 4.1416e-06 | -0.11411 | -0.20844 | -0.28269 | -0.3429 | -0.39447 | -0.43305 | -0.45757 | -0.46282 | -0.45264 | -0.43245 | -0.41501 | -0.0044517 | 0.0035684 | 0.00017842 | 0.00017842 | 0 | 0 | 0.002509 | 0.05 | 0.29868 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.7015 | 0.64334 | 0.5931 | 0.544 | 0.48391 | 0.40861 | 0.32797 | 0.24462 | 0.16901 | 0.10963 | 0.070486 | 0.048383 | 0.041489 | 0.051242 | 0.041425 | 0.048676 | 0.077347 | 0.13479 | 0.2157 | 0.32395 | 0.45312 | 0.59255 | 0.73639 | 0.8819 | 0.97198 | 0.83082 | 0.70409 | 0.59968 | 0.51611 | 0.45331 | 0.40254 | 0.97198 | 24 | Slope | 0.23333 | 0.56717 | 0.54778 | 0.51992 | 0.49244 | 0.4613 | 0.42509 | 0.3871 | 0.34821 | 0.31189 | 0.28099 | 0.25683 | 0.23835 | 0.22494 | 0.21708 | 0.2027 | 0.194 | 0.19245 | 0.20049 | 0.21634 | 0.24132 | 0.27326 | 0.30863 | 0.34546 | 0.38286 | 0.40177 | 0.34361 | 0.29025 | 0.24434 | 0.20537 | 0.17332 | 0.14529 | 0.56717 | 0 | 0.7015 | Slope | 1 | 0.089033 |  | 0.55929 | 0 | 0.7015 | Slope | 2 | 1 | 0 | 20 | -20 | 5.4824e-06 | 0.00026945 | 0.002509
302 | 0:50 | -8.9033 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -8.9143 | -0.089143 | -0.089143 | -8.9033 | 5.4824e-06 | [13 empty] | 0.956 | 1 | 0.96133 | 0.89554 | 0.83124 | 0.782 | 0.74765 | 0.72853 | 0.7183 | 0.70513 | 0.67992 | 0.64003 | 0.5875 | 0.52705 | 0.45603 | 0.37726 | 0.28373 | 0.17386 | 0.047759 | -0.083319 | -0.20219 | -0.30221 | -0.38273 | -0.44994 | -0.50297 | -0.53002 | -0.53297 | -0.5206 | -0.49714 | -0.47097 | -0.44935 | -0.0044571 | 0.0040708 | 0.00020354 | 0.00020354 | 0 | 0 | 0.0026876 | 0.05 | 0.35684 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.64336 | 0.59313 | 0.54402 | 0.48394 | 0.40863 | 0.328 | 0.24465 | 0.16904 | 0.10966 | 0.070511 | 0.048409 | 0.041514 | 0.051267 | 0.041451 | 0.048701 | 0.077372 | 0.13481 | 0.21572 | 0.32398 | 0.45315 | 0.59257 | 0.73642 | 0.88193 | 0.97195 | 0.83079 | 0.70407 | 0.59966 | 0.51608 | 0.45328 | 0.40251 | 0.36035 | 0.97195 | 23 | Slope | 0.26667 | 0.54779 | 0.53104 | 0.50356 | 0.47242 | 0.43621 | 0.39822 | 0.35933 | 0.32301 | 0.29211 | 0.26795 | 0.24947 | 0.23606 | 0.2282 | 0.21382 | 0.20512 | 0.20357 | 0.2116 | 0.22746 | 0.25244 | 0.28438 | 0.31975 | 0.35658 | 0.39398 | 0.41287 | 0.35471 | 0.30136 | 0.25544 | 0.21647 | 0.18443 | 0.15639 | 0.13123 | 0.54779 | 0 | 0.64336 | Slope | 1 | 0.089143 |  | 0.55874 | 0 | 0.64336 | Slope | 2 | 1 | 0 | 20 | -20 | 5.4824e-06 | 0.00028664 | 0.0026876
303 | 0:50 | -8.9143 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -8.9253 | -0.089253 | -0.089253 | -8.9143 | 5.4824e-06 | [13 empty] | 0.96133 | 1 | 0.96552 | 0.90713 | 0.85252 | 0.81045 | 0.77921 | 0.75752 | 0.7405 | 0.72104 | 0.69066 | 0.64453 | 0.58826 | 0.52085 | 0.4446 | 0.3486 | 0.23483 | 0.10201 | -0.037756 | -0.17368 | -0.29831 | -0.40467 | -0.49234 | -0.56055 | -0.59997 | -0.60275 | -0.5865 | -0.55993 | -0.53045 | -0.50071 | -0.4787 | -0.0044626 | 0.0045618 | 0.00022809 | 0.00022809 | 0 | 0 | 0.0028602 | 0.05 | 0.40708 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.59315 | 0.54405 | 0.48396 | 0.40866 | 0.32802 | 0.24467 | 0.16906 | 0.10968 | 0.070536 | 0.048433 | 0.041539 | 0.051292 | 0.041475 | 0.048726 | 0.077397 | 0.13484 | 0.21575 | 0.324 | 0.45317 | 0.5926 | 0.73644 | 0.88195 | 0.97193 | 0.83077 | 0.70404 | 0.59963 | 0.51606 | 0.45326 | 0.40249 | 0.36033 | 0.31819 | 0.97193 | 22 | Slope | 0.3 | 0.53105 | 0.51468 | 0.48354 | 0.44733 | 0.40934 | 0.37045 | 0.33413 | 0.30323 | 0.27907 | 0.26059 | 0.24718 | 0.23932 | 0.22494 | 0.21624 | 0.21469 | 0.22272 | 0.23858 | 0.26356 | 0.2955 | 0.33087 | 0.3677 | 0.4051 | 0.42398 | 0.36581 | 0.31246 | 0.26654 | 0.22758 | 0.19553 | 0.1675 | 0.14233 | 0.11717 | 0.53105 | 0 | 0.59315 | Slope | 1 | 0.089253 |  | 0.5582 | 0 | 0.59315 | Slope | 2 | 1 | 0 | 20 | -20 | 5.4824e-06 | 0.00030522 | 0.0028602
304 | 0:50 | -8.9253 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -8.9362 | -0.089362 | -0.089362 | -8.9253 | 5.4824e-06 | [13 empty] | 0.96552 | 1 | 0.97003 | 0.92123 | 0.87519 | 0.83718 | 0.80391 | 0.77512 | 0.75094 | 0.72501 | 0.68703 | 0.63653 | 0.57273 | 0.50011 | 0.40564 | 0.28844 | 0.15077 | 0.0049895 | -0.13739 | -0.27701 | -0.40621 | -0.51842 | -0.60576 | -0.658 | -0.66992 | -0.65175 | -0.62055 | -0.58792 | -0.55508 | -0.52575 | -0.56785 | -0.0044681 | 0.0051626 | 0.00025813 | 0.00025813 | 0 | 0 | 0.0030947 | 0.05 | 0.45618 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.54408 | 0.48399 | 0.40869 | 0.32805 | 0.2447 | 0.16909 | 0.10971 | 0.070566 | 0.048463 | 0.041569 | 0.051322 | 0.041505 | 0.048756 | 0.077427 | 0.13487 | 0.21578 | 0.32403 | 0.4532 | 0.59263 | 0.73647 | 0.88198 | 0.9719 | 0.83074 | 0.70401 | 0.5996 | 0.51603 | 0.45323 | 0.40246 | 0.3603 | 0.31816 | 0.20343 | 0.9719 | 21 | Slope | 0.33333 | 0.51469 | 0.49466 | 0.45845 | 0.42046 | 0.38157 | 0.34525 | 0.31435 | 0.29019 | 0.27171 | 0.2583 | 0.25044 | 0.23606 | 0.22736 | 0.22581 | 0.23385 | 0.2497 | 0.27468 | 0.30662 | 0.34199 | 0.37882 | 0.41622 | 0.43508 | 0.37691 | 0.32356 | 0.27765 | 0.23868 | 0.20663 | 0.1786 | 0.15343 | 0.12827 | 0.078922 | 0.51469 | 0 | 0.54408 | Slope | 1 | 0.089362 |  | 0.55766 | 0 | 0.54408 | Slope | 2 | 1 | 0 | 20 | -20 | 5.4824e-06 | 0.00032414 | 0.0030947
305 | 0:51 | -8.9362 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -8.9472 | -0.089472 | -0.089472 | -8.9362 | 5.4824e-06 | [13 empty] | 0.97003 | 1 | 0.97542 | 0.93487 | 0.89339 | 0.85343 | 0.81307 | 0.77718 | 0.74601 | 0.71112 | 0.66785 | 0.60896 | 0.53996 | 0.44795 | 0.33123 | 0.18954 | 0.040128 | -0.10535 | -0.24878 | -0.39028 | -0.52276 | -0.63218 | -0.70058 | -0.72199 | -0.71053 | -0.67677 | -0.63989 | -0.60429 | -0.57245 | -0.61649 | -0.63384 | -0.0044736 | 0.0059157 | 0.00029579 | 0.00029579 | 0 | 0 | 0.0034204 | 0.05 | 0.51626 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.48403 | 0.40873 | 0.32809 | 0.24474 | 0.16913 | 0.10975 | 0.070604 | 0.048501 | 0.041606 | 0.051359 | 0.041543 | 0.048794 | 0.077465 | 0.13491 | 0.21582 | 0.32407 | 0.45324 | 0.59266 | 0.73651 | 0.88202 | 0.97186 | 0.8307 | 0.70398 | 0.59956 | 0.51599 | 0.45319 | 0.40242 | 0.36026 | 0.31812 | 0.2034 | 0.10821 | 0.97186 | 20 | Slope | 0.36667 | 0.49468 | 0.46958 | 0.43159 | 0.39269 | 0.35638 | 0.32547 | 0.30131 | 0.28283 | 0.26942 | 0.26156 | 0.24718 | 0.23849 | 0.23693 | 0.24497 | 0.26083 | 0.2858 | 0.31775 | 0.35311 | 0.38995 | 0.42734 | 0.44618 | 0.38801 | 0.33466 | 0.28874 | 0.24977 | 0.21773 | 0.1897 | 0.16453 | 0.13937 | 0.090021 | 0.047182 | 0.49468 | 0 | 0.48403 | Slope | 1 | 0.089472 |  | 0.55711 | 0 | 0.48403 | Slope | 2 | 1 | 0 | 20 | -20 | 5.4824e-06 | 0.00034204 | 0.0034204
306 | 0:51 | -8.9472 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -8.9582 | -0.089582 | -0.089582 | -8.9472 | 5.4824e-06 | [13 empty] | 0.97542 | 1 | 0.97958 | 0.94363 | 0.9019 | 0.8567 | 0.81106 | 0.76963 | 0.73015 | 0.69006 | 0.63776 | 0.57317 | 0.48461 | 0.37014 | 0.22869 | 0.075262 | -0.073834 | -0.22047 | -0.3659 | -0.51041 | -0.63931 | -0.72794 | -0.76281 | -0.75869 | -0.73006 | -0.69064 | -0.65116 | -0.61695 | -0.65461 | -0.67494 | -0.67332 | -0.0044791 | 0.0067221 | 0.0003361 | 0.0003361 | 0 | 0 | 0.0037709 | 0.05 | 0.59157 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.40877 | 0.32813 | 0.24478 | 0.16917 | 0.10979 | 0.070644 | 0.048541 | 0.041647 | 0.0514 | 0.041583 | 0.048834 | 0.077505 | 0.13495 | 0.21586 | 0.32411 | 0.45328 | 0.5927 | 0.73655 | 0.88206 | 0.97182 | 0.83066 | 0.70393 | 0.59952 | 0.51595 | 0.45315 | 0.40238 | 0.36022 | 0.31808 | 0.20336 | 0.10817 | 0.044494 | 0.97182 | 19 | Slope | 0.4 | 0.46959 | 0.44271 | 0.40382 | 0.3675 | 0.3366 | 0.31244 | 0.29396 | 0.28055 | 0.27269 | 0.25831 | 0.24961 | 0.24806 | 0.25609 | 0.27195 | 0.29693 | 0.32887 | 0.36423 | 0.40107 | 0.43846 | 0.45727 | 0.39911 | 0.34576 | 0.29984 | 0.26087 | 0.22883 | 0.20079 | 0.17563 | 0.15047 | 0.10112 | 0.058279 | 0.025942 | 0.46959 | 0 | 0.40877 | Slope | 1 | 0.089582 |  | 0.55657 | 0 | 0.40877 | Slope | 2 | 1 | 0 | 20 | -20 | 5.4824e-06 | 0.00035754 | 0.0037709
307 | 0:51 | -8.9582 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -8.9691 | -0.089691 | -0.089691 | -8.9582 | 5.4824e-06 | [13 empty] | 0.97958 | 1 | 0.9818 | 0.94618 | 0.90073 | 0.85149 | 0.8017 | 0.75326 | 0.70949 | 0.66022 | 0.60152 | 0.51732 | 0.40619 | 0.26671 | 0.11298 | -0.04064 | -0.1915 | -0.34079 | -0.48985 | -0.631 | -0.73824 | -0.79105 | -0.79819 | -0.77535 | -0.74018 | -0.69827 | -0.6606 | -0.68987 | -0.70676 | -0.70878 | -0.69617 | -0.0044846 | 0.0075556 | 0.00037778 | 0.00037778 | 0 | 0 | 0.0041294 | 0.05 | 0.67221 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.32817 | 0.24482 | 0.16921 | 0.10983 | 0.070686 | 0.048583 | 0.041688 | 0.051441 | 0.041625 | 0.048876 | 0.077547 | 0.13499 | 0.2159 | 0.32415 | 0.45332 | 0.59275 | 0.73659 | 0.8821 | 0.97178 | 0.83062 | 0.70389 | 0.59948 | 0.51591 | 0.45311 | 0.40234 | 0.36018 | 0.31804 | 0.20331 | 0.10813 | 0.044452 | 0.017377 | 0.97178 | 18 | Slope | 0.43333 | 0.44272 | 0.41494 | 0.37863 | 0.34772 | 0.32356 | 0.30508 | 0.29167 | 0.28381 | 0.26943 | 0.26074 | 0.25918 | 0.26722 | 0.28308 | 0.30805 | 0.34 | 0.37536 | 0.4122 | 0.44959 | 0.46837 | 0.41021 | 0.35685 | 0.31094 | 0.27197 | 0.23992 | 0.21189 | 0.18673 | 0.16157 | 0.11222 | 0.069377 | 0.03704 | 0.016903 | 0.46837 | 18 | 0.97178 | Slope | 0.43333 | 0.089691 |  | 0.55603 | 0 | 0.97178 | Slope | 2 | 0.43333 | 0 | 20 | -20 | 5.4824e-06 | 0.00036971 | 0.0041294
308 | 0:51 | -8.9691 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -8.9801 | -0.089801 | -0.089801 | -8.9691 | 5.4824e-06 | [13 empty] | 0.9818 | 1 | 0.98225 | 0.94466 | 0.89661 | 0.84437 | 0.78912 | 0.73785 | 0.68575 | 0.62976 | 0.5522 | 0.44601 | 0.31002 | 0.15697 | 0.0006742 | -0.15689 | -0.31257 | -0.46764 | -0.61541 | -0.73611 | -0.8069 | -0.83024 | -0.81701 | -0.78672 | -0.74831 | -0.70825 | -0.72058 | -0.73446 | -0.736 | -0.72827 | -0.71211 | -0.00449 | 0.0083116 | 0.00041558 | 0.00041558 | 0 | 0 | 0.0044345 | 0.05 | 0.75556 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.24486 | 0.16925 | 0.10987 | 0.070723 | 0.048621 | 0.041726 | 0.051479 | 0.041663 | 0.048913 | 0.077584 | 0.13503 | 0.21594 | 0.32419 | 0.45336 | 0.59278 | 0.73663 | 0.88214 | 0.97174 | 0.83058 | 0.70386 | 0.59945 | 0.51587 | 0.45307 | 0.4023 | 0.36014 | 0.318 | 0.20328 | 0.10809 | 0.044414 | 0.017339 | 0.017273 | 0.97174 | 17 | Slope | 0.46667 | 0.41495 | 0.38975 | 0.35885 | 0.33469 | 0.31621 | 0.3028 | 0.29494 | 0.28055 | 0.27186 | 0.27031 | 0.27834 | 0.2942 | 0.31917 | 0.35112 | 0.38648 | 0.42332 | 0.46071 | 0.47947 | 0.42131 | 0.36795 | 0.32204 | 0.28307 | 0.25102 | 0.22299 | 0.19782 | 0.17267 | 0.12331 | 0.080475 | 0.048138 | 0.028002 | 0.016869 | 0.47947 | 17 | 0.97174 | Slope | 0.46667 | 0.089801 |  | 0.55549 | 0 | 0.97174 | Slope | 2 | 0.46667 | 0 | 20 | -20 | 5.4824e-06 | 0.00037773 | 0.0044345
309 | 0:51 | -8.9801 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -8.9911 | -0.089911 | -0.089911 | -8.9801 | 5.4824e-06 | [13 empty] | 0.98225 | 1 | 0.98184 | 0.94298 | 0.89305 | 0.83674 | 0.77995 | 0.72163 | 0.66302 | 0.58989 | 0.49167 | 0.36141 | 0.2106 | 0.052127 | -0.11092 | -0.27606 | -0.44024 | -0.59668 | -0.72622 | -0.8112 | -0.85175 | -0.85325 | -0.83162 | -0.79744 | -0.76045 | -0.75225 | -0.75648 | -0.75845 | -0.75229 | -0.74198 | -0.72425 | -0.0044955 | 0.0089055 | 0.00044527 | 0.00044527 | 0 | 0 | 0.0046523 | 0.05 | 0.83116 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.16928 | 0.1099 | 0.070753 | 0.04865 | 0.041756 | 0.051509 | 0.041692 | 0.048943 | 0.077614 | 0.13506 | 0.21597 | 0.32422 | 0.45339 | 0.59281 | 0.73666 | 0.88217 | 0.97171 | 0.83055 | 0.70383 | 0.59942 | 0.51584 | 0.45304 | 0.40227 | 0.36011 | 0.31797 | 0.20325 | 0.10806 | 0.044385 | 0.017309 | 0.017243 | 0.046154 | 0.97171 | 16 | Slope | 0.5 | 0.38976 | 0.36997 | 0.34581 | 0.32733 | 0.31392 | 0.30606 | 0.29168 | 0.28298 | 0.28143 | 0.28946 | 0.30532 | 0.3303 | 0.36224 | 0.3976 | 0.43444 | 0.47183 | 0.49057 | 0.43241 | 0.37905 | 0.33314 | 0.29417 | 0.26212 | 0.23409 | 0.20893 | 0.18377 | 0.13442 | 0.091576 | 0.059239 | 0.039103 | 0.02797 | 0.026496 | 0.49057 | 16 | 0.97171 | Slope | 0.5 | 0.089911 |  | 0.55494 | 0 | 0.97171 | Slope | 2 | 0.5 | 0 | 20 | -20 | 5.4824e-06 | 0.00038127 | 0.0046523
310 | 0:51 | -8.9911 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -9.002 | -0.09002 | -0.09002 | -8.9911 | 5.4824e-06 | [13 empty] | 0.98184 | 1 | 0.98171 | 0.942 | 0.88939 | 0.83267 | 0.77 | 0.70555 | 0.632 | 0.5402 | 0.4193 | 0.27354 | 0.11493 | -0.052792 | -0.22601 | -0.40231 | -0.57049 | -0.71088 | -0.80587 | -0.86062 | -0.87842 | -0.87071 | -0.84461 | -0.81166 | -0.78707 | -0.77796 | -0.7741 | -0.77021 | -0.76263 | -0.75222 | -0.73375 | -0.004501 | 0.0092969 | 0.00046485 | 0.00046485 | 0 | 0 | 0.0047814 | 0.05 | 0.89055 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.10992 | 0.070773 | 0.04867 | 0.041775 | 0.051528 | 0.041712 | 0.048963 | 0.077634 | 0.13508 | 0.21599 | 0.32424 | 0.45341 | 0.59283 | 0.73668 | 0.88219 | 0.97169 | 0.83053 | 0.70381 | 0.5994 | 0.51582 | 0.45302 | 0.40225 | 0.36009 | 0.31795 | 0.20323 | 0.10804 | 0.044365 | 0.01729 | 0.017223 | 0.046134 | 0.094367 | 0.97169 | 15 | Slope | 0.53333 | 0.36997 | 0.35692 | 0.33845 | 0.32504 | 0.31718 | 0.30279 | 0.2941 | 0.29254 | 0.30058 | 0.31644 | 0.34141 | 0.37336 | 0.40872 | 0.44556 | 0.48295 | 0.50167 | 0.44351 | 0.39016 | 0.34424 | 0.30527 | 0.27323 | 0.24519 | 0.22003 | 0.19487 | 0.14552 | 0.10268 | 0.070344 | 0.050208 | 0.039074 | 0.0376 | 0.042567 | 0.50167 | 15 | 0.97169 | Slope | 0.53333 | 0.09002 |  | 0.5544 | 0 | 0.97169 | Slope | 2 | 0.53333 | 0 | 20 | -20 | 5.4824e-06 | 0.00038044 | 0.0047814
311 | 0:52 | -9.002 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -9.013 | -0.09013 | -0.09013 | -9.002 | 5.4824e-06 | [13 empty] | 0.98171 | 1 | 0.98151 | 0.94021 | 0.88821 | 0.82643 | 0.75787 | 0.6802 | 0.58964 | 0.47647 | 0.33993 | 0.18507 | 0.015673 | -0.16401 | -0.35034 | -0.53283 | -0.68679 | -0.79345 | -0.85824 | -0.88961 | -0.89759 | -0.88489 | -0.85992 | -0.82408 | -0.80379 | -0.78955 | -0.7812 | -0.77654 | -0.76985 | -0.75986 | -0.73926 | -0.0045065 | 0.0095179 | 0.0004759 | 0.0004759 | 0 | 0 | 0.004849 | 0.05 | 0.92969 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.070784 | 0.048681 | 0.041787 | 0.051539 | 0.041723 | 0.048974 | 0.077645 | 0.13509 | 0.216 | 0.32425 | 0.45342 | 0.59284 | 0.73669 | 0.8822 | 0.97168 | 0.83052 | 0.7038 | 0.59938 | 0.51581 | 0.45301 | 0.40224 | 0.36008 | 0.31794 | 0.20322 | 0.10803 | 0.044354 | 0.017279 | 0.017212 | 0.046123 | 0.094355 | 0.15292 | 0.97168 | 14 | Slope | 0.56667 | 0.35693 | 0.34956 | 0.33615 | 0.32829 | 0.31391 | 0.30521 | 0.30366 | 0.3117 | 0.32755 | 0.35253 | 0.38447 | 0.41984 | 0.45668 | 0.49407 | 0.51278 | 0.45462 | 0.40127 | 0.35535 | 0.31638 | 0.28434 | 0.2563 | 0.23114 | 0.20598 | 0.15663 | 0.11379 | 0.081451 | 0.061315 | 0.050182 | 0.048708 | 0.053674 | 0.062085 | 0.51278 | 14 | 0.97168 | Slope | 0.56667 | 0.09013 |  | 0.55386 | 0 | 0.97168 | Slope | 2 | 0.56667 | 0 | 20 | -20 | 5.4824e-06 | 0.00037543 | 0.004849
312 | 0:52 | -9.013 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -9.0239 | -0.090239 | -0.090239 | -9.013 | 5.4824e-06 | [13 empty] | 0.98151 | 1 | 0.98087 | 0.94131 | 0.88494 | 0.81745 | 0.73708 | 0.6437 | 0.53288 | 0.40415 | 0.25783 | 0.09124 | -0.091409 | -0.2858 | -0.48032 | -0.65055 | -0.77167 | -0.84812 | -0.88907 | -0.91026 | -0.91288 | -0.90125 | -0.86048 | -0.83286 | -0.80961 | -0.79197 | -0.7833 | -0.78011 | -0.77467 | -0.76375 | -0.73554 | -0.004512 | 0.0095869 | 0.00047934 | 0.00047934 | 0 | 0 | 0.0048689 | 0.05 | 0.95179 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.048684 | 0.04179 | 0.051543 | 0.041726 | 0.048977 | 0.077648 | 0.13509 | 0.216 | 0.32425 | 0.45342 | 0.59285 | 0.7367 | 0.8822 | 0.97168 | 0.83052 | 0.70379 | 0.59938 | 0.51581 | 0.45301 | 0.40224 | 0.36008 | 0.31793 | 0.20321 | 0.10803 | 0.044351 | 0.017275 | 0.017209 | 0.046119 | 0.094352 | 0.15292 | 0.22563 | 0.97168 | 13 | Slope | 0.6 | 0.34956 | 0.34726 | 0.3394 | 0.32502 | 0.31633 | 0.31477 | 0.32281 | 0.33867 | 0.36364 | 0.39559 | 0.43095 | 0.46779 | 0.50518 | 0.52389 | 0.46573 | 0.41238 | 0.36646 | 0.32749 | 0.29545 | 0.26741 | 0.24225 | 0.21709 | 0.16774 | 0.1249 | 0.092561 | 0.072425 | 0.061292 | 0.059818 | 0.064784 | 0.073195 | 0.086321 | 0.52389 | 13 | 0.97168 | Slope | 0.6 | 0.090239 |  | 0.55331 | 0 | 0.97168 | Slope | 2 | 0.6 | 0 | 20 | -20 | 5.4824e-06 | 0.00036651 | 0.0048689
313 | 0:52 | -9.0239 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -3.708 | -0.03708 | -0.03708 | -9.0239 | 0.002658 | [13 empty] | 0.98087 | 1 | 0.98439 | 0.94136 | 0.87958 | 0.8019 | 0.70732 | 0.59491 | 0.46874 | 0.3297 | 0.17108 | -0.0097518 | -0.20852 | -0.41315 | -0.59775 | -0.73656 | -0.82772 | -0.88 | -0.9107 | -0.92646 | -0.93036 | -0.88985 | -0.86064 | -0.83196 | -0.80627 | -0.78876 | -0.782 | -0.78086 | -0.7756 | -0.76 | -0.7227 | -0.001854 | 0.0094894 | 0.00047447 | 0.00047447 | 0 | 0 | 0.0048425 | 0.05 | 0.95869 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.041785 | 0.051538 | 0.041722 | 0.048972 | 0.077643 | 0.13509 | 0.21599 | 0.32425 | 0.45342 | 0.59284 | 0.73669 | 0.8822 | 0.97168 | 0.83052 | 0.7038 | 0.59939 | 0.51581 | 0.45301 | 0.40224 | 0.36008 | 0.31794 | 0.20322 | 0.10803 | 0.044355 | 0.01728 | 0.017214 | 0.046124 | 0.094357 | 0.15292 | 0.22563 | 0.31343 | 0.97168 | 12 | Slope | 0.63333 | 0.34726 | 0.35051 | 0.33613 | 0.32744 | 0.32588 | 0.33392 | 0.34978 | 0.37475 | 0.40669 | 0.44206 | 0.4789 | 0.51629 | 0.535 | 0.47684 | 0.42349 | 0.37757 | 0.3386 | 0.30656 | 0.27852 | 0.25336 | 0.2282 | 0.17885 | 0.13601 | 0.10367 | 0.083538 | 0.072405 | 0.07093 | 0.075897 | 0.084307 | 0.097434 | 0.11559 | 0.535 | 12 | 0.97168 | Slope | 0.63333 | 0.03708 |  | 0.81645 | 0 | 0.97168 | Slope | 2 | 0.63333 | 0 | 20 | -20 | 0.002658 | 0.00035416 | 0.0048425
314 | 0:52 | -3.708 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.2312 | -0.042312 | -0.042312 | -3.708 | 0.00026158 | [13 empty] | 0.98439 | 1 | 0.984 | 0.941 | 0.87503 | 0.78738 | 0.67923 | 0.55766 | 0.42725 | 0.2807 | 0.11211 | -0.080867 | -0.28903 | -0.48864 | -0.65087 | -0.76746 | -0.84157 | -0.88721 | -0.91486 | -0.93127 | -0.89685 | -0.87334 | -0.85137 | -0.8297 | -0.81083 | -0.80197 | -0.80171 | -0.80343 | -0.79621 | -0.77604 | -0.73422 | -0.0021156 | 0.0095875 | 0.00047938 | 0.00047938 | 0 | 0 | 0.0048604 | 0.05 | 0.94894 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.051543 | 0.041726 | 0.048977 | 0.077648 | 0.13509 | 0.216 | 0.32425 | 0.45342 | 0.59285 | 0.7367 | 0.8822 | 0.97168 | 0.83052 | 0.70379 | 0.59938 | 0.51581 | 0.45301 | 0.40224 | 0.36008 | 0.31793 | 0.20321 | 0.10803 | 0.044351 | 0.017275 | 0.017209 | 0.046119 | 0.094352 | 0.15292 | 0.22563 | 0.31343 | 0.4082 | 0.97168 | 11 | Slope | 0.66667 | 0.35051 | 0.34724 | 0.33855 | 0.33699 | 0.34503 | 0.36089 | 0.38586 | 0.41781 | 0.45317 | 0.49001 | 0.5274 | 0.54611 | 0.48795 | 0.4346 | 0.38868 | 0.34971 | 0.31767 | 0.28963 | 0.26447 | 0.23931 | 0.18996 | 0.14712 | 0.11478 | 0.094647 | 0.083514 | 0.08204 | 0.087006 | 0.095417 | 0.10854 | 0.1267 | 0.14718 | 0.54611 | 11 | 0.97168 | Slope | 0.66667 | 0.042312 |  | 0.79056 | 0 | 0.97168 | Slope | 2 | 0.66667 | 0 | 20 | -20 | 0.00026158 | 0.00033899 | 0.0048604
315 | 0:52 | -4.2312 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -5.9461 | -0.059461 | -0.059461 | -4.2312 | 0.00085747 | [13 empty] | 0.984 | 1 | 0.98435 | 0.93899 | 0.86491 | 0.76516 | 0.64833 | 0.52245 | 0.38456 | 0.22815 | 0.047446 | -0.15604 | -0.36193 | -0.54175 | -0.68242 | -0.78127 | -0.84816 | -0.89047 | -0.91913 | -0.88847 | -0.87226 | -0.85622 | -0.84101 | -0.8262 | -0.81635 | -0.81451 | -0.81801 | -0.82049 | -0.81159 | -0.78942 | -0.73872 | -0.0029731 | 0.009515 | 0.00047575 | 0.00047575 | 0 | 0 | 0.004848 | 0.05 | 0.95875 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.041723 | 0.048974 | 0.077645 | 0.13509 | 0.216 | 0.32425 | 0.45342 | 0.59284 | 0.73669 | 0.8822 | 0.97168 | 0.83052 | 0.7038 | 0.59938 | 0.51581 | 0.45301 | 0.40224 | 0.36008 | 0.31794 | 0.20322 | 0.10803 | 0.044354 | 0.017279 | 0.017212 | 0.046123 | 0.094356 | 0.15292 | 0.22563 | 0.31343 | 0.40821 | 0.50931 | 0.97168 | 10 | Slope | 0.7 | 0.34724 | 0.34966 | 0.3481 | 0.35614 | 0.372 | 0.39697 | 0.42892 | 0.46428 | 0.50112 | 0.53851 | 0.55723 | 0.49906 | 0.44571 | 0.39979 | 0.36083 | 0.32878 | 0.30075 | 0.27558 | 0.25042 | 0.20107 | 0.15823 | 0.1259 | 0.10576 | 0.094626 | 0.093152 | 0.098119 | 0.10653 | 0.11966 | 0.13781 | 0.15829 | 0.18088 | 0.55723 | 10 | 0.97168 | Slope | 0.7 | 0.059461 |  | 0.70567 | 0 | 0.97168 | Slope | 2 | 0.7 | 0 | 20 | -20 | 0.00085747 | 0.00032069 | 0.004848
316 | 0:52 | -5.9461 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.0682 | -0.070682 | -0.070682 | -5.9461 | 0.00056103 | [13 empty] | 0.98435 | 1 | 0.98267 | 0.9304 | 0.84451 | 0.73519 | 0.61271 | 0.4783 | 0.32974 | 0.16049 | -0.03173 | -0.23469 | -0.42187 | -0.57956 | -0.70044 | -0.79077 | -0.85351 | -0.89745 | -0.87372 | -0.86101 | -0.85013 | -0.83807 | -0.82786 | -0.82048 | -0.81684 | -0.81879 | -0.82473 | -0.82756 | -0.81793 | -0.78941 | -0.74094 | -0.0035341 | 0.0092283 | 0.00046142 | 0.00046142 | 0 | 0 | 0.0047953 | 0.05 | 0.9515 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.048959 | 0.07763 | 0.13507 | 0.21598 | 0.32423 | 0.4534 | 0.59283 | 0.73668 | 0.88219 | 0.97169 | 0.83054 | 0.70381 | 0.5994 | 0.51583 | 0.45302 | 0.40225 | 0.36009 | 0.31795 | 0.20323 | 0.10805 | 0.044369 | 0.017293 | 0.017227 | 0.046137 | 0.09437 | 0.15293 | 0.22565 | 0.31345 | 0.40822 | 0.50932 | 0.59556 | 0.97169 | 9 | Slope | 0.73333 | 0.34965 | 0.35921 | 0.36725 | 0.38311 | 0.40808 | 0.44002 | 0.47539 | 0.51223 | 0.54962 | 0.56834 | 0.51018 | 0.45683 | 0.41091 | 0.37194 | 0.3399 | 0.31186 | 0.2867 | 0.26154 | 0.21219 | 0.16935 | 0.13701 | 0.11688 | 0.10574 | 0.10427 | 0.10923 | 0.11764 | 0.13077 | 0.14893 | 0.16941 | 0.192 | 0.20963 | 0.56834 | 9 | 0.97169 | Slope | 0.73333 | 0.070682 |  | 0.65012 | 0 | 0.97169 | Slope | 2 | 0.73333 | 0 | 20 | -20 | 0.00056103 | 0.00029978 | 0.0047953
317 | 0:53 | -7.0682 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.1963 | -0.071963 | -0.071963 | -7.0682 | 6.4052e-05 | [13 empty] | 0.98267 | 1 | 0.97992 | 0.91926 | 0.82495 | 0.70949 | 0.578 | 0.43243 | 0.27076 | 0.08953 | -0.10357 | -0.28966 | -0.45556 | -0.59309 | -0.70535 | -0.79168 | -0.85722 | -0.83608 | -0.83213 | -0.82489 | -0.81696 | -0.80919 | -0.80614 | -0.8054 | -0.80651 | -0.81442 | -0.82466 | -0.82968 | -0.81778 | -0.79039 | -0.7308 | -0.0035982 | 0.0086539 | 0.00043269 | 0.00043269 | 0 | 0 | 0.0047006 | 0.05 | 0.92283 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.077602 | 0.13504 | 0.21595 | 0.32421 | 0.45338 | 0.5928 | 0.73665 | 0.88216 | 0.97172 | 0.83057 | 0.70384 | 0.59943 | 0.51585 | 0.45305 | 0.40228 | 0.36012 | 0.31798 | 0.20326 | 0.10808 | 0.044397 | 0.017322 | 0.017255 | 0.046166 | 0.094399 | 0.15296 | 0.22568 | 0.31347 | 0.40825 | 0.50935 | 0.59559 | 0.69338 | 0.97172 | 8 | Slope | 0.76667 | 0.3592 | 0.37835 | 0.39421 | 0.41918 | 0.45113 | 0.48649 | 0.52333 | 0.56072 | 0.57946 | 0.5213 | 0.46795 | 0.42203 | 0.38306 | 0.35102 | 0.32298 | 0.29782 | 0.27266 | 0.22331 | 0.18047 | 0.14813 | 0.128 | 0.11686 | 0.11539 | 0.12036 | 0.12877 | 0.14189 | 0.16005 | 0.18053 | 0.20312 | 0.22075 | 0.24224 | 0.57946 | 8 | 0.97172 | Slope | 0.76667 | 0.071963 |  | 0.64378 | 0 | 0.97172 | Slope | 2 | 0.76667 | 0 | 20 | -20 | 6.4052e-05 | 0.00027718 | 0.0047006
318 | 0:53 | -7.1963 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.9987 | -0.079987 | -0.079987 | -7.1963 | 0.00040121 | [13 empty] | 0.97992 | 1 | 0.97699 | 0.91135 | 0.81254 | 0.68932 | 0.54761 | 0.38987 | 0.21676 | 0.033725 | -0.14462 | -0.31094 | -0.45723 | -0.58637 | -0.69497 | -0.78496 | -0.77297 | -0.7741 | -0.77672 | -0.77281 | -0.76944 | -0.76937 | -0.77406 | -0.77967 | -0.79061 | -0.80713 | -0.82263 | -0.8304 | -0.81818 | -0.78828 | -0.71984 | -0.0039994 | 0.0078448 | 0.00039224 | 0.00039224 | 0 | 0 | 0.0045971 | 0.05 | 0.86539 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.135 | 0.21591 | 0.32417 | 0.45334 | 0.59276 | 0.73661 | 0.88212 | 0.97176 | 0.83061 | 0.70388 | 0.59947 | 0.51589 | 0.45309 | 0.40232 | 0.36016 | 0.31802 | 0.2033 | 0.10812 | 0.044438 | 0.017362 | 0.017296 | 0.046207 | 0.094439 | 0.153 | 0.22572 | 0.31351 | 0.40829 | 0.50939 | 0.59563 | 0.69343 | 0.79715 | 0.97176 | 7 | Slope | 0.8 | 0.37833 | 0.4053 | 0.43028 | 0.46222 | 0.49759 | 0.53442 | 0.57182 | 0.59059 | 0.53242 | 0.47907 | 0.43316 | 0.39419 | 0.36214 | 0.33411 | 0.30894 | 0.28378 | 0.23443 | 0.19159 | 0.15926 | 0.13912 | 0.12799 | 0.12651 | 0.13148 | 0.13989 | 0.15302 | 0.17117 | 0.19165 | 0.21424 | 0.23188 | 0.25336 | 0.27683 | 0.59059 | 7 | 0.97176 | Slope | 0.8 | 0.079987 |  | 0.60406 | 0 | 0.97176 | Slope | 2 | 0.8 | 0 | 20 | -20 | 0.00040121 | 0.00025432 | 0.0045971
319 | 0:53 | -7.9987 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -9.3591 | -0.093591 | -0.093591 | -7.9987 | 0.0006802 | [13 empty] | 0.97699 | 1 | 0.97574 | 0.90761 | 0.80285 | 0.67078 | 0.518 | 0.34945 | 0.17432 | 0.0053003 | -0.15347 | -0.29954 | -0.43699 | -0.56231 | -0.67546 | -0.67724 | -0.68869 | -0.6963 | -0.70098 | -0.70073 | -0.70439 | -0.71225 | -0.7247 | -0.74444 | -0.76833 | -0.79285 | -0.81575 | -0.82165 | -0.8153 | -0.78402 | -0.70396 | -0.0046796 | 0.0067623 | 0.00033811 | 0.00033811 | 0 | 0 | 0.0044916 | 0.05 | 0.78448 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.21586 | 0.32411 | 0.45328 | 0.59271 | 0.73655 | 0.88206 | 0.97182 | 0.83066 | 0.70393 | 0.59952 | 0.51595 | 0.45315 | 0.40238 | 0.36022 | 0.31808 | 0.20335 | 0.10817 | 0.044492 | 0.017416 | 0.01735 | 0.046261 | 0.094493 | 0.15306 | 0.22577 | 0.31357 | 0.40835 | 0.50945 | 0.59568 | 0.69348 | 0.7972 | 0.88681 | 0.97182 | 6 | Slope | 0.83333 | 0.40529 | 0.44137 | 0.47332 | 0.50868 | 0.54552 | 0.58291 | 0.60172 | 0.54355 | 0.4902 | 0.44429 | 0.40532 | 0.37327 | 0.34524 | 0.32007 | 0.29491 | 0.24556 | 0.20272 | 0.17039 | 0.15025 | 0.13912 | 0.13764 | 0.14261 | 0.15102 | 0.16415 | 0.1823 | 0.20278 | 0.22537 | 0.24301 | 0.26449 | 0.28796 | 0.30671 | 0.60172 | 6 | 0.97182 | Slope | 0.83333 | 0.093591 |  | 0.53672 | 0 | 0.97182 | Slope | 2 | 0.83333 | 0 | 20 | -20 | 0.0006802 | 0.00023258 | 0.0044916
320 | 0:53 | -9.3591 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -10.5496 | -0.1055 | -0.1055 | -9.3591 | 0.00059523 | [13 empty] | 0.97574 | 1 | 0.97483 | 0.90247 | 0.78989 | 0.6471 | 0.48319 | 0.31177 | 0.15024 | 0.0012322 | -0.13595 | -0.27243 | -0.40573 | -0.53677 | -0.56111 | -0.58415 | -0.59905 | -0.60483 | -0.61034 | -0.61411 | -0.62414 | -0.63972 | -0.66881 | -0.7042 | -0.73751 | -0.77234 | -0.79242 | -0.81016 | -0.80714 | -0.76971 | -0.68827 | -0.0052748 | 0.0054706 | 0.00027353 | 0.00027353 | 0 | 0 | 0.0043664 | 0.05 | 0.67623 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.32405 | 0.45322 | 0.59264 | 0.73649 | 0.882 | 0.97188 | 0.83072 | 0.704 | 0.59959 | 0.51601 | 0.45321 | 0.40244 | 0.36028 | 0.31814 | 0.20342 | 0.10823 | 0.044556 | 0.017481 | 0.017415 | 0.046325 | 0.094558 | 0.15312 | 0.22584 | 0.31363 | 0.40841 | 0.50951 | 0.59575 | 0.69354 | 0.79726 | 0.88687 | 0.95903 | 0.97188 | 5 | Slope | 0.86667 | 0.44135 | 0.48441 | 0.51977 | 0.55661 | 0.594 | 0.61285 | 0.55469 | 0.50133 | 0.45542 | 0.41645 | 0.3844 | 0.35637 | 0.3312 | 0.30605 | 0.2567 | 0.21386 | 0.18152 | 0.16138 | 0.15025 | 0.14878 | 0.15374 | 0.16215 | 0.17528 | 0.19343 | 0.21391 | 0.2365 | 0.25414 | 0.27563 | 0.29909 | 0.31785 | 0.33079 | 0.61285 | 5 | 0.97188 | Slope | 0.86667 | 0.1055 |  | 0.47779 | 0 | 0.97188 | Slope | 2 | 0.86667 | 0 | 20 | -20 | 0.00059523 | 0.00021355 | 0.0043664
321 | 0:53 | -10.5496 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -10.7616 | -0.10762 | -0.10762 | -10.5496 | 0.00010599 | [13 empty] | 0.97483 | 1 | 0.97286 | 0.89414 | 0.77098 | 0.61593 | 0.44714 | 0.28793 | 0.14638 | 0.020048 | -0.10702 | -0.23934 | -0.37998 | -0.43182 | -0.47245 | -0.49417 | -0.50191 | -0.50443 | -0.50967 | -0.51676 | -0.53338 | -0.56582 | -0.61129 | -0.65688 | -0.70197 | -0.73423 | -0.76908 | -0.7933 | -0.78969 | -0.75604 | -0.69092 | -0.0053808 | 0.0040763 | 0.00020382 | 0.00020382 | 0 | 0 | 0.0042007 | 0.05 | 0.54706 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.45315 | 0.59257 | 0.73642 | 0.88193 | 0.97195 | 0.83079 | 0.70407 | 0.59966 | 0.51608 | 0.45328 | 0.40251 | 0.36035 | 0.31821 | 0.20349 | 0.1083 | 0.044626 | 0.017551 | 0.017484 | 0.046395 | 0.094628 | 0.15319 | 0.22591 | 0.3137 | 0.40848 | 0.50958 | 0.59582 | 0.69361 | 0.79733 | 0.88694 | 0.9591 | 0.98936 | 0.98936 | 30 | Slope | 0.033333 | 0.48438 | 0.53086 | 0.5677 | 0.60509 | 0.62398 | 0.56582 | 0.51247 | 0.46655 | 0.42758 | 0.39554 | 0.3675 | 0.34234 | 0.31718 | 0.26783 | 0.22499 | 0.19265 | 0.17252 | 0.16138 | 0.15991 | 0.16488 | 0.17329 | 0.18641 | 0.20457 | 0.22505 | 0.24764 | 0.26527 | 0.28676 | 0.31022 | 0.32898 | 0.34192 | 0.3409 | 0.62398 | 4 | 0.97195 | Slope | 0.9 | 0.10762 |  | 0.4673 | 0 | 0.97195 | Slope | 2 | 0.9 | 0 | 20 | -20 | 0.00010599 | 0.00019869 | 0.0042007
322 | 0:53 | -10.7616 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -10.5317 | -0.10532 | -0.10532 | -10.7616 | 0.00011494 | [13 empty] | 0.97286 | 1 | 0.97028 | 0.88364 | 0.74886 | 0.58728 | 0.42852 | 0.28847 | 0.17007 | 0.054428 | -0.068106 | -0.20856 | -0.28041 | -0.34362 | -0.37905 | -0.38952 | -0.39077 | -0.389 | -0.39495 | -0.40713 | -0.44051 | -0.48945 | -0.54588 | -0.60538 | -0.6479 | -0.69811 | -0.74246 | -0.77223 | -0.77761 | -0.76412 | -0.71299 | -0.0052658 | 0.0026378 | 0.00013189 | 0.00013189 | 0 | 0 | 0.0040174 | 0.05 | 0.40763 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.5925 | 0.73635 | 0.88186 | 0.97202 | 0.83087 | 0.70414 | 0.59973 | 0.51615 | 0.45335 | 0.40258 | 0.36042 | 0.31828 | 0.20356 | 0.10838 | 0.044698 | 0.017623 | 0.017556 | 0.046467 | 0.094699 | 0.15326 | 0.22598 | 0.31377 | 0.40855 | 0.50965 | 0.59589 | 0.69369 | 0.79741 | 0.88701 | 0.95917 | 0.98929 | 0.9502 | 0.98929 | 29 | Slope | 0.066667 | 0.53083 | 0.57878 | 0.61617 | 0.63512 | 0.57696 | 0.5236 | 0.47769 | 0.43872 | 0.40667 | 0.37864 | 0.35347 | 0.32832 | 0.27896 | 0.23613 | 0.20379 | 0.18365 | 0.17252 | 0.17104 | 0.17601 | 0.18442 | 0.19755 | 0.2157 | 0.23618 | 0.25877 | 0.27641 | 0.2979 | 0.32136 | 0.34012 | 0.35306 | 0.35199 | 0.32785 | 0.63512 | 3 | 0.97202 | Slope | 0.93333 | 0.10532 |  | 0.47868 | 0 | 0.97202 | Slope | 2 | 0.93333 | 0 | 20 | -20 | 0.00011494 | 0.00018901 | 0.0040174
323 | 0:54 | -10.5317 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -10.1535 | -0.10154 | -0.10154 | -10.5317 | 0.00018909 | [13 empty] | 0.97028 | 1 | 0.96719 | 0.87187 | 0.7301 | 0.57632 | 0.43548 | 0.31865 | 0.21151 | 0.101 | -0.029803 | -0.11234 | -0.19073 | -0.24496 | -0.26544 | -0.26644 | -0.2597 | -0.25541 | -0.26503 | -0.29313 | -0.34276 | -0.4025 | -0.47485 | -0.53216 | -0.59585 | -0.6587 | -0.71472 | -0.75965 | -0.78925 | -0.79233 | -0.73885 | -0.0050768 | 0.0011828 | 5.9138e-05 | 5.9138e-05 | 0 | 0 | 0.0038288 | 0.05 | 0.26378 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.73627 | 0.88178 | 0.9721 | 0.83094 | 0.70421 | 0.5998 | 0.51623 | 0.45343 | 0.40266 | 0.3605 | 0.31835 | 0.20363 | 0.10845 | 0.044771 | 0.017695 | 0.017629 | 0.04654 | 0.094772 | 0.15334 | 0.22605 | 0.31385 | 0.40862 | 0.50972 | 0.59596 | 0.69376 | 0.79748 | 0.88709 | 0.95924 | 0.98922 | 0.95013 | 0.91388 | 0.98922 | 28 | Slope | 0.1 | 0.57876 | 0.62726 | 0.64625 | 0.58809 | 0.53474 | 0.48882 | 0.44985 | 0.41781 | 0.38977 | 0.36461 | 0.33945 | 0.2901 | 0.24726 | 0.21492 | 0.19479 | 0.18365 | 0.18218 | 0.18715 | 0.19556 | 0.20868 | 0.22684 | 0.24732 | 0.26991 | 0.28754 | 0.30903 | 0.33249 | 0.35125 | 0.36419 | 0.36307 | 0.33893 | 0.31574 | 0.64625 | 2 | 0.9721 | Slope | 0.96667 | 0.10154 |  | 0.4974 | 0 | 0.9721 | Slope | 2 | 0.96667 | 0 | 20 | -20 | 0.00018909 | 0.00018468 | 0.0038288
324 | 0:54 | -10.1535 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -8.9344 | -0.089344 | -0.089344 | -10.1535 | 0.00060957 | [13 empty] | 0.96719 | 1 | 0.96381 | 0.86335 | 0.72803 | 0.59101 | 0.47329 | 0.36814 | 0.26675 | 0.14808 | 0.064384 | -0.01997 | -0.085404 | -0.12079 | -0.12896 | -0.11818 | -0.10569 | -0.1026 | -0.12741 | -0.17061 | -0.23036 | -0.30701 | -0.37703 | -0.45967 | -0.53909 | -0.62061 | -0.69871 | -0.77299 | -0.82177 | -0.82461 | -0.76397 | -0.0044672 | -0.00027845 | -1.3923e-05 | -1.3923e-05 | 0 | 0 | 0.0036397 | 0.05 | 0.11828 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.88171 | 0.97217 | 0.83101 | 0.70429 | 0.59987 | 0.5163 | 0.4535 | 0.40273 | 0.36057 | 0.31843 | 0.20371 | 0.10852 | 0.044844 | 0.017768 | 0.017702 | 0.046613 | 0.094845 | 0.15341 | 0.22612 | 0.31392 | 0.4087 | 0.5098 | 0.59603 | 0.69383 | 0.79755 | 0.88716 | 0.95931 | 0.98914 | 0.95006 | 0.91381 | 0.88531 | 0.98914 | 27 | Slope | 0.13333 | 0.62724 | 0.65739 | 0.59923 | 0.54587 | 0.49996 | 0.46099 | 0.42894 | 0.40091 | 0.37575 | 0.35059 | 0.30124 | 0.2584 | 0.22606 | 0.20592 | 0.19479 | 0.19332 | 0.19828 | 0.20669 | 0.21982 | 0.23797 | 0.25845 | 0.28104 | 0.29868 | 0.32017 | 0.34363 | 0.36239 | 0.37533 | 0.37416 | 0.35002 | 0.32682 | 0.30622 | 0.65739 | 1 | 0.97217 | Slope | 1 | 0.089344 |  | 0.55775 | 0 | 0.97217 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00060957 | 0.00018503 | 0.0036397
325 | 0:54 | -8.9344 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -6.3241 | -0.063241 | -0.063241 | -8.9344 | 0.0013051 | [13 empty] | 0.96381 | 1 | 0.96256 | 0.86803 | 0.74807 | 0.63335 | 0.52763 | 0.42892 | 0.32049 | 0.23917 | 0.15822 | 0.090141 | 0.046615 | 0.025488 | 0.031431 | 0.050318 | 0.063528 | 0.053503 | 0.01472 | -0.036767 | -0.1135 | -0.18593 | -0.28469 | -0.38665 | -0.49038 | -0.59913 | -0.70897 | -0.80336 | -0.85329 | -0.85121 | -0.77498 | -0.0031621 | -0.00169 | -8.4501e-05 | -8.4501e-05 | 0 | 0 | 0.0034801 | 0.05 | -0.027845 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.97224 | 0.83108 | 0.70436 | 0.59995 | 0.51637 | 0.45357 | 0.4028 | 0.36064 | 0.3185 | 0.20378 | 0.10859 | 0.044914 | 0.017839 | 0.017773 | 0.046683 | 0.094916 | 0.15348 | 0.22619 | 0.31399 | 0.40877 | 0.50987 | 0.59611 | 0.6939 | 0.79762 | 0.88723 | 0.95939 | 0.98907 | 0.94999 | 0.91374 | 0.88524 | 0.86827 | 0.98907 | 26 | Slope | 0.16667 | 0.65741 | 0.61036 | 0.55701 | 0.51109 | 0.47212 | 0.44008 | 0.41204 | 0.38688 | 0.36172 | 0.31237 | 0.26953 | 0.23719 | 0.21706 | 0.20592 | 0.20445 | 0.20942 | 0.21783 | 0.23095 | 0.24911 | 0.26959 | 0.29218 | 0.30981 | 0.3313 | 0.35476 | 0.37352 | 0.38646 | 0.38525 | 0.36111 | 0.33791 | 0.3173 | 0.30053 | 0.65741 | 0 | 0.97224 | Slope | 1 | 0.063241 |  | 0.68695 | 0 | 0.97224 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0013051 | 0.00018883 | 0.0034801
326 | 0:54 | -6.3241 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.6542 | -0.026542 | -0.026542 | -6.3241 | 0.001835 | [13 empty] | 0.96256 | 1 | 0.9661 | 0.88368 | 0.78328 | 0.68057 | 0.58217 | 0.47912 | 0.39933 | 0.32505 | 0.26174 | 0.21618 | 0.18745 | 0.18041 | 0.19437 | 0.21469 | 0.21643 | 0.19478 | 0.14922 | 0.082454 | 0.012813 | -0.088807 | -0.20875 | -0.33719 | -0.46735 | -0.60325 | -0.72883 | -0.82361 | -0.86893 | -0.85361 | -0.75625 | -0.0013271 | -0.0029573 | -0.00014786 | -0.00014786 | 0 | 0 | 0.0033958 | 0.05 | -0.169 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.83115 | 0.70442 | 0.60001 | 0.51643 | 0.45363 | 0.40286 | 0.3607 | 0.31856 | 0.20384 | 0.10866 | 0.044978 | 0.017902 | 0.017836 | 0.046747 | 0.094979 | 0.15354 | 0.22626 | 0.31405 | 0.40883 | 0.50993 | 0.59617 | 0.69397 | 0.79769 | 0.88729 | 0.95945 | 0.98901 | 0.94992 | 0.91367 | 0.88518 | 0.86821 | 0.86252 | 0.98901 | 25 | Slope | 0.2 | 0.61038 | 0.56814 | 0.52223 | 0.48326 | 0.45121 | 0.42318 | 0.39801 | 0.37285 | 0.3235 | 0.28066 | 0.24833 | 0.22819 | 0.21706 | 0.21558 | 0.22055 | 0.22896 | 0.24209 | 0.26024 | 0.28072 | 0.30331 | 0.32095 | 0.34243 | 0.3659 | 0.38465 | 0.39759 | 0.39634 | 0.3722 | 0.349 | 0.32839 | 0.31162 | 0.29862 | 0.61038 | 0 | 0.83115 | Slope | 1 | 0.026542 |  | 0.86862 | 0 | 0.83115 | Slope | 2 | 1 | 0 | 20 | -20 | 0.001835 | 0.00019469 | 0.0033958
327 | 0:54 | -2.6542 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 0.55704 | 0.0055704 | 0.0055704 | -2.6542 | 0.0016056 | [13 empty] | 0.9661 | 1 | 0.97062 | 0.90128 | 0.81139 | 0.71629 | 0.61702 | 0.53383 | 0.46445 | 0.40642 | 0.36294 | 0.33078 | 0.31447 | 0.31376 | 0.32825 | 0.33818 | 0.32954 | 0.303 | 0.24359 | 0.1869 | 0.089262 | -0.032962 | -0.17692 | -0.32565 | -0.47185 | -0.61459 | -0.73724 | -0.82524 | -0.85727 | -0.82318 | -0.71589 | 0.00027852 | -0.0040014 | -0.00020007 | -0.00020007 | 0 | 0 | 0.0034007 | 0.05 | -0.29573 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.70447 | 0.60006 | 0.51649 | 0.45369 | 0.40292 | 0.36075 | 0.31861 | 0.20389 | 0.10871 | 0.04503 | 0.017955 | 0.017888 | 0.046799 | 0.095031 | 0.1536 | 0.22631 | 0.31411 | 0.40888 | 0.50998 | 0.59622 | 0.69402 | 0.79774 | 0.88735 | 0.9595 | 0.98896 | 0.94987 | 0.91362 | 0.88513 | 0.86815 | 0.86247 | 0.86095 | 0.98896 | 24 | Slope | 0.23333 | 0.56816 | 0.53335 | 0.49438 | 0.46234 | 0.43431 | 0.40914 | 0.38398 | 0.33463 | 0.29179 | 0.25945 | 0.23932 | 0.22818 | 0.22671 | 0.23168 | 0.24009 | 0.25321 | 0.27137 | 0.29185 | 0.31444 | 0.33207 | 0.35356 | 0.37702 | 0.39578 | 0.40872 | 0.40743 | 0.38329 | 0.3601 | 0.33949 | 0.32272 | 0.30971 | 0.2981 | 0.56816 | 0 | 0.70447 | Slope | 1 | 0.0055704 |  | 0.97243 | 0 | 0.70447 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0016056 | 0.00020122 | 0.0034007
328 | 0:54 | 0.55704 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.5582 | 0.035582 | 0.035582 | 0.55704 | 0.0015006 | [13 empty] | 0.97062 | 1 | 0.97524 | 0.91292 | 0.82952 | 0.73577 | 0.64639 | 0.57649 | 0.52121 | 0.47952 | 0.44755 | 0.42614 | 0.41509 | 0.41412 | 0.41876 | 0.41901 | 0.40611 | 0.36749 | 0.31918 | 0.23621 | 0.1185 | -0.024936 | -0.18385 | -0.33913 | -0.48478 | -0.62185 | -0.73526 | -0.80879 | -0.8224 | -0.77953 | -0.65994 | 0.0017791 | -0.0048371 | -0.00024186 | -0.00024186 | 0 | 0 | 0.0034566 | 0.05 | -0.40014 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.6001 | 0.51653 | 0.45373 | 0.40296 | 0.3608 | 0.31866 | 0.20393 | 0.10875 | 0.045072 | 0.017996 | 0.01793 | 0.046841 | 0.095073 | 0.15364 | 0.22635 | 0.31415 | 0.40893 | 0.51003 | 0.59626 | 0.69406 | 0.79778 | 0.88739 | 0.95954 | 0.98891 | 0.94983 | 0.91358 | 0.88508 | 0.86811 | 0.86243 | 0.86091 | 0.86548 | 0.98891 | 23 | Slope | 0.26667 | 0.53337 | 0.50551 | 0.47346 | 0.44543 | 0.42027 | 0.39511 | 0.34576 | 0.30292 | 0.27058 | 0.25044 | 0.23931 | 0.23784 | 0.2428 | 0.25121 | 0.26434 | 0.28249 | 0.30298 | 0.32556 | 0.3432 | 0.36469 | 0.38815 | 0.40691 | 0.41985 | 0.41853 | 0.39439 | 0.37119 | 0.35058 | 0.33382 | 0.32081 | 0.30919 | 0.2996 | 0.53337 | 0 | 0.6001 | Slope | 1 | 0.035582 |  | 0.82387 | 0 | 0.6001 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0015006 | 0.00020742 | 0.0034566
329 | 0:55 | 3.5582 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 5.0168 | 0.050168 | 0.050168 | 3.5582 | 0.00072929 | [13 empty] | 0.97524 | 1 | 0.97718 | 0.91869 | 0.83757 | 0.74306 | 0.66938 | 0.61118 | 0.56823 | 0.53557 | 0.51217 | 0.49492 | 0.48321 | 0.4729 | 0.46785 | 0.46377 | 0.43972 | 0.4129 | 0.33939 | 0.2369 | 0.10061 | -0.053054 | -0.21064 | -0.35951 | -0.4982 | -0.62458 | -0.72277 | -0.77797 | -0.78282 | -0.72761 | -0.60199 | 0.0025084 | -0.0054651 | -0.00027326 | -0.00027326 | 0 | 0 | 0.0035338 | 0.05 | -0.48371 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.51656 | 0.45376 | 0.40299 | 0.36083 | 0.31869 | 0.20397 | 0.10878 | 0.045103 | 0.018028 | 0.017961 | 0.046872 | 0.095105 | 0.15367 | 0.22638 | 0.31418 | 0.40896 | 0.51006 | 0.59629 | 0.69409 | 0.79781 | 0.88742 | 0.95957 | 0.98888 | 0.9498 | 0.91355 | 0.88505 | 0.86808 | 0.86239 | 0.86088 | 0.86544 | 0.87356 | 0.98888 | 22 | Slope | 0.3 | 0.50552 | 0.48459 | 0.45655 | 0.43139 | 0.40623 | 0.35688 | 0.31404 | 0.2817 | 0.26156 | 0.25043 | 0.24896 | 0.25392 | 0.26233 | 0.27546 | 0.29362 | 0.3141 | 0.33669 | 0.35432 | 0.37581 | 0.39927 | 0.41803 | 0.43097 | 0.42963 | 0.40549 | 0.38229 | 0.36168 | 0.34492 | 0.33191 | 0.32029 | 0.3107 | 0.3023 | 0.50552 | 0 | 0.51656 | Slope | 1 | 0.050168 |  | 0.75167 | 0 | 0.51656 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00072929 | 0.00021274 | 0.0035338
330 | 0:55 | 5.0168 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 5.854 | 0.05854 | 0.05854 | 5.0168 | 0.00041864 | [13 empty] | 0.97718 | 1 | 0.97839 | 0.92169 | 0.8289 | 0.75273 | 0.69063 | 0.64367 | 0.6091 | 0.58465 | 0.56548 | 0.5478 | 0.52756 | 0.50757 | 0.49789 | 0.48348 | 0.47139 | 0.42139 | 0.32871 | 0.20819 | 0.062125 | -0.088213 | -0.23741 | -0.37915 | -0.50698 | -0.6183 | -0.69882 | -0.74516 | -0.73741 | -0.67488 | -0.54603 | 0.002927 | -0.0059728 | -0.00029864 | -0.00029864 | 0 | 0 | 0.0036086 | 0.05 | -0.54651 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.45378 | 0.40301 | 0.36085 | 0.31871 | 0.20399 | 0.10881 | 0.045129 | 0.018053 | 0.017987 | 0.046897 | 0.09513 | 0.15369 | 0.22641 | 0.31421 | 0.40898 | 0.51008 | 0.59632 | 0.69412 | 0.79784 | 0.88744 | 0.9596 | 0.98886 | 0.94977 | 0.91352 | 0.88503 | 0.86806 | 0.86237 | 0.86086 | 0.86542 | 0.87354 | 0.8842 | 0.98886 | 21 | Slope | 0.33333 | 0.48459 | 0.46767 | 0.44251 | 0.41735 | 0.368 | 0.32516 | 0.29282 | 0.27268 | 0.26155 | 0.26008 | 0.26504 | 0.27345 | 0.28658 | 0.30474 | 0.32522 | 0.34781 | 0.36544 | 0.38693 | 0.41039 | 0.42915 | 0.44209 | 0.44073 | 0.41659 | 0.3934 | 0.37279 | 0.35602 | 0.34301 | 0.3314 | 0.32181 | 0.3134 | 0.30584 | 0.48459 | 0 | 0.45378 | Slope | 1 | 0.05854 |  | 0.71022 | 0 | 0.45378 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00041864 | 0.00021694 | 0.0036086
331 | 0:55 | 5.854 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 5.3081 | 0.053081 | 0.053081 | 5.854 | 0.000273 | [13 empty] | 0.97839 | 1 | 0.97911 | 0.90059 | 0.82808 | 0.76404 | 0.71322 | 0.67479 | 0.64876 | 0.62901 | 0.6099 | 0.58462 | 0.55511 | 0.52989 | 0.50992 | 0.5074 | 0.47387 | 0.40629 | 0.29527 | 0.16444 | 0.021858 | -0.1196 | -0.26182 | -0.39275 | -0.50608 | -0.60073 | -0.67274 | -0.70657 | -0.69082 | -0.62341 | -0.49578 | 0.002654 | -0.0063945 | -0.00031972 | -0.00031972 | 0 | 0 | 0.003676 | 0.05 | -0.59728 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.40304 | 0.36087 | 0.31873 | 0.20401 | 0.10883 | 0.04515 | 0.018074 | 0.018008 | 0.046919 | 0.095151 | 0.15372 | 0.22643 | 0.31423 | 0.409 | 0.5101 | 0.59634 | 0.69414 | 0.79786 | 0.88747 | 0.95962 | 0.98884 | 0.94975 | 0.9135 | 0.88501 | 0.86803 | 0.86235 | 0.86083 | 0.8654 | 0.87352 | 0.88418 | 0.8953 | 0.98884 | 20 | Slope | 0.36667 | 0.46768 | 0.45362 | 0.42847 | 0.37912 | 0.33628 | 0.30394 | 0.2838 | 0.27267 | 0.2712 | 0.27616 | 0.28457 | 0.2977 | 0.31585 | 0.33633 | 0.35892 | 0.37656 | 0.39805 | 0.42151 | 0.44027 | 0.45321 | 0.45183 | 0.4277 | 0.4045 | 0.38389 | 0.36712 | 0.35412 | 0.3425 | 0.33291 | 0.32451 | 0.31695 | 0.30954 | 0.46768 | 0 | 0.40304 | Slope | 1 | 0.053081 |  | 0.73725 | 0 | 0.40304 | Slope | 2 | 1 | 0 | 20 | -20 | 0.000273 | 0.00022003 | 0.003676
332 | 0:55 | 5.3081 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 4.9571 | 0.049571 | 0.049571 | 5.3081 | 0.0001755 | [13 empty] | 0.97911 | 1 | 0.9491 | 0.89201 | 0.83383 | 0.78375 | 0.74357 | 0.71606 | 0.69645 | 0.67781 | 0.65226 | 0.61875 | 0.58434 | 0.54849 | 0.53987 | 0.51752 | 0.46822 | 0.38108 | 0.25609 | 0.12501 | -0.010306 | -0.14515 | -0.2766 | -0.3934 | -0.49105 | -0.57758 | -0.63746 | -0.6628 | -0.64109 | -0.57301 | -0.45656 | 0.0024785 | -0.0068159 | -0.00034079 | -0.00034079 | 0 | 0 | 0.003738 | 0.05 | -0.63945 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.3609 | 0.31875 | 0.20403 | 0.10885 | 0.045171 | 0.018095 | 0.018029 | 0.04694 | 0.095172 | 0.15374 | 0.22645 | 0.31425 | 0.40902 | 0.51012 | 0.59636 | 0.69416 | 0.79788 | 0.88749 | 0.95964 | 0.98882 | 0.94973 | 0.91348 | 0.88499 | 0.86801 | 0.86233 | 0.86081 | 0.86538 | 0.8735 | 0.88416 | 0.89528 | 0.90085 | 0.98882 | 19 | Slope | 0.4 | 0.45363 | 0.43958 | 0.39023 | 0.34739 | 0.31506 | 0.29492 | 0.28379 | 0.28231 | 0.28728 | 0.29569 | 0.30882 | 0.32697 | 0.34745 | 0.37004 | 0.38768 | 0.40916 | 0.43263 | 0.45138 | 0.46432 | 0.46294 | 0.4388 | 0.4156 | 0.395 | 0.37823 | 0.36522 | 0.3536 | 0.34401 | 0.33561 | 0.32805 | 0.32065 | 0.31139 | 0.46432 | 18 | 0.95964 | Slope | 0.43333 | 0.049571 |  | 0.75463 | 0 | 0.95964 | Slope | 2 | 0.43333 | 0 | 20 | -20 | 0.0001755 | 0.00022263 | 0.003738
333 | 0:55 | 4.9571 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 5.7051 | 0.057051 | 0.057051 | 4.9571 | 0.00037401 | [13 empty] | 0.9491 | 1 | 0.95487 | 0.90347 | 0.85507 | 0.81394 | 0.78122 | 0.756 | 0.73266 | 0.69409 | 0.64618 | 0.60076 | 0.54468 | 0.53401 | 0.48174 | 0.42988 | 0.36138 | 0.26499 | 0.15069 | 0.040564 | -0.073433 | -0.17473 | -0.26315 | -0.33681 | -0.41113 | -0.46815 | -0.50756 | -0.51855 | -0.49402 | -0.44705 | -0.36438 | 0.0028525 | -0.0079631 | -0.00039815 | -0.00039815 | 0 | 0 | 0.0041269 | 0.05 | -0.68159 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.31881 | 0.20409 | 0.10891 | 0.045228 | 0.018153 | 0.018086 | 0.046997 | 0.09523 | 0.15379 | 0.22651 | 0.3143 | 0.40908 | 0.51018 | 0.59642 | 0.69422 | 0.79794 | 0.88754 | 0.9597 | 0.98876 | 0.94967 | 0.91342 | 0.88493 | 0.86796 | 0.86227 | 0.86076 | 0.86532 | 0.87344 | 0.8841 | 0.89522 | 0.90079 | 0.89767 | 0.98876 | 18 | Slope | 0.43333 | 0.4396 | 0.40136 | 0.35852 | 0.32619 | 0.30605 | 0.29492 | 0.29344 | 0.29841 | 0.30682 | 0.31995 | 0.3381 | 0.35858 | 0.38117 | 0.39881 | 0.42029 | 0.44376 | 0.46251 | 0.47546 | 0.47403 | 0.44989 | 0.4267 | 0.40609 | 0.38932 | 0.37631 | 0.3647 | 0.35511 | 0.3467 | 0.33914 | 0.33174 | 0.32249 | 0.31033 | 0.47546 | 17 | 0.9597 | Slope | 0.46667 | 0.057051 |  | 0.7176 | 0 | 0.9597 | Slope | 2 | 0.46667 | 0 | 20 | -20 | 0.00037401 | 0.00022464 | 0.0041269
334 | 0:55 | 5.7051 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 8.5072 | 0.085072 | 0.085072 | 5.7051 | 0.0014011 | [13 empty] | 0.95487 | 1 | 0.96056 | 0.91861 | 0.87923 | 0.8467 | 0.81783 | 0.79053 | 0.75137 | 0.69426 | 0.63576 | 0.57084 | 0.53506 | 0.48665 | 0.40755 | 0.33883 | 0.26187 | 0.17358 | 0.075937 | -0.019457 | -0.10791 | -0.1763 | -0.23172 | -0.28878 | -0.34051 | -0.38157 | -0.40845 | -0.41458 | -0.40423 | -0.38031 | -0.31101 | 0.0042536 | -0.0089149 | -0.00044575 | -0.00044575 | 0 | 0 | 0.0044187 | 0.05 | -0.79631 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.20414 | 0.10895 | 0.045276 | 0.0182 | 0.018134 | 0.047045 | 0.095277 | 0.15384 | 0.22655 | 0.31435 | 0.40913 | 0.51023 | 0.59647 | 0.69426 | 0.79798 | 0.88759 | 0.95975 | 0.98871 | 0.94963 | 0.91338 | 0.88488 | 0.86791 | 0.86222 | 0.86071 | 0.86527 | 0.87339 | 0.88405 | 0.89517 | 0.90075 | 0.89762 | 0.89012 | 0.98871 | 17 | Slope | 0.46667 | 0.40138 | 0.36965 | 0.33731 | 0.31718 | 0.30604 | 0.30457 | 0.30954 | 0.31795 | 0.33107 | 0.34923 | 0.36971 | 0.3923 | 0.40993 | 0.43142 | 0.45488 | 0.47364 | 0.48658 | 0.48513 | 0.46099 | 0.43779 | 0.41718 | 0.40041 | 0.38741 | 0.37579 | 0.3662 | 0.3578 | 0.35024 | 0.34284 | 0.33358 | 0.32143 | 0.30782 | 0.48658 | 16 | 0.95975 | Slope | 0.5 | 0.085072 |  | 0.57889 | 0 | 0.95975 | Slope | 2 | 0.5 | 0 | 20 | -20 | 0.0014011 | 0.00022303 | 0.0044187
335 | 0:56 | 8.5072 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 12.1976 | 0.12198 | 0.12198 | 8.5072 | 0.0018452 | [13 empty] | 0.96056 | 1 | 0.96569 | 0.92997 | 0.89727 | 0.86788 | 0.83728 | 0.79699 | 0.74136 | 0.67336 | 0.5959 | 0.54645 | 0.47585 | 0.40157 | 0.30933 | 0.23853 | 0.17478 | 0.10282 | 0.016282 | -0.058945 | -0.12063 | -0.16267 | -0.20591 | -0.2458 | -0.28537 | -0.31669 | -0.3393 | -0.35646 | -0.36465 | -0.3497 | -0.22083 | 0.0060988 | -0.0095517 | -0.00047759 | -0.00047759 | 0 | 0 | 0.0046211 | 0.05 | -0.89149 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.10899 | 0.045308 | 0.018232 | 0.018166 | 0.047076 | 0.095309 | 0.15387 | 0.22659 | 0.31438 | 0.40916 | 0.51026 | 0.5965 | 0.69429 | 0.79802 | 0.88762 | 0.95978 | 0.98868 | 0.94959 | 0.91334 | 0.88485 | 0.86788 | 0.86219 | 0.86068 | 0.86524 | 0.87336 | 0.88402 | 0.89514 | 0.90071 | 0.89759 | 0.89009 | 0.96652 | 0.98868 | 16 | Slope | 0.5 | 0.36966 | 0.34844 | 0.3283 | 0.31717 | 0.31569 | 0.32066 | 0.32907 | 0.3422 | 0.36035 | 0.38083 | 0.40342 | 0.42106 | 0.44254 | 0.46601 | 0.48476 | 0.4977 | 0.49623 | 0.47209 | 0.44889 | 0.42828 | 0.41151 | 0.39851 | 0.38689 | 0.3773 | 0.3689 | 0.36134 | 0.35394 | 0.34468 | 0.33253 | 0.31892 | 0.33329 | 0.4977 | 15 | 0.95978 | Slope | 0.53333 | 0.12198 |  | 0.39622 | 0 | 0.95978 | Slope | 2 | 0.53333 | 0 | 20 | -20 | 0.0018452 | 0.00021754 | 0.0046211
336 | 0:56 | 12.1976 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 14.4994 | 0.14499 | 0.14499 | 12.1976 | 0.0011509 | [13 empty] | 0.96569 | 1 | 0.96774 | 0.93507 | 0.90352 | 0.87186 | 0.82995 | 0.77398 | 0.70634 | 0.61853 | 0.55129 | 0.46804 | 0.36972 | 0.28718 | 0.20037 | 0.15147 | 0.1063 | 0.042108 | -0.028095 | -0.081333 | -0.12132 | -0.15438 | -0.18446 | -0.21563 | -0.24823 | -0.27695 | -0.30978 | -0.34356 | -0.35976 | -0.24552 | -0.11353 | 0.0072497 | -0.0098225 | -0.00049112 | -0.00049112 | 0 | 0 | 0.004716 | 0.05 | -0.95517 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.045321 | 0.018246 | 0.018179 | 0.04709 | 0.095322 | 0.15389 | 0.2266 | 0.3144 | 0.40917 | 0.51027 | 0.59651 | 0.69431 | 0.79803 | 0.88764 | 0.95979 | 0.98867 | 0.94958 | 0.91333 | 0.88483 | 0.86786 | 0.86218 | 0.86066 | 0.86523 | 0.87335 | 0.88401 | 0.89513 | 0.9007 | 0.89758 | 0.89008 | 0.96651 | 0.96183 | 0.98867 | 15 | Slope | 0.53333 | 0.34844 | 0.33942 | 0.32828 | 0.32681 | 0.33177 | 0.34018 | 0.35331 | 0.37147 | 0.39195 | 0.41454 | 0.43217 | 0.45366 | 0.47712 | 0.49588 | 0.50882 | 0.50733 | 0.48319 | 0.46 | 0.43939 | 0.42262 | 0.40961 | 0.398 | 0.38841 | 0.38 | 0.37245 | 0.36504 | 0.35579 | 0.34364 | 0.33003 | 0.34439 | 0.33172 | 0.50882 | 14 | 0.95979 | Slope | 0.56667 | 0.14499 |  | 0.28228 | 0 | 0.95979 | Slope | 2 | 0.56667 | 0 | 20 | -20 | 0.0011509 | 0.00020833 | 0.004716
337 | 0:56 | 14.4994 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 16.523 | 0.16523 | 0.16523 | 14.4994 | 0.0010118 | [13 empty] | 0.96774 | 1 | 0.96827 | 0.93526 | 0.90088 | 0.85896 | 0.80166 | 0.7326 | 0.64454 | 0.56249 | 0.4607 | 0.34762 | 0.24289 | 0.17168 | 0.11316 | 0.085207 | 0.045881 | -0.0047599 | -0.056151 | -0.09092 | -0.1239 | -0.14631 | -0.16985 | -0.19613 | -0.22759 | -0.26657 | -0.31553 | -0.35767 | -0.24683 | -0.12926 | -0.010559 | 0.0082615 | -0.0098231 | -0.00049116 | -0.00049116 | 0 | 0 | 0.0047162 | 0.05 | -0.98225 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.018246 | 0.018179 | 0.04709 | 0.095323 | 0.15389 | 0.2266 | 0.3144 | 0.40917 | 0.51027 | 0.59651 | 0.69431 | 0.79803 | 0.88764 | 0.95979 | 0.98867 | 0.94958 | 0.91333 | 0.88483 | 0.86786 | 0.86218 | 0.86066 | 0.86523 | 0.87335 | 0.88401 | 0.89513 | 0.9007 | 0.89758 | 0.89008 | 0.96651 | 0.96183 | 0.90196 | 0.98867 | 14 | Slope | 0.56667 | 0.33942 | 0.33939 | 0.33792 | 0.34289 | 0.3513 | 0.36442 | 0.38258 | 0.40306 | 0.42565 | 0.44328 | 0.46477 | 0.48823 | 0.50699 | 0.51993 | 0.51844 | 0.4943 | 0.47111 | 0.4505 | 0.43373 | 0.42073 | 0.40911 | 0.39952 | 0.39112 | 0.38356 | 0.37615 | 0.3669 | 0.35475 | 0.34114 | 0.3555 | 0.34283 | 0.31177 | 0.51993 | 13 | 0.95979 | Slope | 0.6 | 0.16523 |  | 0.18211 | 0 | 0.95979 | Slope | 2 | 0.6 | 0 | 20 | -20 | 0.0010118 | 0.00019604 | 0.0047162
338 | 0:56 | 16.523 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 16.9532 | 0.16953 | 0.16953 | 16.523 | 0.00021509 | [13 empty] | 0.96827 | 1 | 0.96636 | 0.92983 | 0.88618 | 0.82933 | 0.75762 | 0.66723 | 0.58039 | 0.46261 | 0.32739 | 0.20916 | 0.12024 | 0.084144 | 0.049104 | 0.025779 | -0.0024211 | -0.037605 | -0.074194 | -0.10411 | -0.12907 | -0.14696 | -0.16757 | -0.19434 | -0.23644 | -0.29157 | -0.35018 | -0.23713 | -0.12254 | -0.016162 | 0.094691 | 0.0084766 | -0.009534 | -0.0004767 | -0.0004767 | 0 | 0 | 0.0046019 | 0.05 | -0.98231 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.018165 | 0.047075 | 0.095308 | 0.15387 | 0.22659 | 0.31438 | 0.40916 | 0.51026 | 0.5965 | 0.69429 | 0.79801 | 0.88762 | 0.95978 | 0.98868 | 0.9496 | 0.91334 | 0.88485 | 0.86788 | 0.86219 | 0.86068 | 0.86524 | 0.87336 | 0.88402 | 0.89514 | 0.90071 | 0.89759 | 0.89009 | 0.96652 | 0.96182 | 0.90195 | 0.85157 | 0.98868 | 13 | Slope | 0.6 | 0.33939 | 0.34903 | 0.35399 | 0.3624 | 0.37553 | 0.39368 | 0.41416 | 0.43675 | 0.45439 | 0.47588 | 0.49934 | 0.5181 | 0.53104 | 0.52956 | 0.50542 | 0.48223 | 0.46162 | 0.44485 | 0.43184 | 0.42023 | 0.41064 | 0.40223 | 0.39467 | 0.38727 | 0.37802 | 0.36586 | 0.35225 | 0.36662 | 0.35394 | 0.32287 | 0.29497 | 0.53104 | 12 | 0.95978 | Slope | 0.63333 | 0.16953 |  | 0.16082 | 0 | 0.95978 | Slope | 2 | 0.63333 | 0 | 20 | -20 | 0.00021509 | 0.00018134 | 0.0046019
339 | 0:56 | 16.9532 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 16.0106 | 0.16011 | 0.16011 | 16.9532 | 0.00047134 | [13 empty] | 0.96636 | 1 | 0.96267 | 0.91797 | 0.86006 | 0.7883 | 0.69467 | 0.60162 | 0.47906 | 0.32463 | 0.18285 | 0.082675 | 0.032491 | 0.022044 | -0.0095786 | -0.023319 | -0.038111 | -0.060912 | -0.094518 | -0.11846 | -0.1406 | -0.15684 | -0.17893 | -0.21631 | -0.27443 | -0.34028 | -0.22666 | -0.10919 | -0.0036771 | 0.096596 | 0.20575 | 0.0080053 | -0.0090517 | -0.00045258 | -0.00045258 | 0 | 0 | 0.0044079 | 0.05 | -0.9534 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.047051 | 0.095284 | 0.15385 | 0.22656 | 0.31436 | 0.40914 | 0.51024 | 0.59647 | 0.69427 | 0.79799 | 0.8876 | 0.95975 | 0.9887 | 0.94962 | 0.91337 | 0.88487 | 0.8679 | 0.86221 | 0.8607 | 0.86526 | 0.87339 | 0.88404 | 0.89517 | 0.90074 | 0.89762 | 0.89012 | 0.96655 | 0.96179 | 0.90192 | 0.85155 | 0.80923 | 0.9887 | 12 | Slope | 0.63333 | 0.34902 | 0.36509 | 0.37351 | 0.38663 | 0.40479 | 0.42527 | 0.44786 | 0.46549 | 0.48698 | 0.51044 | 0.5292 | 0.54214 | 0.54068 | 0.51654 | 0.49335 | 0.47274 | 0.45597 | 0.44296 | 0.43135 | 0.42175 | 0.41335 | 0.40579 | 0.39839 | 0.38913 | 0.37698 | 0.36337 | 0.37774 | 0.36504 | 0.33397 | 0.30607 | 0.28085 | 0.54214 | 11 | 0.95975 | Slope | 0.66667 | 0.16011 |  | 0.20748 | 0 | 0.95975 | Slope | 2 | 0.66667 | 0 | 20 | -20 | 0.00047134 | 0.00016545 | 0.0044079
340 | 0:56 | 16.0106 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 14.3427 | 0.14343 | 0.14343 | 16.0106 | 0.00083392 | [13 empty] | 0.96267 | 1 | 0.95606 | 0.89846 | 0.8259 | 0.73279 | 0.63359 | 0.50534 | 0.34549 | 0.18179 | 0.056994 | -0.0034341 | -0.02809 | -0.034894 | -0.059105 | -0.061123 | -0.064857 | -0.085278 | -0.11484 | -0.13717 | -0.15886 | -0.17707 | -0.20927 | -0.26173 | -0.33099 | -0.21832 | -0.099943 | 0.010656 | 0.11194 | 0.21206 | 0.30901 | 0.0071714 | -0.008466 | -0.0004233 | -0.0004233 | 0 | 0 | 0.0041776 | 0.05 | -0.90517 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | -0.22087 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.095255 | 0.15382 | 0.22653 | 0.31433 | 0.40911 | 0.51021 | 0.59644 | 0.69424 | 0.79796 | 0.88757 | 0.95972 | 0.98873 | 0.94965 | 0.9134 | 0.8849 | 0.86793 | 0.86224 | 0.86073 | 0.86529 | 0.87341 | 0.88407 | 0.8952 | 0.90077 | 0.89765 | 0.89014 | 0.96658 | 0.96176 | 0.90189 | 0.85152 | 0.8092 | 0.77955 | 0.98873 | 11 | Slope | 0.66667 | 0.36508 | 0.38461 | 0.39773 | 0.41589 | 0.43637 | 0.45896 | 0.47659 | 0.49808 | 0.52154 | 0.5403 | 0.55324 | 0.5518 | 0.52766 | 0.50447 | 0.48386 | 0.46709 | 0.45408 | 0.44247 | 0.43288 | 0.42447 | 0.41691 | 0.40951 | 0.40026 | 0.3881 | 0.37449 | 0.38886 | 0.37614 | 0.34508 | 0.31717 | 0.29195 | 0.27096 | 0.55324 | 10 | 0.95972 | Slope | 0.7 | 0.14343 |  | 0.29004 | 0 | 0.95972 | Slope | 2 | 0.7 | 0 | 20 | -20 | 0.00083392 | 0.00014978 | 0.0041776
341 | 0:57 | 14.3427 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 13.0921 | 0.13092 | 0.13092 | 14.3427 | 0.00062532 | [13 empty] | 0.95606 | 1 | 0.94748 | 0.87753 | 0.78629 | 0.68394 | 0.55368 | 0.39011 | 0.21905 | 0.068859 | -0.018918 | -0.055598 | -0.078691 | -0.080189 | -0.098338 | -0.093333 | -0.095653 | -0.1144 | -0.14483 | -0.16846 | -0.19328 | -0.22004 | -0.26456 | -0.32721 | -0.22062 | -0.10323 | 0.012028 | 0.12228 | 0.22736 | 0.31912 | 0.40355 | 0.006546 | -0.0077389 | -0.00038695 | -0.00038695 | 0 | 0 | 0.0039235 | 0.05 | -0.8466 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | -0.22087 | -0.23791 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.15378 | 0.2265 | 0.31429 | 0.40907 | 0.51017 | 0.59641 | 0.6942 | 0.79793 | 0.88753 | 0.95969 | 0.98877 | 0.94968 | 0.91343 | 0.88494 | 0.86797 | 0.86228 | 0.86077 | 0.86533 | 0.87345 | 0.88411 | 0.89523 | 0.9008 | 0.89768 | 0.89018 | 0.96661 | 0.96173 | 0.90186 | 0.85148 | 0.80916 | 0.77952 | 0.76247 | 0.98877 | 10 | Slope | 0.7 | 0.38459 | 0.40883 | 0.42699 | 0.44747 | 0.47006 | 0.48769 | 0.50918 | 0.53264 | 0.5514 | 0.56434 | 0.56292 | 0.53878 | 0.51559 | 0.49498 | 0.47821 | 0.4652 | 0.45359 | 0.444 | 0.43559 | 0.42804 | 0.42063 | 0.41138 | 0.39923 | 0.38562 | 0.39998 | 0.38724 | 0.35617 | 0.32827 | 0.30305 | 0.28206 | 0.26527 | 0.56434 | 9 | 0.95969 | Slope | 0.73333 | 0.13092 |  | 0.35194 | 0 | 0.95969 | Slope | 2 | 0.73333 | 0 | 20 | -20 | 0.00062532 | 0.00013605 | 0.0039235
342 | 0:57 | 13.0921 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 12.0623 | 0.12062 | 0.12062 | 13.0921 | 0.0005149 | [13 empty] | 0.94748 | 1 | 0.93828 | 0.85309 | 0.74891 | 0.62044 | 0.45746 | 0.2809 | 0.12099 | 0.0046739 | -0.06207 | -0.099397 | -0.1219 | -0.12109 | -0.13866 | -0.1338 | -0.13639 | -0.15764 | -0.1918 | -0.21973 | -0.25219 | -0.28845 | -0.34198 | -0.2265 | -0.1161 | 0.0017147 | 0.12059 | 0.23961 | 0.34151 | 0.42488 | 0.49602 | 0.0060311 | -0.0068609 | -0.00034305 | -0.00034305 | 0 | 0 | 0.003652 | 0.05 | -0.77389 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | -0.22087 | -0.23791 | -0.24253 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.22645 | 0.31425 | 0.40903 | 0.51013 | 0.59636 | 0.69416 | 0.79788 | 0.88749 | 0.95964 | 0.98881 | 0.94973 | 0.91348 | 0.88498 | 0.86801 | 0.86232 | 0.86081 | 0.86537 | 0.87349 | 0.88415 | 0.89528 | 0.90085 | 0.89773 | 0.89023 | 0.96666 | 0.96168 | 0.90181 | 0.85144 | 0.80912 | 0.77947 | 0.76243 | 0.75782 | 0.98881 | 9 | Slope | 0.73333 | 0.40882 | 0.43808 | 0.45856 | 0.48115 | 0.49879 | 0.52028 | 0.54374 | 0.5625 | 0.57544 | 0.57405 | 0.54991 | 0.52671 | 0.50611 | 0.48934 | 0.47633 | 0.46471 | 0.45512 | 0.44672 | 0.43916 | 0.43176 | 0.4225 | 0.41035 | 0.39674 | 0.41111 | 0.39834 | 0.36727 | 0.33937 | 0.31415 | 0.29316 | 0.27637 | 0.26372 | 0.57544 | 8 | 0.95964 | Slope | 0.76667 | 0.12062 |  | 0.40292 | 0 | 0.95964 | Slope | 2 | 0.76667 | 0 | 20 | -20 | 0.0005149 | 0.00012632 | 0.003652
343 | 0:57 | 12.0623 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 10.7266 | 0.10727 | 0.10727 | 12.0623 | 0.00066783 | [13 empty] | 0.93828 | 1 | 0.92604 | 0.82651 | 0.69866 | 0.53892 | 0.3613 | 0.19348 | 0.065737 | -0.032009 | -0.10251 | -0.14256 | -0.16769 | -0.16791 | -0.18882 | -0.18542 | -0.19065 | -0.21624 | -0.25622 | -0.29155 | -0.33286 | -0.37734 | -0.24606 | -0.12581 | -0.01363 | 0.11025 | 0.24152 | 0.3617 | 0.45875 | 0.53094 | 0.55535 | 0.0053633 | -0.0059132 | -0.00029566 | -0.00029566 | 0 | 0 | 0.003374 | 0.05 | -0.68609 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | -0.22087 | -0.23791 | -0.24253 | -0.23113 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.3142 | 0.40898 | 0.51008 | 0.59632 | 0.69411 | 0.79783 | 0.88744 | 0.9596 | 0.98886 | 0.94978 | 0.91353 | 0.88503 | 0.86806 | 0.86237 | 0.86086 | 0.86542 | 0.87354 | 0.8842 | 0.89532 | 0.9009 | 0.89777 | 0.89027 | 0.96671 | 0.96164 | 0.90177 | 0.85139 | 0.80907 | 0.77943 | 0.76238 | 0.75777 | 0.76917 | 0.98886 | 8 | Slope | 0.76667 | 0.43807 | 0.46966 | 0.49225 | 0.50988 | 0.53137 | 0.55483 | 0.57359 | 0.58653 | 0.58518 | 0.56104 | 0.53784 | 0.51723 | 0.50046 | 0.48746 | 0.47584 | 0.46625 | 0.45785 | 0.45029 | 0.44289 | 0.43363 | 0.42148 | 0.40787 | 0.42224 | 0.40943 | 0.37837 | 0.35046 | 0.32525 | 0.30425 | 0.28746 | 0.27481 | 0.2675 | 0.58653 | 7 | 0.9596 | Slope | 0.8 | 0.10727 |  | 0.46903 | 0 | 0.9596 | Slope | 2 | 0.8 | 0 | 20 | -20 | 0.00066783 | 0.00012221 | 0.003374
344 | 0:57 | 10.7266 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 9.6085 | 0.096085 | 0.096085 | 10.7266 | 0.00055907 | [13 empty] | 0.92604 | 1 | 0.91123 | 0.79383 | 0.63796 | 0.46256 | 0.29125 | 0.15294 | 0.041891 | -0.062918 | -0.14149 | -0.18992 | -0.22257 | -0.22643 | -0.25331 | -0.2536 | -0.26325 | -0.29477 | -0.34201 | -0.38448 | -0.4338 | -0.29284 | -0.15525 | -0.029736 | 0.090106 | 0.22968 | 0.36694 | 0.48754 | 0.5777 | 0.60258 | 0.58152 | 0.0048042 | -0.0049022 | -0.00024511 | -0.00024511 | 0 | 0 | 0.0031103 | 0.05 | -0.59132 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | -0.22087 | -0.23791 | -0.24253 | -0.23113 | -0.20284 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.40893 | 0.51003 | 0.59627 | 0.69406 | 0.79778 | 0.88739 | 0.95955 | 0.98891 | 0.94983 | 0.91358 | 0.88508 | 0.86811 | 0.86242 | 0.86091 | 0.86547 | 0.87359 | 0.88425 | 0.89538 | 0.90095 | 0.89782 | 0.89032 | 0.96676 | 0.96159 | 0.90172 | 0.85134 | 0.80902 | 0.77937 | 0.76233 | 0.75772 | 0.76912 | 0.79741 | 0.98891 | 7 | Slope | 0.8 | 0.46964 | 0.50334 | 0.52098 | 0.54247 | 0.56593 | 0.58469 | 0.59763 | 0.5963 | 0.57216 | 0.54897 | 0.52836 | 0.51159 | 0.49859 | 0.48697 | 0.47738 | 0.46898 | 0.46142 | 0.45401 | 0.44476 | 0.43261 | 0.419 | 0.43336 | 0.42053 | 0.38946 | 0.36156 | 0.33634 | 0.31535 | 0.29856 | 0.28591 | 0.2786 | 0.27691 | 0.59763 | 6 | 0.95955 | Slope | 0.83333 | 0.096085 |  | 0.52438 | 0 | 0.95955 | Slope | 2 | 0.83333 | 0 | 20 | -20 | 0.00055907 | 0.0001245 | 0.0031103
345 | 0:57 | 9.6085 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 8.2325 | 0.082325 | 0.082325 | 9.6085 | 0.00068799 | [13 empty] | 0.91123 | 1 | 0.88932 | 0.74099 | 0.56556 | 0.39277 | 0.24918 | 0.12714 | 0.0082677 | -0.10539 | -0.19252 | -0.24721 | -0.285 | -0.29109 | -0.32271 | -0.32579 | -0.33982 | -0.37991 | -0.43841 | -0.49058 | -0.34645 | -0.19594 | -0.052389 | 0.081176 | 0.21491 | 0.35921 | 0.49629 | 0.60936 | 0.65126 | 0.62805 | 0.58208 | 0.0041163 | -0.0040398 | -0.00020199 | -0.00020199 | 0 | 0 | 0.0028464 | 0.05 | -0.49022 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | -0.22087 | -0.23791 | -0.24253 | -0.23113 | -0.20284 | -0.16183 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.50999 | 0.59622 | 0.69402 | 0.79774 | 0.88735 | 0.9595 | 0.98895 | 0.94987 | 0.91362 | 0.88512 | 0.86815 | 0.86247 | 0.86095 | 0.86552 | 0.87364 | 0.8843 | 0.89542 | 0.90099 | 0.89787 | 0.89037 | 0.9668 | 0.96154 | 0.90167 | 0.8513 | 0.80898 | 0.77933 | 0.76229 | 0.75767 | 0.76908 | 0.79737 | 0.83837 | 0.98895 | 6 | Slope | 0.83333 | 0.50333 | 0.53207 | 0.55356 | 0.57702 | 0.59578 | 0.60872 | 0.60743 | 0.58329 | 0.5601 | 0.53949 | 0.52272 | 0.50971 | 0.4981 | 0.48851 | 0.4801 | 0.47254 | 0.46514 | 0.45589 | 0.44373 | 0.43012 | 0.44449 | 0.43163 | 0.40056 | 0.37265 | 0.34744 | 0.32644 | 0.30965 | 0.297 | 0.28969 | 0.28801 | 0.29057 | 0.60872 | 5 | 0.9595 | Slope | 0.86667 | 0.082325 |  | 0.59249 | 0 | 0.9595 | Slope | 2 | 0.86667 | 0 | 20 | -20 | 0.00068799 | 0.00013218 | 0.0028464
346 | 0:57 | 8.2325 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 7.3512 | 0.073512 | 0.073512 | 8.2325 | 0.00044064 | [13 empty] | 0.88932 | 1 | 0.86653 | 0.69913 | 0.52393 | 0.37593 | 0.24661 | 0.11469 | -0.018289 | -0.15065 | -0.25512 | -0.32011 | -0.36749 | -0.37933 | -0.41848 | -0.42646 | -0.44542 | -0.49197 | -0.56 | -0.42442 | -0.27159 | -0.10987 | 0.047308 | 0.20052 | 0.34385 | 0.49455 | 0.63146 | 0.69855 | 0.69467 | 0.65047 | 0.57591 | 0.0036756 | -0.0030618 | -0.00015309 | -0.00015309 | 0 | 0 | 0.0026115 | 0.05 | -0.40398 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | -0.22087 | -0.23791 | -0.24253 | -0.23113 | -0.20284 | -0.16183 | -0.10166 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.59617 | 0.69397 | 0.79769 | 0.8873 | 0.95945 | 0.989 | 0.94992 | 0.91367 | 0.88517 | 0.8682 | 0.86251 | 0.861 | 0.86556 | 0.87368 | 0.88434 | 0.89547 | 0.90104 | 0.89792 | 0.89041 | 0.96685 | 0.96149 | 0.90162 | 0.85125 | 0.80893 | 0.77928 | 0.76224 | 0.75763 | 0.76903 | 0.79732 | 0.83832 | 0.89849 | 0.989 | 5 | Slope | 0.86667 | 0.53206 | 0.56466 | 0.58812 | 0.60688 | 0.61982 | 0.61856 | 0.59442 | 0.57122 | 0.55061 | 0.53384 | 0.52084 | 0.50922 | 0.49963 | 0.49123 | 0.48367 | 0.47627 | 0.46701 | 0.45486 | 0.44125 | 0.45562 | 0.44272 | 0.41165 | 0.38375 | 0.35853 | 0.33754 | 0.32075 | 0.3081 | 0.30079 | 0.29911 | 0.30166 | 0.31061 | 0.61982 | 4 | 0.95945 | Slope | 0.9 | 0.073512 |  | 0.63611 | 0 | 0.95945 | Slope | 2 | 0.9 | 0 | 20 | -20 | 0.00044064 | 0.00014613 | 0.0026115
347 | 0:58 | 7.3512 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 4.6777 | 0.046777 | 0.046777 | 7.3512 | 0.0013368 | [13 empty] | 0.86653 | 1 | 0.84855 | 0.67985 | 0.52723 | 0.39256 | 0.25218 | 0.10269 | -0.055145 | -0.21414 | -0.33562 | -0.4156 | -0.47409 | -0.49336 | -0.54098 | -0.55239 | -0.57371 | -0.62775 | -0.50792 | -0.36548 | -0.19895 | -0.019319 | 0.16304 | 0.33176 | 0.485 | 0.64047 | 0.73222 | 0.75463 | 0.73321 | 0.66375 | 0.62396 | 0.0023389 | -0.0020246 | -0.00010123 | -0.00010123 | 0 | 0 | 0.0023994 | 0.05 | -0.30618 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | -0.22087 | -0.23791 | -0.24253 | -0.23113 | -0.20284 | -0.16183 | -0.10166 | -0.043042 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.69392 | 0.79764 | 0.88725 | 0.9594 | 0.98906 | 0.94997 | 0.91372 | 0.88522 | 0.86825 | 0.86257 | 0.86105 | 0.86562 | 0.87374 | 0.8844 | 0.89552 | 0.90109 | 0.89797 | 0.89047 | 0.9669 | 0.96144 | 0.90157 | 0.85119 | 0.80888 | 0.77923 | 0.76219 | 0.75757 | 0.76897 | 0.79727 | 0.83827 | 0.89844 | 0.95706 | 0.98906 | 4 | Slope | 0.9 | 0.56464 | 0.59921 | 0.61797 | 0.63091 | 0.62969 | 0.60555 | 0.58235 | 0.56174 | 0.54497 | 0.53197 | 0.52035 | 0.51076 | 0.50236 | 0.4948 | 0.4874 | 0.47814 | 0.46599 | 0.45238 | 0.46674 | 0.45381 | 0.42275 | 0.39484 | 0.36963 | 0.34863 | 0.33184 | 0.31919 | 0.31188 | 0.3102 | 0.31276 | 0.3217 | 0.33013 | 0.63091 | 3 | 0.9594 | Slope | 0.93333 | 0.046777 |  | 0.76845 | 0 | 0.9594 | Slope | 2 | 0.93333 | 0 | 20 | -20 | 0.0013368 | 0.00016328 | 0.0023994
348 | 0:58 | 4.6777 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 1.7176 | 0.017176 | 0.017176 | 4.6777 | 0.0014801 | [13 empty] | 0.84855 | 1 | 0.84202 | 0.68903 | 0.5483 | 0.40629 | 0.25197 | 0.080317 | -0.1026 | -0.27875 | -0.4167 | -0.50786 | -0.57523 | -0.60031 | -0.65235 | -0.6644 | -0.68945 | -0.59132 | -0.4678 | -0.31485 | -0.13334 | 0.069078 | 0.26777 | 0.4474 | 0.60456 | 0.72002 | 0.77441 | 0.78452 | 0.74503 | 0.70379 | 0.63236 | 0.0008588 | -0.0011285 | -5.6427e-05 | -5.6427e-05 | 0 | 0 | 0.0022714 | 0.05 | -0.20246 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | -0.22087 | -0.23791 | -0.24253 | -0.23113 | -0.20284 | -0.16183 | -0.10166 | -0.043042 | 0.043593 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.79759 | 0.8872 | 0.95936 | 0.9891 | 0.95002 | 0.91376 | 0.88527 | 0.8683 | 0.86261 | 0.8611 | 0.86566 | 0.87378 | 0.88444 | 0.89556 | 0.90113 | 0.89801 | 0.89051 | 0.96695 | 0.9614 | 0.90153 | 0.85115 | 0.80883 | 0.77919 | 0.76214 | 0.75753 | 0.76893 | 0.79722 | 0.83823 | 0.8984 | 0.95701 | 0.95635 | 0.9891 | 3 | Slope | 0.93333 | 0.5992 | 0.62907 | 0.64201 | 0.64081 | 0.61667 | 0.59348 | 0.57287 | 0.5561 | 0.54309 | 0.53148 | 0.52189 | 0.51348 | 0.50592 | 0.49852 | 0.48927 | 0.47712 | 0.4635 | 0.47787 | 0.46491 | 0.43384 | 0.40594 | 0.38072 | 0.35973 | 0.34294 | 0.33029 | 0.32298 | 0.3213 | 0.32385 | 0.3328 | 0.34123 | 0.32989 | 0.64201 | 2 | 0.95936 | Slope | 0.96667 | 0.017176 |  | 0.91498 | 0 | 0.95936 | Slope | 2 | 0.96667 | 0 | 20 | -20 | 0.0014801 | 0.00018106 | 0.0022714
349 | 0:58 | 1.7176 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -1.3531 | -0.013531 | -0.013531 | 1.7176 | 0.0015353 | [13 empty] | 0.84202 | 1 | 0.84711 | 0.70343 | 0.56007 | 0.4096 | 0.2388 | 0.047292 | -0.14738 | -0.33664 | -0.48328 | -0.58085 | -0.65287 | -0.67952 | -0.73172 | -0.74562 | -0.67075 | -0.57069 | -0.43972 | -0.27653 | -0.078513 | 0.13829 | 0.34743 | 0.53101 | 0.65539 | 0.74261 | 0.78945 | 0.78892 | 0.76679 | 0.70384 | 0.63209 | -0.00067653 | -0.00040699 | -2.035e-05 | -2.035e-05 | 0 | 0 | 0.0022263 | 0.05 | -0.11285 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | -0.22087 | -0.23791 | -0.24253 | -0.23113 | -0.20284 | -0.16183 | -0.10166 | -0.043042 | 0.043593 | 0.14056 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.88717 | 0.95932 | 0.98914 | 0.95005 | 0.9138 | 0.88531 | 0.86833 | 0.86265 | 0.86113 | 0.8657 | 0.87382 | 0.88448 | 0.8956 | 0.90117 | 0.89805 | 0.89055 | 0.96698 | 0.96136 | 0.90149 | 0.85111 | 0.80879 | 0.77915 | 0.76211 | 0.75749 | 0.76889 | 0.79719 | 0.83819 | 0.89836 | 0.95698 | 0.95639 | 0.85942 | 0.98914 | 2 | Slope | 0.96667 | 0.62906 | 0.65311 | 0.65193 | 0.62779 | 0.6046 | 0.58399 | 0.56722 | 0.55422 | 0.5426 | 0.53301 | 0.52461 | 0.51705 | 0.50964 | 0.50039 | 0.48824 | 0.47463 | 0.48899 | 0.47601 | 0.44494 | 0.41704 | 0.39182 | 0.37083 | 0.35404 | 0.34139 | 0.33408 | 0.3324 | 0.33495 | 0.3439 | 0.35233 | 0.34102 | 0.29758 | 0.65311 | 1 | 0.95932 | Slope | 1 | 0.013531 |  | 0.93302 | 0 | 0.95932 | Slope | 2 | 1 | 0 | 20 | -20 | 0.0015353 | 0.00019831 | 0.0022263
350 | 0:58 | -1.3531 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.9171 | -0.029171 | -0.029171 | -1.3531 | 0.00078205 | [13 empty] | 0.84711 | 1 | 0.85137 | 0.70878 | 0.56174 | 0.4003 | 0.21514 | 0.017251 | -0.18533 | -0.37847 | -0.52744 | -0.62632 | -0.69786 | -0.72299 | -0.77582 | -0.75138 | -0.67314 | -0.56645 | -0.42794 | -0.25382 | -0.043304 | 0.18357 | 0.39729 | 0.55903 | 0.66601 | 0.74931 | 0.79123 | 0.79288 | 0.75791 | 0.69969 | 0.63767 | -0.0014586 | 0.00010843 | 5.4217e-06 | 5.4217e-06 | 0 | 0 | 0.0022369 | 0.05 | -0.040699 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | -0.22087 | -0.23791 | -0.24253 | -0.23113 | -0.20284 | -0.16183 | -0.10166 | -0.043042 | 0.043593 | 0.14056 | 0.2303 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.9593 | 0.98916 | 0.95008 | 0.91383 | 0.88533 | 0.86836 | 0.86267 | 0.86116 | 0.86572 | 0.87384 | 0.8845 | 0.89563 | 0.9012 | 0.89807 | 0.89057 | 0.96701 | 0.96134 | 0.90147 | 0.85109 | 0.80877 | 0.77912 | 0.76208 | 0.75747 | 0.76887 | 0.79716 | 0.83816 | 0.89833 | 0.95695 | 0.95641 | 0.85944 | 0.76971 | 0.98916 | 1 | Slope | 1 | 0.6531 | 0.66305 | 0.63891 | 0.61572 | 0.59511 | 0.57834 | 0.56534 | 0.55372 | 0.54413 | 0.53573 | 0.52817 | 0.52076 | 0.51151 | 0.49936 | 0.48575 | 0.50011 | 0.48711 | 0.45604 | 0.42814 | 0.40292 | 0.38193 | 0.36514 | 0.35249 | 0.34518 | 0.3435 | 0.34605 | 0.355 | 0.36343 | 0.35214 | 0.3087 | 0.26768 | 0.66305 | 1 | 0.98916 | Slope | 1 | 0.029171 |  | 0.8556 | 0 | 0.98916 | Slope | 2 | 1 | 0 | 20 | -20 | 0.00078205 | 0.00021417 | 0.0022369
351 | 0:58 | -2.9171 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.9134 | -0.029134 | -0.029134 | -2.9171 | 1.895e-06 | [13 empty] | 0.85137 | 1 | 0.85375 | 0.70981 | 0.5546 | 0.38105 | 0.19107 | -0.013191 | -0.21805 | -0.4114 | -0.55946 | -0.65658 | -0.72602 | -0.75134 | -0.79804 | -0.76898 | -0.68393 | -0.57034 | -0.42318 | -0.23649 | -0.014608 | 0.21904 | 0.4188 | 0.5691 | 0.67396 | 0.75423 | 0.78864 | 0.78004 | 0.75006 | 0.702 | 0.64608 | -0.0014567 | 0.00049928 | 2.4964e-05 | 2.4964e-05 | 0 | 0 | 0.002259 | 0.05 | 0.010843 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | -0.22087 | -0.23791 | -0.24253 | -0.23113 | -0.20284 | -0.16183 | -0.10166 | -0.043042 | 0.043593 | 0.14056 | 0.2303 | 0.31123 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.98918 | 0.9501 | 0.91385 | 0.88535 | 0.86838 | 0.86269 | 0.86118 | 0.86574 | 0.87386 | 0.88452 | 0.89565 | 0.90122 | 0.89809 | 0.89059 | 0.96703 | 0.96132 | 0.90145 | 0.85107 | 0.80875 | 0.7791 | 0.76206 | 0.75745 | 0.76885 | 0.79714 | 0.83814 | 0.89832 | 0.95693 | 0.95643 | 0.85946 | 0.76973 | 0.6888 | 0.98918 | 0 | Slope | 1 | 0.66306 | 0.65003 | 0.62684 | 0.60623 | 0.58946 | 0.57645 | 0.56484 | 0.55525 | 0.54684 | 0.53929 | 0.53188 | 0.52263 | 0.51048 | 0.49686 | 0.51123 | 0.49822 | 0.46715 | 0.43925 | 0.41403 | 0.39303 | 0.37624 | 0.36359 | 0.35628 | 0.3546 | 0.35716 | 0.36611 | 0.37453 | 0.36325 | 0.31982 | 0.2788 | 0.24071 | 0.66306 | 0 | 0.98918 | Slope | 1 | 0.029134 |  | 0.85579 | 0 | 0.98918 | Slope | 2 | 1 | 0 | 20 | -20 | 1.895e-06 | 0.00022806 | 0.002259
352 | 0:58 | -2.9134 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.9096 | -0.029096 | -0.029096 | -2.9134 | 1.895e-06 | [13 empty] | 0.85375 | 1 | 0.85381 | 0.7033 | 0.53675 | 0.35816 | 0.16134 | -0.045758 | -0.25121 | -0.44314 | -0.58881 | -0.68412 | -0.75392 | -0.77281 | -0.81635 | -0.78193 | -0.69077 | -0.56984 | -0.41042 | -0.21159 | 0.019006 | 0.24174 | 0.43026 | 0.57768 | 0.67886 | 0.75013 | 0.77128 | 0.76575 | 0.74551 | 0.70446 | 0.65215 | -0.0014548 | 0.00086179 | 4.3089e-05 | 4.3089e-05 | 0 | 0 | 0.0022757 | 0.05 | 0.049928 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | -0.22087 | -0.23791 | -0.24253 | -0.23113 | -0.20284 | -0.16183 | -0.10166 | -0.043042 | 0.043593 | 0.14056 | 0.2303 | 0.31123 | 0.38496 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.95011 | 0.91386 | 0.88537 | 0.8684 | 0.86271 | 0.8612 | 0.86576 | 0.87388 | 0.88454 | 0.89566 | 0.90123 | 0.89811 | 0.89061 | 0.96704 | 0.9613 | 0.90143 | 0.85105 | 0.80873 | 0.77909 | 0.76204 | 0.75743 | 0.76883 | 0.79712 | 0.83813 | 0.8983 | 0.95692 | 0.95645 | 0.85948 | 0.76975 | 0.68881 | 0.61509 | 0.96704 | 13 | Slope | 0.6 | 0.65004 | 0.63795 | 0.61735 | 0.60058 | 0.58757 | 0.57595 | 0.56636 | 0.55796 | 0.5504 | 0.543 | 0.53374 | 0.52159 | 0.50798 | 0.52235 | 0.50932 | 0.47825 | 0.45035 | 0.42513 | 0.40414 | 0.38735 | 0.3747 | 0.36739 | 0.36571 | 0.36826 | 0.37721 | 0.38564 | 0.37437 | 0.33094 | 0.28992 | 0.25183 | 0.21614 | 0.65004 | 0 | 0.95011 | Slope | 1 | 0.029096 |  | 0.85598 | 0 | 0.95011 | Slope | 2 | 1 | 0 | 20 | -20 | 1.895e-06 | 0.00023918 | 0.0022757
353 | 0:59 | -2.9096 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.9058 | -0.029058 | -0.029058 | -2.9096 | 1.895e-06 | [13 empty] | 0.85381 | 1 | 0.85073 | 0.69158 | 0.52028 | 0.33522 | 0.13517 | -0.073081 | -0.27773 | -0.46815 | -0.61392 | -0.71077 | -0.77254 | -0.78696 | -0.82897 | -0.79114 | -0.69507 | -0.56394 | -0.39338 | -0.18545 | 0.037906 | 0.25015 | 0.4347 | 0.5758 | 0.66677 | 0.72036 | 0.74252 | 0.74781 | 0.73609 | 0.69976 | 0.65061 | -0.0014529 | 0.0011467 | 5.7337e-05 | 5.7337e-05 | 0 | 0 | 0.0022788 | 0.05 | 0.086179 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | -0.22087 | -0.23791 | -0.24253 | -0.23113 | -0.20284 | -0.16183 | -0.10166 | -0.043042 | 0.043593 | 0.14056 | 0.2303 | 0.31123 | 0.38496 | 0.45305 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.91388 | 0.88538 | 0.86841 | 0.86272 | 0.86121 | 0.86577 | 0.8739 | 0.88455 | 0.89568 | 0.90125 | 0.89813 | 0.89063 | 0.96706 | 0.96128 | 0.90141 | 0.85104 | 0.80872 | 0.77907 | 0.76203 | 0.75742 | 0.76882 | 0.79711 | 0.83811 | 0.89828 | 0.9569 | 0.95646 | 0.8595 | 0.76976 | 0.68883 | 0.6151 | 0.54701 | 0.96706 | 12 | Slope | 0.63333 | 0.63796 | 0.62846 | 0.61169 | 0.59869 | 0.58707 | 0.57748 | 0.56908 | 0.56152 | 0.55411 | 0.54486 | 0.53271 | 0.5191 | 0.53346 | 0.52043 | 0.48936 | 0.46146 | 0.43624 | 0.41525 | 0.39845 | 0.38581 | 0.37849 | 0.37681 | 0.37937 | 0.38832 | 0.39674 | 0.38549 | 0.34205 | 0.30103 | 0.26294 | 0.22726 | 0.19345 | 0.63796 | 0 | 0.91388 | Slope | 1 | 0.029058 |  | 0.85616 | 0 | 0.91388 | Slope | 2 | 1 | 0 | 20 | -20 | 1.895e-06 | 0.00024603 | 0.0022788
354 | 0:59 | -2.9058 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.902 | -0.02902 | -0.02902 | -2.9058 | 1.895e-06 | [13 empty] | 0.85073 | 1 | 0.84696 | 0.68445 | 0.50857 | 0.32097 | 0.11995 | -0.087806 | -0.29268 | -0.48619 | -0.63535 | -0.71847 | -0.77675 | -0.79203 | -0.83581 | -0.79797 | -0.69589 | -0.557 | -0.37942 | -0.17606 | 0.037046 | 0.24345 | 0.41786 | 0.54666 | 0.61579 | 0.66817 | 0.70294 | 0.71941 | 0.71394 | 0.68177 | 0.63491 | -0.001451 | 0.0013165 | 6.5823e-05 | 6.5823e-05 | 0 | 0 | 0.0022712 | 0.05 | 0.11467 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | -0.22087 | -0.23791 | -0.24253 | -0.23113 | -0.20284 | -0.16183 | -0.10166 | -0.043042 | 0.043593 | 0.14056 | 0.2303 | 0.31123 | 0.38496 | 0.45305 | 0.51813 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.88539 | 0.86842 | 0.86273 | 0.86122 | 0.86578 | 0.8739 | 0.88456 | 0.89569 | 0.90126 | 0.89813 | 0.89063 | 0.96707 | 0.96128 | 0.90141 | 0.85103 | 0.80871 | 0.77906 | 0.76202 | 0.75741 | 0.76881 | 0.7971 | 0.8381 | 0.89827 | 0.95689 | 0.95647 | 0.85951 | 0.76977 | 0.68884 | 0.61511 | 0.54702 | 0.48194 | 0.96707 | 11 | Slope | 0.66667 | 0.62846 | 0.62281 | 0.6098 | 0.59818 | 0.58859 | 0.58019 | 0.57263 | 0.56523 | 0.55597 | 0.54382 | 0.53021 | 0.54458 | 0.53154 | 0.50047 | 0.47256 | 0.44735 | 0.42635 | 0.40956 | 0.39691 | 0.3896 | 0.38792 | 0.39048 | 0.39942 | 0.40785 | 0.3966 | 0.35317 | 0.31214 | 0.27406 | 0.23837 | 0.20456 | 0.17176 | 0.62846 | 0 | 0.88539 | Slope | 1 | 0.02902 |  | 0.85635 | 0 | 0.88539 | Slope | 2 | 1 | 0 | 20 | -20 | 1.895e-06 | 0.00024827 | 0.0022712
355 | 0:59 | -2.902 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.8982 | -0.028982 | -0.028982 | -2.902 | 1.8951e-06 | [13 empty] | 0.84696 | 1 | 0.84592 | 0.68174 | 0.50507 | 0.31778 | 0.11796 | -0.090692 | -0.30049 | -0.49849 | -0.62544 | -0.70566 | -0.76948 | -0.78866 | -0.83856 | -0.80095 | -0.69574 | -0.55342 | -0.37945 | -0.18745 | 0.0171 | 0.20919 | 0.37094 | 0.47267 | 0.53898 | 0.60464 | 0.65243 | 0.67661 | 0.67613 | 0.64639 | 0.60233 | -0.0014491 | 0.0013733 | 6.8666e-05 | 6.8666e-05 | 0 | 0 | 0.0022654 | 0.05 | 0.13165 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | -0.22087 | -0.23791 | -0.24253 | -0.23113 | -0.20284 | -0.16183 | -0.10166 | -0.043042 | 0.043593 | 0.14056 | 0.2303 | 0.31123 | 0.38496 | 0.45305 | 0.51813 | 0.57649 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.86842 | 0.86274 | 0.86122 | 0.86579 | 0.87391 | 0.88457 | 0.89569 | 0.90126 | 0.89814 | 0.89064 | 0.96707 | 0.96127 | 0.9014 | 0.85102 | 0.80871 | 0.77906 | 0.76202 | 0.7574 | 0.7688 | 0.7971 | 0.8381 | 0.89827 | 0.95689 | 0.95648 | 0.85951 | 0.76977 | 0.68884 | 0.61511 | 0.54702 | 0.48194 | 0.42358 | 0.96707 | 10 | Slope | 0.7 | 0.62281 | 0.62091 | 0.6093 | 0.59971 | 0.5913 | 0.58374 | 0.57634 | 0.56709 | 0.55493 | 0.54132 | 0.55569 | 0.54265 | 0.51158 | 0.48367 | 0.45846 | 0.43746 | 0.42067 | 0.40802 | 0.40071 | 0.39903 | 0.40159 | 0.41053 | 0.41896 | 0.40771 | 0.36428 | 0.32326 | 0.28517 | 0.24948 | 0.21567 | 0.18287 | 0.1523 | 0.62281 | 0 | 0.86842 | Slope | 1 | 0.028982 |  | 0.85654 | 0 | 0.86842 | Slope | 2 | 1 | 0 | 20 | -20 | 1.8951e-06 | 0.00024698 | 0.0022654
356 | 0:59 | -2.8982 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.8944 | -0.028944 | -0.028944 | -2.8982 | 1.895e-06 | [13 empty] | 0.84592 | 1 | 0.84529 | 0.68089 | 0.50493 | 0.31914 | 0.11904 | -0.094054 | -0.30805 | -0.47449 | -0.60111 | -0.68901 | -0.75948 | -0.78531 | -0.84024 | -0.80268 | -0.6954 | -0.55579 | -0.39383 | -0.21111 | -0.021518 | 0.16263 | 0.29559 | 0.39089 | 0.46879 | 0.54607 | 0.60111 | 0.6301 | 0.63161 | 0.60446 | 0.56728 | -0.0014472 | 0.0013885 | 6.9423e-05 | 6.9423e-05 | 0 | 0 | 0.0022634 | 0.05 | 0.13733 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | -0.22087 | -0.23791 | -0.24253 | -0.23113 | -0.20284 | -0.16183 | -0.10166 | -0.043042 | 0.043593 | 0.14056 | 0.2303 | 0.31123 | 0.38496 | 0.45305 | 0.51813 | 0.57649 | 0.62301 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.86274 | 0.86122 | 0.86579 | 0.87391 | 0.88457 | 0.89569 | 0.90126 | 0.89814 | 0.89064 | 0.96707 | 0.96127 | 0.9014 | 0.85102 | 0.8087 | 0.77906 | 0.76202 | 0.7574 | 0.7688 | 0.7971 | 0.8381 | 0.89827 | 0.95689 | 0.95648 | 0.85951 | 0.76977 | 0.68884 | 0.61511 | 0.54702 | 0.48194 | 0.42358 | 0.37706 | 0.96707 | 9 | Slope | 0.73333 | 0.62091 | 0.62041 | 0.61082 | 0.60241 | 0.59486 | 0.58745 | 0.5782 | 0.56605 | 0.55243 | 0.5668 | 0.55376 | 0.52269 | 0.49479 | 0.46957 | 0.44858 | 0.43178 | 0.41913 | 0.41182 | 0.41014 | 0.4127 | 0.42165 | 0.43007 | 0.41883 | 0.37539 | 0.33437 | 0.29628 | 0.26059 | 0.22678 | 0.19398 | 0.16342 | 0.1368 | 0.62091 | 0 | 0.86274 | Slope | 1 | 0.028944 |  | 0.85673 | 0 | 0.86274 | Slope | 2 | 1 | 0 | 20 | -20 | 1.895e-06 | 0.00024373 | 0.0022634
357 | 0:59 | -2.8944 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.8906 | -0.028906 | -0.028906 | -2.8944 | 1.895e-06 | [13 empty] | 0.84529 | 1 | 0.84646 | 0.68386 | 0.51029 | 0.32482 | 0.12065 | -0.095905 | -0.2649 | -0.43337 | -0.57072 | -0.66747 | -0.74779 | -0.78096 | -0.84093 | -0.80448 | -0.69991 | -0.5736 | -0.42261 | -0.25661 | -0.070294 | 0.083101 | 0.20551 | 0.30973 | 0.39862 | 0.48264 | 0.54218 | 0.57271 | 0.57626 | 0.55604 | 0.53311 | -0.0014453 | 0.0013428 | 6.7141e-05 | 6.7141e-05 | 0 | 0 | 0.0022711 | 0.05 | 0.13885 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | -0.22087 | -0.23791 | -0.24253 | -0.23113 | -0.20284 | -0.16183 | -0.10166 | -0.043042 | 0.043593 | 0.14056 | 0.2303 | 0.31123 | 0.38496 | 0.45305 | 0.51813 | 0.57649 | 0.62301 | 0.65267 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.86122 | 0.86578 | 0.87391 | 0.88456 | 0.89569 | 0.90126 | 0.89814 | 0.89064 | 0.96707 | 0.96127 | 0.9014 | 0.85103 | 0.80871 | 0.77906 | 0.76202 | 0.75741 | 0.76881 | 0.7971 | 0.8381 | 0.89827 | 0.95689 | 0.95647 | 0.85951 | 0.76977 | 0.68884 | 0.61511 | 0.54702 | 0.48194 | 0.42358 | 0.37706 | 0.3474 | 0.96707 | 8 | Slope | 0.76667 | 0.62041 | 0.62193 | 0.61352 | 0.60597 | 0.59856 | 0.58931 | 0.57716 | 0.56355 | 0.57791 | 0.56487 | 0.5338 | 0.5059 | 0.48068 | 0.45969 | 0.4429 | 0.43025 | 0.42294 | 0.42125 | 0.42381 | 0.43276 | 0.44119 | 0.42994 | 0.3865 | 0.34548 | 0.30739 | 0.2717 | 0.2379 | 0.20509 | 0.17453 | 0.14791 | 0.12691 | 0.62193 | 1 | 0.86578 | Slope | 1 | 0.028906 |  | 0.85691 | 0 | 0.86578 | Slope | 2 | 1 | 0 | 20 | -20 | 1.895e-06 | 0.00023853 | 0.0022711
358 | 0:59 | -2.8906 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.8868 | -0.028868 | -0.028868 | -2.8906 | 1.895e-06 | [13 empty] | 0.84646 | 1 | 0.84882 | 0.6891 | 0.51657 | 0.32777 | 0.121 | -0.036837 | -0.20966 | -0.39095 | -0.5392 | -0.64724 | -0.73833 | -0.77857 | -0.84247 | -0.80872 | -0.7183 | -0.60368 | -0.46978 | -0.30028 | -0.14415 | -0.0050412 | 0.12211 | 0.23473 | 0.32966 | 0.41733 | 0.47766 | 0.50974 | 0.51971 | 0.51413 | 0.49847 | -0.0014434 | 0.0012616 | 6.3081e-05 | 6.3081e-05 | 0 | 0 | 0.0022871 | 0.05 | 0.13428 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | -0.22087 | -0.23791 | -0.24253 | -0.23113 | -0.20284 | -0.16183 | -0.10166 | -0.043042 | 0.043593 | 0.14056 | 0.2303 | 0.31123 | 0.38496 | 0.45305 | 0.51813 | 0.57649 | 0.62301 | 0.65267 | 0.67436 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.86578 | 0.8739 | 0.88456 | 0.89568 | 0.90125 | 0.89813 | 0.89063 | 0.96706 | 0.96128 | 0.90141 | 0.85103 | 0.80871 | 0.77907 | 0.76202 | 0.75741 | 0.76881 | 0.7971 | 0.83811 | 0.89828 | 0.9569 | 0.95647 | 0.8595 | 0.76977 | 0.68883 | 0.61511 | 0.54701 | 0.48194 | 0.42358 | 0.37705 | 0.3474 | 0.3257 | 0.96706 | 7 | Slope | 0.8 | 0.62193 | 0.62463 | 0.61708 | 0.60967 | 0.60042 | 0.58827 | 0.57465 | 0.58902 | 0.57598 | 0.54491 | 0.51701 | 0.49179 | 0.4708 | 0.45401 | 0.44136 | 0.43405 | 0.43237 | 0.43492 | 0.44387 | 0.4523 | 0.44105 | 0.39761 | 0.35659 | 0.3185 | 0.28281 | 0.249 | 0.2162 | 0.18564 | 0.15902 | 0.13802 | 0.11968 | 0.62463 | 1 | 0.8739 | Slope | 1 | 0.028868 |  | 0.8571 | 0 | 0.8739 | Slope | 2 | 1 | 0 | 20 | -20 | 1.895e-06 | 0.00023265 | 0.0022871
359 | 1:00 | -2.8868 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.883 | -0.02883 | -0.02883 | -2.8868 | 1.895e-06 | [13 empty] | 0.84882 | 1 | 0.852 | 0.69392 | 0.5188 | 0.32814 | 0.19381 | 0.030416 | -0.1562 | -0.34983 | -0.51075 | -0.63204 | -0.73312 | -0.77948 | -0.84641 | -0.82679 | -0.74843 | -0.65079 | -0.50635 | -0.36481 | -0.22541 | -0.085806 | 0.046499 | 0.16357 | 0.26163 | 0.34923 | 0.41057 | 0.4485 | 0.47263 | 0.4741 | 0.4685 | -0.0014415 | 0.001155 | 5.7751e-05 | 5.7751e-05 | 0 | 0 | 0.0023105 | 0.05 | 0.12616 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | -0.22087 | -0.23791 | -0.24253 | -0.23113 | -0.20284 | -0.16183 | -0.10166 | -0.043042 | 0.043593 | 0.14056 | 0.2303 | 0.31123 | 0.38496 | 0.45305 | 0.51813 | 0.57649 | 0.62301 | 0.65267 | 0.67436 | 0.68513 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.8739 | 0.88455 | 0.89568 | 0.90125 | 0.89813 | 0.89063 | 0.96706 | 0.96128 | 0.90141 | 0.85104 | 0.80872 | 0.77907 | 0.76203 | 0.75742 | 0.76882 | 0.79711 | 0.83811 | 0.89828 | 0.9569 | 0.95646 | 0.8595 | 0.76976 | 0.68883 | 0.6151 | 0.54701 | 0.48193 | 0.42357 | 0.37705 | 0.34739 | 0.32569 | 0.31492 | 0.96706 | 6 | Slope | 0.83333 | 0.62463 | 0.62818 | 0.62078 | 0.61153 | 0.59938 | 0.58576 | 0.60013 | 0.58709 | 0.55603 | 0.52812 | 0.50291 | 0.48191 | 0.46512 | 0.45247 | 0.44516 | 0.44348 | 0.44604 | 0.45498 | 0.46341 | 0.45215 | 0.40872 | 0.3677 | 0.32961 | 0.29392 | 0.26011 | 0.22731 | 0.19675 | 0.17013 | 0.14913 | 0.13079 | 0.11609 | 0.62818 | 1 | 0.88455 | Slope | 1 | 0.02883 |  | 0.85729 | 0 | 0.88455 | Slope | 2 | 1 | 0 | 20 | -20 | 1.895e-06 | 0.0002287 | 0.0023105
360 | 1:00 | -2.883 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.8792 | -0.028792 | -0.028792 | -2.883 | 1.895e-06 | [13 empty] | 0.852 | 1 | 0.85413 | 0.6942 | 0.51768 | 0.41184 | 0.26997 | 0.092198 | -0.10727 | -0.31423 | -0.49091 | -0.62442 | -0.73347 | -0.78489 | -0.86503 | -0.85632 | -0.79391 | -0.67825 | -0.55824 | -0.43409 | -0.29776 | -0.15639 | -0.021437 | 0.097676 | 0.19546 | 0.28379 | 0.35039 | 0.40154 | 0.43192 | 0.44323 | 0.44524 | -0.0014396 | 0.0010438 | 5.219e-05 | 5.219e-05 | 0 | 0 | 0.0023366 | 0.05 | 0.1155 | 0.10438 | 0.098809 | 0.10193 | 0.10943 | 0.032999 | -0.038659 | -0.098529 | -0.14891 | -0.19123 | -0.22087 | -0.23791 | -0.24253 | -0.23113 | -0.20284 | -0.16183 | -0.10166 | -0.043042 | 0.043593 | 0.14056 | 0.2303 | 0.31123 | 0.38496 | 0.45305 | 0.51813 | 0.57649 | 0.62301 | 0.65267 | 0.67436 | 0.68513 | 0.6877 | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope |  | 0.88455 | 0.89567 | 0.90124 | 0.89812 | 0.89062 | 0.96705 | 0.96129 | 0.90142 | 0.85104 | 0.80872 | 0.77908 | 0.76203 | 0.75742 | 0.76882 | 0.79711 | 0.83812 | 0.89829 | 0.95691 | 0.95646 | 0.85949 | 0.76975 | 0.68882 | 0.61509 | 0.547 | 0.48192 | 0.42356 | 0.37704 | 0.34739 | 0.32569 | 0.31492 | 0.31235 | 0.96705 | 5 | Slope | 0.86667 | 0.62818 | 0.63189 | 0.62264 | 0.61048 | 0.59687 | 0.61124 | 0.59821 | 0.56714 | 0.53924 | 0.51402 | 0.49303 | 0.47623 | 0.46358 | 0.45627 | 0.45459 | 0.45715 | 0.4661 | 0.47452 | 0.46326 | 0.41983 | 0.37881 | 0.34072 | 0.30503 | 0.27122 | 0.23842 | 0.20785 | 0.18124 | 0.16024 | 0.1419 | 0.12719 | 0.11523 | 0.63189 | 1 | 0.89567 | Slope | 1 | 0.028792 |  | 0.85748 | 0 | 0.89567 | Slope | 2 | 1 | 0 | 20 | -20 | 1.895e-06 | 0.00023508 | 0.0023366
361 | 1:00 | -2.8792 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.8755 | -0.028755 | -0.028755 | -2.8792 | [45 empty] | -0.0014377 | 0.00098809 | 4.9405e-05 | 4.9405e-05 | 0 | 0 | 0.0023489 | 0.05
362 | 1:00 | -2.8755 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.8717 | -0.028717 | -0.028717 | -2.8755 | [45 empty] | -0.0014358 | 0.0010193 | 6.6879e-05 | 6.6879e-05 | 0 | 0
363 | 1:00 | -2.8717 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -15.0425 | -0.15043 | -0.15043 | -2.8717 | [45 empty] | -0.0075213 | 0.0010943 | 8.7748e-05 | 8.7748e-05 | 0 | 0 | [63 empty] | 184 | 00:30:40 | 0.60757 | 0.5566 | 0.51734 | 0.49678 | 0.49836 | 0.52572 | 0.57307 | 0.63428 | 0.7092 | 0.79326 | 0.87638 | 0.95041 | 0.98054 | 0.91048 | 0.84289 | 0.78002 | 0.72183 | 0.66686 | 0.61474 | 0.56495 | 0.52367 | 0.4916 | 0.46435 | 0.44403 | 0.40197 | 0.38464 | 0.39522 | 0.43442 | 0.49558 | 0.56255 | 0.62925
364 | 1:00 | -15.0425 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -13.9436 | -0.13944 | -0.13944 | -15.0425 | [45 empty] | -0.0069718 | 0.00032999 | 6.4426e-05 | 6.4426e-05 | 0 | 0 | [65 empty] | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope | Slope
365 | 1:01 | -13.9436 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -13.0333 | -0.13033 | -0.13033 | -13.9436 | [45 empty] | -0.0065167 | -0.00038659 | 3.9668e-05 | 3.9668e-05 | 0 | 0 | [64 empty] | Correl | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
366 | 1:01 | -13.0333 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -12.3542 | -0.12354 | -0.12354 | -13.0333 | [45 empty] | -0.0061771 | -0.00098529 | 1.2575e-05 | 1.2575e-05 | 0 | 0 | [64 empty] | Slope | 0.60757 | 0.5566 | 0.51734 | 0.49678 | 0.49836 | 0.52572 | 0.57307 | 0.63428 | 0.7092 | 0.79326 | 0.87638 | 0.95041 | 0.98054 | 0.91048 | 0.84289 | 0.78002 | 0.72183 | 0.66686 | 0.61474 | 0.56495 | 0.52367 | 0.4916 | 0.46435 | 0.44403 | 0.40197 | 0.38464 | 0.39522 | 0.43442 | 0.49558 | 0.56255 | 0.62925
367 | 1:01 | -12.3542 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -11.9808 | -0.11981 | -0.11981 | -12.3542 | [45 empty] | -0.0059904 | -0.0014891 | -1.8292e-05 | -1.8292e-05 | 0 | 0
368 | 1:01 | -11.9808 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -11.1138 | -0.11114 | -0.11114 | -11.9808 | [45 empty] | -0.0055569 | -0.0019123 | -5.5319e-05 | -5.5319e-05 | 0 | 0
369 | 1:01 | -11.1138 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -10.2206 | -0.10221 | -0.10221 | -11.1138 | [45 empty] | -0.0051103 | -0.0022087 | -9.7087e-05 | -9.7087e-05 | 0 | 0
370 | 1:01 | -10.2206 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -9.3184 | -0.093184 | -0.093184 | -10.2206 | [45 empty] | -0.0046592 | -0.0023791 | -0.00014427 | -0.00014427 | 0 | 0
371 | 1:02 | -9.3184 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -6.8888 | -0.068888 | -0.068888 | -9.3184 | [45 empty] | -0.0034444 | -0.0024253 | -0.00019778 | -0.00019778 | 0 | 0
372 | 1:02 | -6.8888 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.4762 | -0.044762 | -0.044762 | -6.8888 | [45 empty] | -0.0022381 | -0.0023113 | -0.00024672 | -0.00024672 | 0 | 0
373 | 1:02 | -4.4762 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -3.3951 | -0.033951 | -0.033951 | -4.4762 | [45 empty] | -0.0016975 | -0.0020284 | -0.00028735 | -0.00028735 | 0 | 0
374 | 1:02 | -3.3951 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -1.9554 | -0.019554 | -0.019554 | -3.3951 | [45 empty] | -0.00097771 | -0.0016183 | -0.00032688 | -0.00032688 | 0 | 0
375 | 1:02 | -1.9554 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.0655 | -0.040655 | -0.040655 | -1.9554 | [45 empty] | -0.0020328 | -0.0010166 | -0.00035901 | -0.00035901 | 0 | 0
376 | 1:03 | -4.0655 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -1.5983 | -0.015983 | -0.015983 | -4.0655 | [45 empty] | -0.00079914 | -0.00043042 | -0.00042221 | -0.00042221 | 0 | 0
377 | 1:03 | -1.5983 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -0.33417 | -0.0033417 | -0.0033417 | -1.5983 | [45 empty] | -0.00016709 | 0.00043593 | -0.00046698 | -0.00046698 | 0 | 0
378 | 1:03 | -0.33417 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -0.32809 | -0.0032809 | -0.0032809 | -0.33417 | [45 empty] | -0.00016405 | 0.0014056 | -0.00049766 | -0.00049766 | 0 | 0
379 | 1:03 | -0.32809 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -0.39 | -0.0039 | -0.0039 | -0.32809 | [45 empty] | -0.000195 | 0.002303 | -0.00052561 | -0.00052561 | 0 | 0
380 | 1:03 | -0.39 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -0.66294 | -0.0066294 | -0.0066294 | -0.39 | [45 empty] | -0.00033147 | 0.0031123 | -0.00054758 | -0.00054758 | 0 | 0
381 | 1:03 | -0.66294 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -1.0083 | -0.010083 | -0.010083 | -0.66294 | [45 empty] | -0.00050415 | 0.0038496 | -0.00056151 | -0.00056151 | 0 | 0
382 | 1:04 | -1.0083 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -1.3536 | -0.013536 | -0.013536 | -1.0083 | [45 empty] | -0.00067682 | 0.0045305 | -0.00055973 | -0.00055973 | 0 | 0
383 | 1:04 | -1.3536 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.536 | -0.02536 | -0.02536 | -1.3536 | [45 empty] | -0.001268 | 0.0051813 | -0.00052422 | -0.00052422 | 0 | 0
384 | 1:04 | -2.536 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.4202 | -0.044202 | -0.044202 | -2.536 | [45 empty] | -0.0022101 | 0.0057649 | -0.00046164 | -0.00046164 | 0 | 0
385 | 1:04 | -4.4202 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -6.3912 | -0.063912 | -0.063912 | -4.4202 | [45 empty] | -0.0031956 | 0.0062301 | -0.00039619 | -0.00039619 | 0 | 0
386 | 1:04 | -6.3912 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.3178 | -0.073178 | -0.073178 | -6.3912 | [45 empty] | -0.0036589 | 0.0065267 | -0.00035694 | -0.00035694 | 0 | 0
387 | 1:04 | -7.3178 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -8.6211 | -0.086211 | -0.086211 | -7.3178 | [45 empty] | -0.0043105 | 0.0067436 | -0.00027897 | -0.00027897 | 0 | 0
388 | 1:05 | -8.6211 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -9.595 | -0.09595 | -0.09595 | -8.6211 | [45 empty] | -0.0047975 | 0.0068513 | -0.00019241 | -0.00019241 | 0 | 0
389 | 1:05 | -9.595 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -10.4658 | -0.10466 | -0.10466 | -9.595 | [45 empty] | -0.0052329 | 0.006877 | -5.4156e-05 | -5.4156e-05 | 0 | 0
390 | 1:05 | -10.4658 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -11.0518 | -0.11052 | -0.11052 | -10.4658 | [45 empty] | -0.0055259 | 0.0068253 | 0.0001847 | 0.0001847 | 0 | 0
391 | 1:05 | -11.0518 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -10.6824 | -0.10682 | -0.10682 | -11.0518 | [45 empty] | -0.0053412 | 0.0067085 | #DIV/0! | #DIV/0! | 0 | 0
392 | 1:05 | -10.6824 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -9.7695 | -0.097695 | -0.097695 | -10.6824
393 | 1:05 | -9.7695 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -9.5091 | -0.095091 | -0.095091 | -9.7695
394 | 1:06 | -9.5091 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -10.8465 | -0.10847 | -0.10847 | -9.5091
395 | 1:06 | -10.8465 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -10.9493 | -0.10949 | -0.10949 | -10.8465
396 | 1:06 | -10.9493 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -9.7718 | -0.097718 | -0.097718 | -10.9493
397 | 1:06 | -9.7718 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -8.7094 | -0.087094 | -0.087094 | -9.7718
398 | 1:06 | -8.7094 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -7.5324 | -0.075324 | -0.075324 | -8.7094
399 | 1:06 | -7.5324 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -6.0651 | -0.060651 | -0.060651 | -7.5324
400 | 1:07 | -6.0651 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -4.5978 | -0.045978 | -0.045978 | -6.0651
401 | 1:07 | -4.5978 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -3.1304 | -0.031304 | -0.031304 | -4.5978
402 | 1:07 | -3.1304 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.6617 | -0.026617 | -0.026617 | -3.1304
403 | 1:07 | -2.6617 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -2.1606 | -0.021606 | -0.021606 | -2.6617
404 | 1:07 | -2.1606 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | -1.0576 | -0.010576 | -0.010576 | -2.1606
405 | 1:07 | -1.0576 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 0.73137 | 0.0073137 | 0.0073137 | -1.0576
406 | 1:08 | 0.73137 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 2.9046 | 0.029046 | 0.029046 | 0.73137
407 | 1:08 | 2.9046 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 5.3697 | 0.053697 | 0.053697 | 2.9046
408 | 1:08 | 5.3697 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 6.1941 | 0.061941 | 0.061941 | 5.3697
409 | 1:08 | 6.1941 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 5.4275 | 0.054275 | 0.054275 | 6.1941
410 | 1:08 | 5.4275 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 4.4213 | 0.044213 | 0.044213 | 5.4275
411 | 1:08 | 4.4213 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.8423 | 0.038423 | 0.038423 | 4.4213
412 | 1:09 | 3.8423 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.579 | 0.03579 | 0.03579 | 3.8423
413 | 1:09 | 3.579 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 3.7553 | 0.037553 | 0.037553 | 3.579
414 | 1:09 | 3.7553 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 4.246 | 0.04246 | 0.04246 | 3.7553
415 | 1:09 | 4.246 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 4.7508 | 0.047508 | 0.047508 | 4.246
416 | 1:09 | 4.7508 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 4.6763 | 0.046763 | 0.046763 | 4.7508
417 | 1:09 | 4.6763 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 5.0867 | 0.050867 | 0.050867 | 4.6763
418 | 1:10 | 5.0867 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 5.497 | 0.05497 | 0.05497 | 5.0867
419 | 1:10 | 5.497 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 6.1202 | 0.061202 | 0.061202 | 5.497
420 | 1:10 | 6.1202 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 6.819 | 0.06819 | 0.06819 | 6.1202
421 | 1:10 | 6.819 | 0 | 999999 | 166666.5 | 0 | 20 | 2000 | 7.5179 | 0.075179 | 0.075179 | 6.819
|  | 7.5179 | [5 empty] | 2000 | 7.0368
|  | 7.0368 | [5 empty] | 2000 | 5.4049
|  | 5.4049 | [5 empty] | 2000 | 5.0209
|  | 5.0209 | [5 empty] | 2000 | 5.2346
|  | 5.2346 | [5 empty] | 2000 | 5.5583
|  | 5.5583 | [5 empty] | 2000 | 5.6493
|  | 5.6493 | [5 empty] | 2000 | 5.284
|  | 5.284 | [5 empty] | 2000 | 4.9188
|  | 4.9188 | [5 empty] | 2000 | 4.1196
|  | 4.1196 | [5 empty] | 2000 | 2.914
|  | 2.914 | [5 empty] | 2000 | 1.3524
|  | 1.3524 | [5 empty] | 2000 | 0.37752
|  | 0.37752 | [5 empty] | 2000 | -0.38917
|  | -0.38917 | [5 empty] | 2000 | -1.5125
|  | -1.5125 | [5 empty] | 2000 | -2.7616
|  | -2.7616 | [5 empty] | 2000 | -4.0886
|  | -4.0886 | [5 empty] | 2000 | -5.8789
|  | -5.8789 | [5 empty] | 2000 | -7.8942
|  | -7.8942 | [5 empty] | 2000 | -9.1666
|  | -9.1666 | [5 empty] | 2000 | -9.6274
|  | -9.6274 | [5 empty] | 2000 | -8.6029
|  | -8.6029 | [5 empty] | 2000 | -7.0786
|  | -7.0786 | [5 empty] | 2000 | -5.945
|  | -5.945 | [5 empty] | 2000 | -5.1691
|  | -5.1691 | [5 empty] | 2000 | -4.377
|  | -4.377 | [5 empty] | 2000 | -3.4129
|  | -3.4129 | [5 empty] | 2000 | -1.5814
|  | -1.5814 | [5 empty] | 2000 | -1.3524
|  | -1.3524 | [5 empty] | 2000 | -1.9944
|  | -1.9944 | [5 empty] | 2000 | -1.581
|  | -1.581 | [5 empty] | 2000 | -0.63566
|  | -0.63566 | [5 empty] | 2000 | -0.73259
|  | -0.73259 | [5 empty] | 2000 | -0.82951
|  | -0.82951 | [5 empty] | 2000 | -0.046031
|  | -0.046031 | [5 empty] | 2000 | -0.21482
|  | -0.21482 | [5 empty] | 2000 | -0.14768
|  | -0.14768 | [5 empty] | 2000 | 0.089413
|  | 0.089413 | [5 empty] | 2000 | 1.5881
|  | 1.5881 | [5 empty] | 2000 | 1.7688
|  | 1.7688 | [5 empty] | 2000 | 2.1627
|  | 2.1627 | [5 empty] | 2000 | 2.9334
|  | 2.9334 | [5 empty] | 2000 | 2.907
|  | 2.907 | [5 empty] | 2000 | 3.9455
|  | 3.9455 | [5 empty] | 2000 | 4.9528
|  | 4.9528 | [5 empty] | 2000 | 6.828
|  | 6.828 | [5 empty] | 2000 | 8.0476
|  | 8.0476 | [5 empty] | 2000 | 8.6541
|  | 8.6541 | [5 empty] | 2000 | 8.546
|  | 8.546 | [5 empty] | 2000 | 7.9177
|  | 7.9177 | [5 empty] | 2000 | 7.1957
|  | 7.1957 | [5 empty] | 2000 | 6.4691
|  | 6.4691 | [5 empty] | 2000 | 5.7386
|  | 5.7386 | [5 empty] | 2000 | 4.4664
|  | 4.4664 | [5 empty] | 2000 | 3.4415
|  | 3.4415 | [5 empty] | 2000 | 2.9061
|  | 2.9061 | [5 empty] | 2000 | 2.3137
|  | 2.3137 | [5 empty] | 2000 | 2.809
|  | 2.809 | [5 empty] | 2000 | 3.9174
|  | 3.9174 | [5 empty] | 2000 | 4.4385
|  | 4.4385 | [5 empty] | 2000 | 4.4707
|  | 4.4707 | [5 empty] | 2000 | 4.4707
|  | 4.4707 | [5 empty] | 2000 | 4.4707
|  | 4.4707 | [5 empty] | 2000 | 4.4707
|  | 4.4707 | [5 empty] | 2000 | 4.4707
|  | 4.4707 | [5 empty] | 2000 | 4.4707
|  | 4.4707 | [5 empty] | 2000 | 4.4707
|  | 4.4707 | [5 empty] | 2000 | 4.4707
|  | 4.4707 | [5 empty] | 2000 | 4.4707
|  | 4.4707 | [5 empty] | 2000 | 4.4707
|  | 4.4707 | [5 empty] | 2000 | 4.4707
|  | 4.4707 | [5 empty] | 2000 | -13.4053
|  | -13.4053 | [5 empty] | 2000 | -13.2539
|  | -13.2539 | [5 empty] | 2000 | -12.7756
|  | -12.7756 | [5 empty] | 2000 | -12.2861
|  | -12.2861 | [5 empty] | 2000 | -12.4524
|  | -12.4524 | [5 empty] | 2000 | -11.3503
|  | -11.3503 | [5 empty] | 2000 | -10.164
|  | -10.164 | [5 empty] | 2000 | -8.898
|  | -8.898 | [5 empty] | 2000 | -8.0352
|  | -8.0352 | [5 empty] | 2000 | -7.3251
|  | -7.3251 | [5 empty] | 2000 | -6.7286
|  | -6.7286 | [5 empty] | 2000 | -6.0755
|  | -6.0755 | [5 empty] | 2000 | -4.538
|  | -4.538 | [5 empty] | 2000 | -3.4367
|  | -3.4367 | [5 empty] | 2000 | -2.2049
|  | -2.2049 | [5 empty] | 2000 | -0.7172
|  | -0.7172 | [5 empty] | 2000 | 0.77047
|  | 0.77047 | [5 empty] | 2000 | 1.9986
|  | 1.9986 | [5 empty] | 2000 | 2.6478
|  | 2.6478 | [5 empty] | 2000 | 2.8797
|  | 2.8797 | [5 empty] | 2000 | 3.3077
|  | 3.3077 | [5 empty] | 2000 | 3.7488
|  | 3.7488 | [5 empty] | 2000 | 3.2966
|  | 3.2966 | [5 empty] | 2000 | 2.7844
|  | 2.7844 | [5 empty] | 2000 | 1.4065
|  | 1.4065 | [5 empty] | 2000 | 0.64063
|  | 0.64063 | [5 empty] | 2000 | 1.0799
|  | 1.0799 | [5 empty] | 2000 | 2.7251
|  | 2.7251 | [5 empty] | 2000 | 3.8038
|  | 3.8038 | [5 empty] | 2000 | 4.96
|  | 4.96 | [5 empty] | 2000 | 5.4748
|  | 5.4748 | [5 empty] | 2000 | 5.8891
|  | 5.8891 | [5 empty] | 2000 | 7.455
|  | 7.455 | [5 empty] | 2000 | 9.5667
|  | 9.5667 | [5 empty] | 2000 | 11.8729
|  | 11.8729 | [5 empty] | 2000 | 14.1792
|  | 14.1792 | [5 empty] | 2000 | 15.5261
|  | 15.5261 | [5 empty] | 2000 | 15.6372
|  | 15.6372 | [5 empty] | 2000 | 15.5621
|  | 15.5621 | [5 empty] | 2000 | 15.5543
|  | 15.5543 | [5 empty] | 2000 | 15.1425
|  | 15.1425 | [5 empty] | 2000 | 15.4938
|  | 15.4938 | [5 empty] | 2000 | 15.6899
|  | 15.6899 | [5 empty] | 2000 | 15.2896
|  | 15.2896 | [5 empty] | 2000 | 14.4242
|  | 14.4242 | [5 empty] | 2000 | 12.8945
|  | 12.8945 | [5 empty] | 2000 | 10.7943
|  | 10.7943 | [5 empty] | 2000 | 9.5799
|  | 9.5799 | [5 empty] | 2000 | 8.5836
|  | 8.5836 | [5 empty] | 2000 | 7.0957
|  | 7.0957 | [5 empty] | 2000 | 5.5914
|  | 5.5914 | [5 empty] | 2000 | 3.7601
|  | 3.7601 | [5 empty] | 2000 | 0.48622
|  | 0.48622 | [5 empty] | 2000 | -3.2844
|  | -3.2844 | [5 empty] | 2000 | -4.8491
|  | -4.8491 | [5 empty] | 2000 | -5.5748
|  | -5.5748 | [5 empty] | 2000 | -5.9459
|  | -5.9459 | [5 empty] | 2000 | -6.1345
|  | -6.1345 | [5 empty] | 2000 | -6.1137
|  | -6.1137 | [5 empty] | 2000 | -7.0196
|  | -7.0196 | [5 empty] | 2000 | -7.9256
|  | -7.9256 | [5 empty] | 2000 | -8.4312
|  | -8.4312 | [5 empty] | 2000 | -7.7451
|  | -7.7451 | [5 empty] | 2000 | -6.609
|  | -6.609 | [5 empty] | 2000 | -5.3857
|  | -5.3857 | [5 empty] | 2000 | -3.9937
|  | -3.9937 | [5 empty] | 2000 | -3.1734
|  | -3.1734 | [5 empty] | 2000 | -3.9216
|  | -3.9216 | [5 empty] | 2000 | -4.8072
|  | -4.8072 | [5 empty] | 2000 | -5.2444
|  | -5.2444 | [5 empty] | 2000 | -5.6156
|  | -5.6156 | [5 empty] | 2000 | -5.7169
|  | -5.7169 | [5 empty] | 2000 | -4.775
|  | -4.775 | [5 empty] | 2000 | -3.5311
|  | -3.5311 | [5 empty] | 2000 | -1.7623
|  | -1.7623 | [5 empty] | 2000 | -0.12349
|  | -0.12349 | [5 empty] | 2000 | 0.95962
|  | 0.95962 | [5 empty] | 2000 | 1.5011
|  | 1.5011 | [5 empty] | 2000 | 2.3924
|  | 2.3924 | [5 empty] | 2000 | 3.2414
|  | 3.2414 | [5 empty] | 2000 | 4.8505
|  | 4.8505 | [5 empty] | 2000 | 6.1373
|  | 6.1373 | [5 empty] | 2000 | 6.4019
|  | 6.4019 | [5 empty] | 2000 | 6.7333
|  | 6.7333 | [5 empty] | 2000 | 7.1309
|  | 7.1309 | [5 empty] | 2000 | 7.0343
|  | 7.0343 | [5 empty] | 2000 | 7.4699
|  | 7.4699 | [5 empty] | 2000 | 7.9054
|  | 7.9054 | [5 empty] | 2000 | 8.2454
|  | 8.2454 | [5 empty] | 2000 | 7.8315
|  | 7.8315 | [5 empty] | 2000 | 6.4373
|  | 6.4373 | [5 empty] | 2000 | 4.9401
|  | 4.9401 | [5 empty] | 2000 | 3.4535
|  | 3.4535 | [5 empty] | 2000 | 2.2203
|  | 2.2203 | [5 empty] | 2000 | 0.98717
|  | 0.98717 | [5 empty] | 2000 | -0.09493
|  | -0.09493 | [5 empty] | 2000 | -0.94842
|  | -0.94842 | [5 empty] | 2000 | -1.6099
|  | -1.6099 | [5 empty] | 2000 | -3.2664
|  | -3.2664 | [5 empty] | 2000 | -4.605
|  | -4.605 | [5 empty] | 2000 | -5.8456
|  | -5.8456 | [5 empty] | 2000 | -6.2089
|  | -6.2089 | [5 empty] | 2000 | -6.5223
|  | -6.5223 | [5 empty] | 2000 | -6.7916
|  | -6.7916 | [5 empty] | 2000 | -6.6266
|  | -6.6266 | [5 empty] | 2000 | -6.08
|  | -6.08 | [5 empty] | 2000 | -6.1863
|  | -6.1863 | [5 empty] | 2000 | -7.2112
|  | -7.2112 | [5 empty] | 2000 | -9.3418
|  | -9.3418 | [5 empty] | 2000 | -10.9045
|  | -10.9045 | [5 empty] | 2000 | -11.6384
|  | -11.6384 | [5 empty] | 2000 | -12.001
|  | -12.001 | [5 empty] | 2000 | -13.249
|  | -13.249 | [5 empty] | 2000 | -13.1412
|  | -13.1412 | [5 empty] | 2000 | -12.932
|  | -12.932 | [5 empty] | 2000 | -10.9618
|  | -10.9618 | [5 empty] | 2000 | -8.7326
|  | -8.7326 | [5 empty] | 2000 | -6.5808
|  | -6.5808 | [5 empty] | 2000 | -4.1991
|  | -4.1991 | [5 empty] | 2000 | -2.1178
|  | -2.1178 | [5 empty] | 2000 | 0.54137
|  | 0.54137 | [5 empty] | 2000 | 2.9912
|  | 2.9912 | [5 empty] | 2000 | 4.5397
|  | 4.5397 | [5 empty] | 2000 | 6.9369
|  | 6.9369 | [5 empty] | 2000 | 8.6116
|  | 8.6116 | [5 empty] | 2000 | 8.7262
|  | 8.7262 | [5 empty] | 2000 | 8.8408
|  | 8.8408 | [5 empty] | 2000 | 9.3511
|  | 9.3511 | [5 empty] | 2000 | 10.0068
|  | 10.0068 | [5 empty] | 2000 | 10.5822
|  | 10.5822 | [5 empty] | 2000 | 10.2537
|  | 10.2537 | [5 empty] | 2000 | 10.2596
|  | 10.2596 | [5 empty] | 2000 | 10.3498
|  | 10.3498 | [5 empty] | 2000 | 10.0248
|  | 10.0248 | [5 empty] | 2000 | 9.539
|  | 9.539 | [5 empty] | 2000 | 7.9964
|  | 7.9964 | [5 empty] | 2000 | 6.3095
|  | 6.3095 | [5 empty] | 2000 | 4.3328
|  | 4.3328 | [5 empty] | 2000 | 2.417
|  | 2.417 | [5 empty] | 2000 | 0.49836
|  | 0.49836 | [5 empty] | 2000 | -1.23
|  | -1.23 | [5 empty] | 2000 | -2.7462
|  | -2.7462 | [5 empty] | 2000 | -2.6746
|  | -2.6746 | [5 empty] | 2000 | -2.4865
|  | -2.4865 | [5 empty] | 2000 | -2.2985
|  | -2.2985 | [5 empty] | 2000 | -2.1104
|  | -2.1104 | [5 empty] | 2000 | -1.9223
|  | -1.9223 | [5 empty] | 2000 | -1.1284
|  | -1.1284 | [5 empty] | 2000 | -1.4766
|  | -1.4766 | [5 empty] | 2000 | -1.9126
|  | -1.9126 | [5 empty] | 2000 | -2.4262
|  | -2.4262 | [5 empty] | 2000 | -3.0959
|  | -3.0959 | [5 empty] | 2000 | -2.9703
|  | -2.9703 | [5 empty] | 2000 | -2.8695
|  | -2.8695 | [5 empty] | 2000 | -3.4787
|  | -3.4787 | [5 empty] | 2000 | -4.5659
|  | -4.5659 | [5 empty] | 2000 | -5.8184
|  | -5.8184 | [5 empty] | 2000 | -6.517
|  | -6.517 | [5 empty] | 2000 | -5.7985
|  | -5.7985 | [5 empty] | 2000 | -5.0324
|  | -5.0324 | [5 empty] | 2000 | -4.6545
|  | -4.6545 | [5 empty] | 2000 | -4.6191
|  | -4.6191 | [5 empty] | 2000 | -4.5836
|  | -4.5836 | [5 empty] | 2000 | -6.06
|  | -6.06 | [5 empty] | 2000 | -5.7011
|  | -5.7011 | [5 empty] | 2000 | -3.942
|  | -3.942 | [5 empty] | 2000 | -1.9441
|  | -1.9441 | [5 empty] | 2000 | -1.0107
|  | -1.0107 | [5 empty] | 2000 | 0.22738
|  | 0.22738 | [5 empty] | 2000 | 2.1895
|  | 2.1895 | [5 empty] | 2000 | 3.3621
|  | 3.3621 | [5 empty] | 2000 | 3.9614
|  | 3.9614 | [5 empty] | 2000 | 4.0853
|  | 4.0853 | [5 empty] | 2000 | 4.1641
|  | 4.1641 | [5 empty] | 2000 | 5.1052
|  | 5.1052 | [5 empty] | 2000 | 5.3846
|  | 5.3846 | [5 empty] | 2000 | 6.863
|  | 6.863 | [5 empty] | 2000 | 9.6428
|  | 9.6428 | [5 empty] | 2000 | 11.7662
|  | 11.7662 | [5 empty] | 2000 | 12.9489
|  | 12.9489 | [5 empty] | 2000 | 14.0675
|  | 14.0675 | [5 empty] | 2000 | 15.0898
|  | 15.0898 | [5 empty] | 2000 | 12.4005
|  | 12.4005 | [5 empty] | 2000 | 10.1368
|  | 10.1368 | [5 empty] | 2000 | 8.7103
|  | 8.7103 | [5 empty] | 2000 | 8.3955
|  | 8.3955 | [5 empty] | 2000 | 8.1128
|  | 8.1128 | [5 empty] | 2000 | 7.2117
|  | 7.2117 | [5 empty] | 2000 | 5.4868
|  | 5.4868 | [5 empty] | 2000 | 2.3486
|  | 2.3486 | [5 empty] | 2000 | -0.15587
|  | -0.15587 | [5 empty] | 2000 | -2.0978
|  | -2.0978 | [5 empty] | 2000 | -2.9575
|  | -2.9575 | [5 empty] | 2000 | -3.6404
|  | -3.6404 | [5 empty] | 2000 | -3.6845
|  | -3.6845 | [5 empty] | 2000 | -3.7287
|  | -3.7287 | [5 empty] | 2000 | -3.9987
|  | -3.9987 | [5 empty] | 2000 | -5.1626
|  | -5.1626 | [5 empty] | 2000 | -6.4866
|  | -6.4866 | [5 empty] | 2000 | -7.4264
|  | -7.4264 | [5 empty] | 2000
Used Load BP
Note on N3: This is the average delay of the resource relative to the signal, based on the Accuracy Score Method
Note on N4: Based on the Precision Score Method, this is the Denominator that is used to calculate the Precision scores
Note on N5: This is the actual Mileage generated by the regulation signal in this hour
Note on C8: This quantity is the resource (net) output/consumption, as telemetered to PJM
Note on D8: This is the economic basepoint / non-regulation setpoint
Note on E8: This is the economic ramp rate limit of the resource, as submitted to eMKT
Note on H8: This is the regulation assignment, in MW
Note on I8: This is the fleet TREG, as telemetered to PJM
Note on J8: This is the regulation signal, as sent from PJM, calculated by the EMS

## Data
RawUnitReg | Unit Response | Corr | M
0.0065 | 1.3 | 0.95331 | 1.3005
-0.0036 | 0.65 |  | 0.65133
-0.012 | -0.36 |  | -0.3605
-0.0218 | -1.2 |  | -1.2035
-0.0334 | -2.18 |  | -2.1812
-0.041 | -3.34 |  | -3.3365
-0.0462 | -4.1 |  | -4.1028
-0.047 | -4.62 |  | -4.6209
-0.0583 | -4.7 |  | -4.7019
-0.0565 | -5.83 |  | -5.8313
-0.0532 | -5.65 |  | -5.6481
-0.0549 | -5.32 |  | -5.3186
-0.0589 | -5.49 |  | -5.489
-0.0714 | -5.89 |  | -5.8874
-0.0891 | -7.14 |  | -7.145
-0.1093 | -8.91 |  | -8.9076
-0.1233 | -10.93 |  | -10.9315
-0.115 | -12.33 |  | -12.329
-0.1029 | -11.5 |  | -11.4961
-0.0813 | -10.29 |  | -10.2902
-0.0647 | -8.13 |  | -8.1304
-0.0465 | -6.47 |  | -6.4699
-0.0349 | -4.65 |  | -4.6468
-0.0334 | -3.49 |  | -3.4866
-0.033 | -3.34 |  | -3.3387
-0.0276 | -3.3 |  | -3.3012
-0.0116 | -2.76 |  | -2.7638
0.0001 | -1.16 |  | -1.1566
0.0082 | 0.01 |  | 0.0093071
0.0124 | 0.82 |  | 0.81819
1.2351